## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1202-14_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1202-14_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1202-14_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1202-14_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1202-14_0_3_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1202-14_0_3_node_34 | 0.4 | n |  | TRUE
6 | bus_LV_1202-14_0_3_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_1202-14_0_3_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_1202-14_0_3_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1202-14_0_3_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_1202-14_0_3_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1202-14_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1202-14_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1202-14_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1202-14_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1202-14_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1202-14_0_3_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1202-14_0_3_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1202-14_0_3_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_1202-14_0_3_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_1202-14_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1202-14_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1202-14_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1202-14_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1202-14_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1202-14_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1202-14_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1202-14_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1202-14_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1202-14_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1202-14_0_3_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_1202-14_0_3_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1202-14_0_3_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_1202-14_0_3_node_29 | 0.4 | n |  | TRUE
34 | bus_MV_132_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1202-14_0_3_load_0 | 0 | 0.0031425 | 0.00078759 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1202-14_0_3_load_2 | 2 | 0.0095732 | 0.0023993 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1202-14_0_3_load_3 | 3 | 0.0058375 | 0.001463 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1202-14_0_3_load_34 | 5 | 0.01079 | 0.0027041 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1202-14_0_3_load_25 | 7 | 0.0030744 | 0.00077053 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1202-14_0_3_load_4 | 8 | 0.025272 | 0.0063338 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1202-14_0_3_load_32 | 9 | 0.0040437 | 0.0010135 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1202-14_0_3_load_30 | 10 | 0.0037698 | 0.00094481 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1202-14_0_3_load_7 | 11 | 0.010929 | 0.002739 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1202-14_0_3_load_8 | 12 | 0.011256 | 0.0028209 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1202-14_0_3_load_9 | 13 | 0.0079794 | 0.0019998 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1202-14_0_3_load_10 | 14 | 0.002109 | 0.00052858 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1202-14_0_3_load_11 | 15 | 0.0065798 | 0.0016491 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1202-14_0_3_load_17 | 16 | 0.0055248 | 0.0013846 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1202-14_0_3_load_33 | 18 | 0.0052064 | 0.0013048 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1202-14_0_3_load_22 | 19 | 0.0056672 | 0.0014203 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1202-14_0_3_load_12 | 20 | 0.0074675 | 0.0018715 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1202-14_0_3_load_13 | 21 | 0.0047956 | 0.0012019 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1202-14_0_3_load_14 | 22 | 0.0073493 | 0.0018419 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1202-14_0_3_load_18 | 25 | 0.0021873 | 0.0005482 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1202-14_0_3_load_19 | 26 | 0.014177 | 0.0035532 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1202-14_0_3_load_20 | 27 | 0.006172 | 0.0015468 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1202-14_0_3_load_21 | 28 | 0.017891 | 0.0044839 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1202-14_0_3_load_26 | 29 | 0.0078472 | 0.0019667 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1202-14_0_3_load_35 | 30 | 0.0026654 | 0.000668 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1202-14_0_3_load_27 | 31 | 0.0049061 | 0.0012296 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1202-14_0_3_load_28 | 32 | 0.010248 | 0.0025685 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1202-14_0_3_load_29 | 33 | 0.0051473 | 0.00129 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1202-14_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.058366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1202-14_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0011252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1202-14_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0078368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1202-14_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.027787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1202-14_0_3_line_4 | NAYY 4x150 SE | 3 | 7 | 0.016208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1202-14_0_3_line_5 | NAYY 4x150 SE | 4 | 8 | 0.011487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1202-14_0_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.012406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1202-14_0_3_line_7 | NAYY 4x150 SE | 6 | 18 | 0.0054213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1202-14_0_3_line_8 | NAYY 4x150 SE | 6 | 33 | 0.010813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1202-14_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.040302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1202-14_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0091958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1202-14_0_3_line_11 | NAYY 4x150 SE | 10 | 33 | 0.029416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1202-14_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.020311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1202-14_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.0044122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1202-14_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.0046774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1202-14_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.040284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1202-14_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.01374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1202-14_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.015573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1202-14_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.018373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1202-14_0_3_line_19 | NAYY 4x150 SE | 17 | 19 | 0.028486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1202-14_0_3_line_20 | NAYY 4x150 SE | 19 | 30 | 0.093638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1202-14_0_3_line_21 | NAYY 4x150 SE | 19 | 25 | 0.01994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1202-14_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.0035217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1202-14_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.018549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1202-14_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.028265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1202-14_0_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.0079763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1202-14_0_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.023582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1202-14_0_3_line_27 | NAYY 4x150 SE | 23 | 26 | 0.033824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1202-14_0_3_line_28 | NAYY 4x150 SE | 24 | 27 | 0.023701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1202-14_0_3_line_29 | NAYY 4x150 SE | 24 | 28 | 0.024964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1202-14_0_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.0027188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1202-14_0_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.0093384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1202-14_0_3_line_32 | NAYY 4x150 SE | 31 | 32 | 0.0092289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1202-14_0_3_trafo_33 | 0.25 MVA 20/0.4 kV | 34 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2688699.6636 | 1165573.0258 | 2688710.1961 | 1165593.0822 | 2688719.8654 | 1165620.2525 | 2688721.3522 | 1165626.9619
1 | 2688721.5957 | 1165628.0605 | 2688721.3522 | 1165626.9619
2 | 2688699.6636 | 1165573.0258 | 2688703.2977 | 1165570.1555 | 2688705.5749 | 1165567.8988
3 | 2688699.6636 | 1165573.0258 | 2688673.6575 | 1165582.8147
4 | 2688705.5749 | 1165567.8988 | 2688707.5354 | 1165560.6345 | 2688706.0765 | 1165552.0744
5 | 2688673.6575 | 1165582.8147 | 2688670.6755 | 1165593.9076
6 | 2688769.7244 | 1165560.3301 | 2688771.1624 | 1165548.0105
7 | 2688771.1624 | 1165548.0105 | 2688775.7302 | 1165547.7667 | 2688776.3072 | 1165547.1468
8 | 2688771.1624 | 1165548.0105 | 2688764.5439 | 1165539.4594
9 | 2688731.6176 | 1165520.8992 | 2688706.0765 | 1165552.0744
10 | 2688731.6176 | 1165520.8992 | 2688740.0588 | 1165524.5471
11 | 2688764.5439 | 1165539.4594 | 2688759.507 | 1165532.9515 | 2688740.0588 | 1165524.5471
12 | 2688793.044 | 1165494.6751 | 2688789.7441 | 1165499.0998 | 2688788.1309 | 1165507.7256 | 2688787.906 | 1165513.7375
13 | 2688796.1363 | 1165491.5954 | 2688794.3695 | 1165492.8977 | 2688793.044 | 1165494.6751
14 | 2688787.7311 | 1165518.4116 | 2688787.906 | 1165513.7375
15 | 2688796.1363 | 1165491.5954 | 2688803.3897 | 1165486.2491 | 2688812.0406 | 1165482.8193 | 2688818.4962 | 1165482.3255 | 2688826.3783 | 1165483.7651 | 2688833.6507 | 1165485.518
16 | 2688786.3108 | 1165532.0407 | 2688787.4474 | 1165525.9933 | 2688787.7311 | 1165518.4116
17 | 2688848.921 | 1165482.9532 | 2688840.7936 | 1165485.1567 | 2688833.6507 | 1165485.518 | 2688833.6507 | 1165485.518
18 | 2688776.3072 | 1165547.1468 | 2688781.3643 | 1165541.7129 | 2688785.9846 | 1165533.7764 | 2688786.3108 | 1165532.0407
19 | 2688848.921 | 1165482.9532 | 2688859.5326 | 1165494.5282 | 2688866.1839 | 1165505.444
20 | 2688866.1839 | 1165505.444 | 2688938.7976 | 1165446.323
21 | 2688866.1839 | 1165505.444 | 2688866.4711 | 1165505.9154 | 2688875.0542 | 1165520.0175 | 2688876.3882 | 1165522.5695
22 | 2688862.5715 | 1165562.0143 | 2688864.3483 | 1165558.9737
23 | 2688853.2126 | 1165578.0297 | 2688862.5715 | 1165562.0143
24 | 2688887.3127 | 1165543.4685 | 2688873.6091 | 1165549.3695 | 2688864.401 | 1165558.8835 | 2688864.3483 | 1165558.9737
25 | 2688846.4193 | 1165582.2096 | 2688853.2126 | 1165578.0297
26 | 2688887.3127 | 1165543.4685 | 2688876.3882 | 1165522.5695
27 | 2688887.3127 | 1165543.4685 | 2688893.5509 | 1165554.5563 | 2688895.7772 | 1165557.8135 | 2688902.7561 | 1165568.0117 | 2688906.3258 | 1165571.2198
28 | 2688846.4193 | 1165582.2096 | 2688837.8317 | 1165586.0184 | 2688823.597 | 1165587.4533
29 | 2688838.3962 | 1165605.8498 | 2688846.4193 | 1165582.2096
30 | 2688823.597 | 1165587.4533 | 2688823.597 | 1165587.4533 | 2688821.2007 | 1165588.7377
31 | 2688821.2007 | 1165588.7377 | 2688812.9701 | 1165593.1493
32 | 2688809.9904 | 1165601.8277 | 2688812.7977 | 1165593.2417 | 2688812.9701 | 1165593.1493

## bus_geodata
| x | y | coords
0 | 2688721.3522 | 1165626.9619
1 | 2688699.6636 | 1165573.0258
2 | 2688721.5957 | 1165628.0605
3 | 2688705.5749 | 1165567.8988
4 | 2688673.6575 | 1165582.8147
5 | 2688769.7244 | 1165560.3301
6 | 2688771.1624 | 1165548.0105
7 | 2688706.0765 | 1165552.0744
8 | 2688670.6755 | 1165593.9076
9 | 2688731.6176 | 1165520.8992
10 | 2688740.0588 | 1165524.5471
11 | 2688793.044 | 1165494.6751
12 | 2688787.906 | 1165513.7375
13 | 2688796.1363 | 1165491.5954
14 | 2688787.7311 | 1165518.4116
15 | 2688833.6507 | 1165485.518
16 | 2688786.3108 | 1165532.0407
17 | 2688848.921 | 1165482.9532
18 | 2688776.3072 | 1165547.1468
19 | 2688866.1839 | 1165505.444
20 | 2688862.5715 | 1165562.0143
21 | 2688864.3483 | 1165558.9737
22 | 2688853.2126 | 1165578.0297
23 | 2688887.3127 | 1165543.4685
24 | 2688846.4193 | 1165582.2096
25 | 2688876.3882 | 1165522.5695
26 | 2688906.3258 | 1165571.2198
27 | 2688823.597 | 1165587.4533
28 | 2688838.3962 | 1165605.8498
29 | 2688821.2007 | 1165588.7377
30 | 2688938.7976 | 1165446.323
31 | 2688812.9701 | 1165593.1493
32 | 2688809.9904 | 1165601.8277
33 | 2688764.5439 | 1165539.4594
34 | 2688771.1624 | 1165548.0105

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99029 | -0.068032 | 0.0031425 | 0.00078759
1 | 0.99136 | -0.060486 | 0 | 0
2 | 0.99028 | -0.068142 | 0.0095732 | 0.0023993
3 | 0.99179 | -0.057463 | 0.0058375 | 0.001463
4 | 0.99035 | -0.067625 | 0 | 0
5 | 0.99926 | -0.0051636 | 0.01079 | 0.0027041
6 | 0.99945 | -0.0038259 | 0 | 0
7 | 0.99281 | -0.050262 | 0.0030744 | 0.00077053
8 | 0.98993 | -0.07058 | 0.025272 | 0.0063338
9 | 0.99553 | -0.03117 | 0.0040437 | 0.0010135
10 | 0.99621 | -0.026454 | 0.0037698 | 0.00094481
11 | 0.99472 | -0.036414 | 0.010929 | 0.002739
12 | 0.99645 | -0.02446 | 0.011256 | 0.0028209
13 | 0.99438 | -0.038773 | 0.0079794 | 0.0019998
14 | 0.99689 | -0.021449 | 0.002109 | 0.00052858
15 | 0.98861 | -0.078849 | 0.0065798 | 0.0016491
16 | 0.99819 | -0.012473 | 0.0055248 | 0.0013846
17 | 0.98653 | -0.093415 | 0 | 0
18 | 1 | 0 | -0.21028 | -0.052904
19 | 0.98272 | -0.12022 | 0.0056672 | 0.0014203
20 | 0.97441 | -0.17927 | 0.0074675 | 0.0018715
21 | 0.97473 | -0.17698 | 0.0047956 | 0.0012019
22 | 0.97293 | -0.1899 | 0.0073493 | 0.0018419
23 | 0.9775 | -0.15724 | 0 | 0
24 | 0.97238 | -0.19386 | 0 | 0
25 | 0.98029 | -0.13738 | 0.0021873 | 0.0005482
26 | 0.9768 | -0.16225 | 0.014177 | 0.0035532
27 | 0.97137 | -0.20117 | 0.006172 | 0.0015468
28 | 0.97173 | -0.19858 | 0.017891 | 0.0044839
29 | 0.97128 | -0.20183 | 0.0078472 | 0.0019667
30 | 0.98235 | -0.1228 | 0.0026654 | 0.000668
31 | 0.97107 | -0.20333 | 0.0049061 | 0.0012296
32 | 0.97093 | -0.20433 | 0.010248 | 0.0025685
33 | 0.99852 | -0.010301 | 0.0051473 | 0.00129
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012716 | -0.0031869 | 0.012729 | 0.0031913 | 1.3296e-05 | 4.362e-06 | 0.019107 | 0.019107 | 0.019107 | 0.99029 | -0.068032 | 0.99136 | -0.060486 | 7.0766
1 | 0.0095734 | 0.0023993 | -0.0095732 | -0.0023993 | 1.4529e-07 | 4.1405e-08 | 0.014385 | 0.014385 | 0.014385 | 0.99029 | -0.068032 | 0.99028 | -0.068142 | 5.3278
2 | -0.038037 | -0.0095381 | 0.038053 | 0.0095442 | 1.5941e-05 | 6.03e-06 | 0.057094 | 0.057094 | 0.057094 | 0.99136 | -0.060486 | 0.99179 | -0.057463 | 21.146
3 | 0.025307 | 0.0063469 | -0.025282 | -0.0063376 | 2.5022e-05 | 9.2658e-06 | 0.037988 | 0.037988 | 0.037988 | 0.99136 | -0.060486 | 0.99035 | -0.067625 | 14.0695
4 | -0.04389 | -0.011007 | 0.043934 | 0.011024 | 4.3858e-05 | 1.6659e-05 | 0.065852 | 0.065852 | 0.065852 | 0.99179 | -0.057463 | 0.99281 | -0.050262 | 24.3898
5 | 0.025282 | 0.0063376 | -0.025272 | -0.0063338 | 1.0343e-05 | 3.8305e-06 | 0.037988 | 0.037988 | 0.037988 | 0.99035 | -0.067625 | 0.98993 | -0.07058 | 14.0695
6 | -0.01079 | -0.0027041 | 0.010792 | 0.0027047 | 1.9984e-06 | 6.0607e-07 | 0.016067 | 0.016067 | 0.016067 | 0.99926 | -0.0051636 | 0.99945 | -0.0038259 | 5.9508
7 | -0.071098 | -0.017876 | 0.071135 | 0.01789 | 3.7919e-05 | 1.4513e-05 | 0.10587 | 0.10587 | 0.10587 | 0.99945 | -0.0038259 | 1 | 0 | 39.212
8 | 0.060306 | 0.015171 | -0.060251 | -0.01515 | 5.4418e-05 | 2.0789e-05 | 0.089806 | 0.089806 | 0.089806 | 0.99945 | -0.0038259 | 0.99852 | -0.010301 | 33.2613
9 | -0.047008 | -0.011794 | 0.047133 | 0.011842 | 0.00012485 | 4.7498e-05 | 0.07046 | 0.07046 | 0.07046 | 0.99281 | -0.050262 | 0.99553 | -0.03117 | 26.0964
10 | -0.051177 | -0.012855 | 0.051211 | 0.012868 | 3.3585e-05 | 1.2798e-05 | 0.076504 | 0.076504 | 0.076504 | 0.99553 | -0.03117 | 0.99621 | -0.026454 | 28.3349
11 | -0.05498 | -0.013813 | 0.055104 | 0.01386 | 0.00012383 | 4.7243e-05 | 0.082135 | 0.082135 | 0.082135 | 0.99621 | -0.026454 | 0.99852 | -0.010301 | 30.4204
12 | -0.11879 | -0.030025 | 0.11899 | 0.030101 | 0.00020031 | 7.6513e-05 | 0.17779 | 0.17779 | 0.17779 | 0.99472 | -0.036414 | 0.99645 | -0.02446 | 32.9239
13 | 0.10786 | 0.027286 | -0.10782 | -0.027272 | 3.5878e-05 | 1.3685e-05 | 0.16144 | 0.16144 | 0.16144 | 0.99472 | -0.036414 | 0.99438 | -0.038773 | 29.8964
14 | -0.13025 | -0.032922 | 0.1303 | 0.032943 | 5.5263e-05 | 2.1133e-05 | 0.1946 | 0.1946 | 0.1946 | 0.99645 | -0.02446 | 0.99689 | -0.021449 | 36.0365
15 | 0.099846 | 0.025272 | -0.099284 | -0.025057 | 0.00056183 | 0.00021557 | 0.1495 | 0.1495 | 0.1495 | 0.99438 | -0.038773 | 0.98861 | -0.078849 | 55.3704
16 | -0.13241 | -0.033472 | 0.13258 | 0.033536 | 0.00016763 | 6.4116e-05 | 0.19775 | 0.19775 | 0.19775 | 0.99689 | -0.021449 | 0.99819 | -0.012473 | 36.6195
17 | 0.092704 | 0.023408 | -0.092515 | -0.023335 | 0.00018937 | 7.2633e-05 | 0.1396 | 0.1396 | 0.1396 | 0.98861 | -0.078849 | 0.98653 | -0.093415 | 51.7024
18 | -0.1381 | -0.034921 | 0.13835 | 0.035014 | 0.00024321 | 9.306e-05 | 0.20598 | 0.20598 | 0.20598 | 0.99819 | -0.012473 | 1 | 0 | 38.1446
19 | 0.092515 | 0.023335 | -0.092168 | -0.023202 | 0.00034639 | 0.00013286 | 0.1396 | 0.1396 | 0.1396 | 0.98653 | -0.093415 | 0.98272 | -0.12022 | 51.7024
20 | 0.0026663 | 0.00066718 | -0.0026654 | -0.000668 | 9.5232e-07 | -8.1965e-07 | 0.0040369 | 0.0040373 | 0.0040373 | 0.98272 | -0.12022 | 0.98235 | -0.1228 | 1.4953
21 | 0.083835 | 0.021115 | -0.083634 | -0.021038 | 0.00020062 | 7.691e-05 | 0.12698 | 0.12698 | 0.12698 | 0.98272 | -0.12022 | 0.98029 | -0.13738 | 47.0291
22 | -0.062036 | -0.015567 | 0.062055 | 0.015575 | 1.9725e-05 | 7.5426e-06 | 0.094741 | 0.094741 | 0.094741 | 0.97441 | -0.17927 | 0.97473 | -0.17698 | 35.0892
23 | 0.054568 | 0.013696 | -0.054488 | -0.013665 | 8.0389e-05 | 3.0688e-05 | 0.083337 | 0.083337 | 0.083337 | 0.97441 | -0.17927 | 0.97293 | -0.1899 | 30.8657
24 | -0.066851 | -0.016776 | 0.067035 | 0.016847 | 0.00018372 | 7.0308e-05 | 0.10206 | 0.10206 | 0.10206 | 0.97473 | -0.17698 | 0.9775 | -0.15724 | 37.8006
25 | 0.047138 | 0.011823 | -0.047113 | -0.011813 | 2.5872e-05 | 9.8516e-06 | 0.072097 | 0.072097 | 0.072097 | 0.97293 | -0.1899 | 0.97238 | -0.19386 | 26.7027
26 | -0.081222 | -0.020403 | 0.081447 | 0.02049 | 0.00022502 | 8.6248e-05 | 0.12366 | 0.12366 | 0.12366 | 0.9775 | -0.15724 | 0.98029 | -0.13738 | 45.7994
27 | 0.014187 | 0.0035565 | -0.014177 | -0.0035532 | 9.8448e-06 | 3.3628e-06 | 0.021597 | 0.021597 | 0.021597 | 0.9775 | -0.15724 | 0.9768 | -0.16225 | 7.9989
28 | 0.02921 | 0.007325 | -0.02918 | -0.0073139 | 2.9552e-05 | 1.1072e-05 | 0.044701 | 0.044701 | 0.044701 | 0.97238 | -0.19386 | 0.97137 | -0.20117 | 16.5558
29 | 0.017903 | 0.0044881 | -0.017891 | -0.0044839 | 1.1692e-05 | 4.1875e-06 | 0.027397 | 0.027397 | 0.027397 | 0.97238 | -0.19386 | 0.97173 | -0.19858 | 10.1469
30 | 0.023008 | 0.005767 | -0.023006 | -0.0057663 | 2.1075e-06 | 7.7694e-07 | 0.035246 | 0.035246 | 0.035246 | 0.97137 | -0.20117 | 0.97128 | -0.20183 | 13.0541
31 | 0.015159 | 0.0037996 | -0.015156 | -0.0037985 | 3.1429e-06 | 1.0933e-06 | 0.023224 | 0.023224 | 0.023224 | 0.97128 | -0.20183 | 0.97107 | -0.20333 | 8.6015
32 | 0.01025 | 0.0025689 | -0.010248 | -0.0025685 | 1.4206e-06 | 4.3224e-07 | 0.015706 | 0.015706 | 0.015706 | 0.97107 | -0.20333 | 0.97093 | -0.20433 | 5.8172

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21549 | 0.054209

## res_load
| p_mw | q_mvar
0 | 0.0031425 | 0.00078759
1 | 0.0095732 | 0.0023993
2 | 0.0058375 | 0.001463
3 | 0.01079 | 0.0027041
4 | 0.0030744 | 0.00077053
5 | 0.025272 | 0.0063338
6 | 0.0040437 | 0.0010135
7 | 0.0037698 | 0.00094481
8 | 0.010929 | 0.002739
9 | 0.011256 | 0.0028209
10 | 0.0079794 | 0.0019998
11 | 0.002109 | 0.00052858
12 | 0.0065798 | 0.0016491
13 | 0.0055248 | 0.0013846
14 | 0.0052064 | 0.0013048
15 | 0.0056672 | 0.0014203
16 | 0.0074675 | 0.0018715
17 | 0.0047956 | 0.0012019
18 | 0.0073493 | 0.0018419
19 | 0.0021873 | 0.0005482
20 | 0.014177 | 0.0035532
21 | 0.006172 | 0.0015468
22 | 0.017891 | 0.0044839
23 | 0.0078472 | 0.0019667
24 | 0.0026654 | 0.000668
25 | 0.0049061 | 0.0012296
26 | 0.010248 | 0.0025685
27 | 0.0051473 | 0.00129

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1