## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1202-19_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1202-19_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1202-19_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1202-19_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1202-19_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1202-19_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1202-19_0_3_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_1202-19_0_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1202-19_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1202-19_0_3_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_1202-19_0_3_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1202-19_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1202-19_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1202-19_0_3_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_1202-19_0_3_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1202-19_0_3_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1202-19_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1202-19_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1202-19_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1202-19_0_3_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1202-19_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1202-19_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1202-19_0_3_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1202-19_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1202-19_0_3_node_22 | 0.4 | n |  | TRUE
25 | bus_MV_132_0_node_32 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1202-19_0_3_load_0 | 0 | 0.01231 | 0.0030851 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1202-19_0_3_load_1 | 1 | 0.0093558 | 0.0023448 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1202-19_0_3_load_2 | 2 | 0.004792 | 0.001201 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1202-19_0_3_load_3 | 3 | 0.01433 | 0.0035914 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1202-19_0_3_load_4 | 4 | 0.018822 | 0.0047172 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1202-19_0_3_load_23 | 6 | 0.0046732 | 0.0011712 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1202-19_0_3_load_16 | 7 | 0.025032 | 0.0062735 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1202-19_0_3_load_5 | 10 | 0.017414 | 0.0043643 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1202-19_0_3_load_25 | 13 | 0.032449 | 0.0081325 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1202-19_0_3_load_26 | 14 | 0.010877 | 0.002726 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1202-19_0_3_load_24 | 15 | 0.0049065 | 0.0012297 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1202-19_0_3_load_10 | 16 | 0.015788 | 0.0039568 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1202-19_0_3_load_12 | 17 | 0.026074 | 0.0065348 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1202-19_0_3_load_27 | 19 | 0.0079167 | 0.0019841 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1202-19_0_3_load_17 | 20 | 0.0042075 | 0.0010545 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1202-19_0_3_load_18 | 21 | 0.011465 | 0.0028735 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1202-19_0_3_load_20 | 22 | 0.008927 | 0.0022373 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1202-19_0_3_load_21 | 23 | 0.0059727 | 0.0014969 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1202-19_0_3_load_22 | 24 | 0.0033789 | 0.00084684 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1202-19_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1202-19_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0050924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1202-19_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.012734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1202-19_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.01298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1202-19_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.030168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1202-19_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0074429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1202-19_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.059057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1202-19_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.003505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1202-19_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.042784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1202-19_0_3_line_9 | NAYY 4x150 SE | 7 | 14 | 0.020823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1202-19_0_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.0095576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1202-19_0_3_line_11 | NAYY 4x150 SE | 9 | 18 | 0.027172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1202-19_0_3_line_12 | NAYY 4x150 SE | 10 | 11 | 0.0063554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1202-19_0_3_line_13 | NAYY 4x150 SE | 11 | 12 | 0.033443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1202-19_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.021269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1202-19_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.022501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1202-19_0_3_line_16 | NAYY 4x150 SE | 14 | 19 | 0.0088852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1202-19_0_3_line_17 | NAYY 4x150 SE | 15 | 24 | 0.0050327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1202-19_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.025746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1202-19_0_3_line_19 | NAYY 4x150 SE | 17 | 18 | 0.061949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1202-19_0_3_line_20 | NAYY 4x150 SE | 20 | 21 | 0.019211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1202-19_0_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.016244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1202-19_0_3_line_22 | NAYY 4x150 SE | 22 | 23 | 0.012406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1202-19_0_3_line_23 | NAYY 4x150 SE | 23 | 24 | 0.018356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1202-19_0_3_trafo_1 | 0.25 MVA 20/0.4 kV | 25 | 1 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2688608.9639 | 1165448.0821 | 2688615.2604 | 1165456.4553
1 | 2688608.9639 | 1165448.0821 | 2688605.9033 | 1165444.0121
2 | 2688615.2604 | 1165456.4553 | 2688618.7518 | 1165461.0982 | 2688624.5394 | 1165464.8999
3 | 2688598.0287 | 1165433.6947 | 2688600.6428 | 1165437.0167 | 2688605.9033 | 1165444.0121
4 | 2688650.5511 | 1165480.1675 | 2688645.7662 | 1165477.4731 | 2688627.8764 | 1165467.0919 | 2688624.5394 | 1165464.8999
5 | 2688593.4262 | 1165427.8456 | 2688598.0287 | 1165433.6947
6 | 2688650.5511 | 1165480.1675 | 2688654.6269 | 1165471.7558 | 2688656.1126 | 1165469.1651 | 2688659.3566 | 1165463.6651 | 2688662.1687 | 1165458.8926 | 2688666.6758 | 1165454.9901 | 2688673.6672 | 1165448.2891 | 2688679.571 | 1165443.1509 | 2688686.5646 | 1165437.3394 | 2688688.3576 | 1165436.0086
7 | 2688649.0265 | 1165483.3247 | 2688650.5511 | 1165480.1675
8 | 2688566.3528 | 1165397.2541 | 2688566.3891 | 1165402.0687 | 2688568.2052 | 1165406.1534 | 2688571.2899 | 1165409.3786 | 2688588.9681 | 1165422.1802 | 2688593.4262 | 1165427.8456
9 | 2688688.3576 | 1165436.0086 | 2688700.3553 | 1165427.1034 | 2688705.2553 | 1165423.8509
10 | 2688649.0265 | 1165483.3247 | 2688645.9289 | 1165484.0906 | 2688643.381 | 1165486.0097 | 2688641.801 | 1165488.7659
11 | 2688574.2857 | 1165372.4004 | 2688568.9641 | 1165378.0476 | 2688566.3355 | 1165394.2743 | 2688566.3528 | 1165397.2541
12 | 2688642.3528 | 1165494.9666 | 2688641.4404 | 1165491.9291 | 2688641.801 | 1165488.7659
13 | 2688642.3528 | 1165494.9666 | 2688635.5177 | 1165504.5828 | 2688630.5872 | 1165514.3493 | 2688628.9858 | 1165517.5165 | 2688625.7515 | 1165523.9171
14 | 2688625.7515 | 1165523.9171 | 2688607.1742 | 1165513.5617
15 | 2688587.5201 | 1165502.6062 | 2688607.1742 | 1165513.5617
16 | 2688712.6994 | 1165419.0023 | 2688711.1367 | 1165419.947 | 2688705.2553 | 1165423.8509
17 | 2688587.5201 | 1165502.6062 | 2688583.1242 | 1165500.1558
18 | 2688635.2977 | 1165373.6226 | 2688656.1281 | 1165366.3921 | 2688659.6308 | 1165365.2114
19 | 2688574.2857 | 1165372.4004 | 2688585.6833 | 1165375.3924 | 2688601.3665 | 1165377.0356 | 2688611.3793 | 1165378.3729 | 2688622.3426 | 1165377.0559 | 2688630.5327 | 1165375.2756 | 2688635.2977 | 1165373.6226
20 | 2688542.0666 | 1165477.2695 | 2688535.4446 | 1165473.5783 | 2688528.788 | 1165472.1238 | 2688524.5461 | 1165469.8443
21 | 2688542.0666 | 1165477.2695 | 2688556.2549 | 1165485.1783
22 | 2688556.2549 | 1165485.1783 | 2688567.0912 | 1165491.2187
23 | 2688583.1242 | 1165500.1558 | 2688567.0912 | 1165491.2187

## bus_geodata
| x | y | coords
0 | 2688608.9639 | 1165448.0821
1 | 2688615.2604 | 1165456.4553
2 | 2688605.9033 | 1165444.0121
3 | 2688624.5394 | 1165464.8999
4 | 2688598.0287 | 1165433.6947
5 | 2688650.5511 | 1165480.1675
6 | 2688593.4262 | 1165427.8456
7 | 2688688.3576 | 1165436.0086
8 | 2688649.0265 | 1165483.3247
9 | 2688566.3528 | 1165397.2541
10 | 2688641.801 | 1165488.7659
11 | 2688642.3528 | 1165494.9666
12 | 2688625.7515 | 1165523.9171
13 | 2688607.1742 | 1165513.5617
14 | 2688705.2553 | 1165423.8509
15 | 2688587.5201 | 1165502.6062
16 | 2688659.6308 | 1165365.2114
17 | 2688635.2977 | 1165373.6226
18 | 2688574.2857 | 1165372.4004
19 | 2688712.6994 | 1165419.0023
20 | 2688524.5461 | 1165469.8443
21 | 2688542.0666 | 1165477.2695
22 | 2688556.2549 | 1165485.1783
23 | 2688567.0912 | 1165491.2187
24 | 2688583.1242 | 1165500.1558
25 | 2688626.9111 | 1165466.4578

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99876 | -0.0086344 | 0.01231 | 0.0030851
1 | 1 | 0 | -0.23213 | -0.058237
2 | 0.99825 | -0.012211 | 0.004792 | 0.001201
3 | 0.99865 | -0.0093476 | 0.01433 | 0.0035914
4 | 0.99703 | -0.02072 | 0.018822 | 0.0047172
5 | 0.99577 | -0.029417 | 0 | 0
6 | 0.99653 | -0.0242 | 0.0046732 | 0.0011712
7 | 0.99205 | -0.055569 | 0.025032 | 0.0062735
8 | 0.99532 | -0.032549 | 0 | 0
9 | 0.99394 | -0.042252 | 0 | 0
10 | 0.9941 | -0.041104 | 0.017414 | 0.0043643
11 | 0.99345 | -0.045684 | 0 | 0
12 | 0.99 | -0.069888 | 0 | 0
13 | 0.98781 | -0.085368 | 0.032449 | 0.0081325
14 | 0.99149 | -0.05954 | 0.010877 | 0.002726
15 | 0.98654 | -0.094324 | 0.0049065 | 0.0012297
16 | 0.98798 | -0.084307 | 0.015788 | 0.0039568
17 | 0.98856 | -0.080153 | 0.026074 | 0.0065348
18 | 0.9923 | -0.053765 | 0 | 0
19 | 0.99139 | -0.060254 | 0.0079167 | 0.0019841
20 | 0.98456 | -0.10843 | 0.0042075 | 0.0010545
21 | 0.98467 | -0.1076 | 0.011465 | 0.0028735
22 | 0.98504 | -0.10498 | 0.008927 | 0.0022373
23 | 0.98548 | -0.10184 | 0.0059727 | 0.0014969
24 | 0.9863 | -0.096077 | 0.0033789 | 0.00084684
25 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.082931 | -0.020845 | 0.083031 | 0.020884 | 9.9834e-05 | 3.826e-05 | 0.12358 | 0.12358 | 0.12358 | 0.99876 | -0.0086344 | 1 | 0 | 45.7694
1 | 0.070621 | 0.01776 | -0.070586 | -0.017747 | 3.5192e-05 | 1.3469e-05 | 0.10524 | 0.10524 | 0.10524 | 0.99876 | -0.0086344 | 0.99825 | -0.012211 | 38.9769
2 | 0.1483 | 0.037353 | -0.1481 | -0.037279 | 0.00019358 | 7.412e-05 | 0.22074 | 0.22074 | 0.22074 | 1 | 0 | 0.99865 | -0.0093476 | 40.8771
3 | 0.065794 | 0.016546 | -0.065716 | -0.016516 | 7.7937e-05 | 2.9806e-05 | 0.098094 | 0.098094 | 0.098094 | 0.99825 | -0.012211 | 0.99703 | -0.02072 | 36.3313
4 | 0.13378 | 0.033688 | -0.1334 | -0.033545 | 0.00037418 | 0.00014313 | 0.19938 | 0.19938 | 0.19938 | 0.99865 | -0.0093476 | 0.99577 | -0.029417 | 36.9231
5 | 0.046894 | 0.011799 | -0.046871 | -0.01179 | 2.276e-05 | 8.6567e-06 | 0.070004 | 0.070004 | 0.070004 | 0.99703 | -0.02072 | 0.99653 | -0.0242 | 25.9272
6 | 0.043996 | 0.011048 | -0.043836 | -0.010988 | 0.00015932 | 6.0512e-05 | 0.065752 | 0.065752 | 0.065752 | 0.99577 | -0.029417 | 0.99205 | -0.055569 | 24.3526
7 | 0.089406 | 0.022497 | -0.089366 | -0.022482 | 3.9057e-05 | 1.4976e-05 | 0.13363 | 0.13363 | 0.13363 | 0.99577 | -0.029417 | 0.99532 | -0.032549 | 49.4938
8 | 0.042198 | 0.010619 | -0.042092 | -0.010579 | 0.00010605 | 4.0231e-05 | 0.063026 | 0.063026 | 0.063026 | 0.99653 | -0.0242 | 0.99394 | -0.042252 | 23.3429
9 | 0.018805 | 0.004714 | -0.018794 | -0.0047103 | 1.0337e-05 | 3.7072e-06 | 0.028206 | 0.028206 | 0.028206 | 0.99205 | -0.055569 | 0.99149 | -0.05954 | 10.4467
10 | 0.089366 | 0.022482 | -0.08926 | -0.022441 | 0.0001065 | 4.0839e-05 | 0.13363 | 0.13363 | 0.13363 | 0.99532 | -0.032549 | 0.9941 | -0.041104 | 49.4938
11 | 0.042092 | 0.010579 | -0.042025 | -0.010553 | 6.7351e-05 | 2.5553e-05 | 0.063026 | 0.063026 | 0.063026 | 0.99394 | -0.042252 | 0.9923 | -0.053765 | 23.3429
12 | 0.071846 | 0.018077 | -0.0718 | -0.018059 | 4.5887e-05 | 1.7566e-05 | 0.10757 | 0.10757 | 0.10757 | 0.9941 | -0.041104 | 0.99345 | -0.045684 | 39.8398
13 | 0.0718 | 0.018059 | -0.071559 | -0.017967 | 0.00024146 | 9.2439e-05 | 0.10757 | 0.10757 | 0.10757 | 0.99345 | -0.045684 | 0.99 | -0.069888 | 39.8399
14 | 0.071559 | 0.017967 | -0.071405 | -0.017908 | 0.00015356 | 5.879e-05 | 0.10757 | 0.10757 | 0.10757 | 0.99 | -0.069888 | 0.98781 | -0.085368 | 39.8399
15 | 0.038956 | 0.0097752 | -0.038908 | -0.0097569 | 4.8359e-05 | 1.8312e-05 | 0.058687 | 0.058687 | 0.058687 | 0.98781 | -0.085368 | 0.98654 | -0.094324 | 21.7359
16 | 0.0079175 | 0.0019843 | -0.0079167 | -0.0019841 | 7.8283e-07 | 1.8651e-07 | 0.011882 | 0.011883 | 0.011883 | 0.99149 | -0.05954 | 0.99139 | -0.060254 | 4.4009
17 | 0.034001 | 0.0085272 | -0.033993 | -0.0085241 | 8.2603e-06 | 3.1128e-06 | 0.051286 | 0.051286 | 0.051286 | 0.98654 | -0.094324 | 0.9863 | -0.096077 | 18.995
18 | -0.015788 | -0.0039568 | 0.015797 | 0.00396 | 9.0838e-06 | 3.1639e-06 | 0.023779 | 0.023779 | 0.023779 | 0.98798 | -0.084307 | 0.98856 | -0.080153 | 8.8069
19 | -0.041871 | -0.010495 | 0.042025 | 0.010553 | 0.00015355 | 5.8262e-05 | 0.063026 | 0.063026 | 0.063026 | 0.98856 | -0.080153 | 0.9923 | -0.053765 | 23.343
20 | -0.0042075 | -0.0010545 | 0.004208 | 0.0010544 | 4.8473e-07 | -5.79e-08 | 0.006359 | 0.0063589 | 0.006359 | 0.98456 | -0.10843 | 0.98467 | -0.1076 | 2.3552
21 | -0.015673 | -0.0039279 | 0.015679 | 0.0039299 | 5.6862e-06 | 1.9803e-06 | 0.023685 | 0.023685 | 0.023685 | 0.98467 | -0.1076 | 0.98504 | -0.10498 | 8.7723
22 | -0.024606 | -0.0061673 | 0.024617 | 0.0061712 | 1.0696e-05 | 3.9558e-06 | 0.03717 | 0.03717 | 0.03717 | 0.98504 | -0.10498 | 0.98548 | -0.10184 | 13.7668
23 | -0.03059 | -0.0076681 | 0.030614 | 0.0076773 | 2.4436e-05 | 9.1643e-06 | 0.046189 | 0.046189 | 0.046189 | 0.98548 | -0.10184 | 0.9863 | -0.096077 | 17.1069

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24149 | 0.060582

## res_load
| p_mw | q_mvar
0 | 0.01231 | 0.0030851
1 | 0.0093558 | 0.0023448
2 | 0.004792 | 0.001201
3 | 0.01433 | 0.0035914
4 | 0.018822 | 0.0047172
5 | 0.0046732 | 0.0011712
6 | 0.025032 | 0.0062735
7 | 0.017414 | 0.0043643
8 | 0.032449 | 0.0081325
9 | 0.010877 | 0.002726
10 | 0.0049065 | 0.0012297
11 | 0.015788 | 0.0039568
12 | 0.026074 | 0.0065348
13 | 0.0079167 | 0.0019841
14 | 0.0042075 | 0.0010545
15 | 0.011465 | 0.0028735
16 | 0.008927 | 0.0022373
17 | 0.0059727 | 0.0014969
18 | 0.0033789 | 0.00084684

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1