## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1215-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1215-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1215-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1215-5_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1215-5_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1215-5_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1215-5_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1215-5_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1215-5_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1215-5_0_3_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_1215-5_0_3_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1215-5_0_3_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1215-5_0_3_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1215-5_0_3_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1215-5_0_3_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1215-5_0_3_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1215-5_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1215-5_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1215-5_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1215-5_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1215-5_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1215-5_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1215-5_0_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1215-5_0_3_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_1215-5_0_3_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1215-5_0_3_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_1215-5_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1215-5_0_3_node_42 | 0.4 | n |  | TRUE
28 | bus_LV_1215-5_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1215-5_0_3_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1215-5_0_3_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_1215-5_0_3_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_1215-5_0_3_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1215-5_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1215-5_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1215-5_0_3_node_91 | 0.4 | n |  | TRUE
36 | bus_LV_1215-5_0_3_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1215-5_0_3_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_1215-5_0_3_node_92 | 0.4 | n |  | TRUE
39 | bus_LV_1215-5_0_3_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_1215-5_0_3_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1215-5_0_3_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1215-5_0_3_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_1215-5_0_3_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_1215-5_0_3_node_48 | 0.4 | n |  | TRUE
45 | bus_LV_1215-5_0_3_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_1215-5_0_3_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_1215-5_0_3_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_1215-5_0_3_node_79 | 0.4 | n |  | TRUE
49 | bus_LV_1215-5_0_3_node_86 | 0.4 | n |  | TRUE
50 | bus_LV_1215-5_0_3_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_1215-5_0_3_node_60 | 0.4 | n |  | TRUE
52 | bus_LV_1215-5_0_3_node_61 | 0.4 | n |  | TRUE
53 | bus_LV_1215-5_0_3_node_62 | 0.4 | n |  | TRUE
54 | bus_LV_1215-5_0_3_node_63 | 0.4 | n |  | TRUE
55 | bus_LV_1215-5_0_3_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_1215-5_0_3_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_1215-5_0_3_node_83 | 0.4 | n |  | TRUE
58 | bus_LV_1215-5_0_3_node_75 | 0.4 | n |  | TRUE
59 | bus_LV_1215-5_0_3_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_1215-5_0_3_node_51 | 0.4 | n |  | TRUE
61 | bus_LV_1215-5_0_3_node_73 | 0.4 | n |  | TRUE
62 | bus_LV_1215-5_0_3_node_85 | 0.4 | n |  | TRUE
63 | bus_LV_1215-5_0_3_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_1215-5_0_3_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_1215-5_0_3_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_1215-5_0_3_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_1215-5_0_3_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_1215-5_0_3_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_1215-5_0_3_node_82 | 0.4 | n |  | TRUE
70 | bus_LV_1215-5_0_3_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_1215-5_0_3_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_1215-5_0_3_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_1215-5_0_3_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_1215-5_0_3_node_81 | 0.4 | n |  | TRUE
75 | bus_LV_1215-5_0_3_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_1215-5_0_3_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_1215-5_0_3_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_1215-5_0_3_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_1215-5_0_3_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_1215-5_0_3_node_69 | 0.4 | n |  | TRUE
81 | bus_LV_1215-5_0_3_node_78 | 0.4 | n |  | TRUE
82 | bus_LV_1215-5_0_3_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_1215-5_0_3_node_93 | 0.4 | n |  | TRUE
84 | bus_LV_1215-5_0_3_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_1215-5_0_3_node_74 | 0.4 | n |  | TRUE
86 | bus_LV_1215-5_0_3_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_1215-5_0_3_node_87 | 0.4 | n |  | TRUE
88 | bus_LV_1215-5_0_3_node_96 | 0.4 | n |  | TRUE
89 | bus_LV_1215-5_0_3_node_95 | 0.4 | n |  | TRUE
90 | bus_LV_1215-5_0_3_node_88 | 0.4 | n |  | TRUE
91 | bus_LV_1215-5_0_3_node_89 | 0.4 | n |  | TRUE
92 | bus_LV_1215-5_0_3_node_90 | 0.4 | n |  | TRUE
93 | bus_LV_1215-5_0_3_node_115 | 0.4 | n |  | TRUE
94 | bus_LV_1215-5_0_3_node_116 | 0.4 | n |  | TRUE
95 | bus_LV_1215-5_0_3_node_109 | 0.4 | n |  | TRUE
96 | bus_LV_1215-5_0_3_node_117 | 0.4 | n |  | TRUE
97 | bus_LV_1215-5_0_3_node_113 | 0.4 | n |  | TRUE
98 | bus_LV_1215-5_0_3_node_118 | 0.4 | n |  | TRUE
99 | bus_LV_1215-5_0_3_node_99 | 0.4 | n |  | TRUE
100 | bus_LV_1215-5_0_3_node_94 | 0.4 | n |  | TRUE
101 | bus_LV_1215-5_0_3_node_100 | 0.4 | n |  | TRUE
102 | bus_LV_1215-5_0_3_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_1215-5_0_3_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_1215-5_0_3_node_101 | 0.4 | n |  | TRUE
105 | bus_LV_1215-5_0_3_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_1215-5_0_3_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_1215-5_0_3_node_106 | 0.4 | n |  | TRUE
108 | bus_LV_1215-5_0_3_node_107 | 0.4 | n |  | TRUE
109 | bus_LV_1215-5_0_3_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_1215-5_0_3_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_1215-5_0_3_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_1215-5_0_3_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_1215-5_0_3_node_111 | 0.4 | n |  | TRUE
114 | bus_LV_1215-5_0_3_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_1215-5_0_3_node_114 | 0.4 | n |  | TRUE
116 | bus_MV_12_0_node_35 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1215-5_0_3_load_0 | 0 | 0.0059081 | 0.0014807 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1215-5_0_3_load_1 | 1 | 0.0016609 | 0.00041627 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1215-5_0_3_load_3 | 3 | 0.0028977 | 0.00072624 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1215-5_0_3_load_4 | 4 | 0.0026814 | 0.00067202 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1215-5_0_3_load_5 | 5 | 0.0057016 | 0.0014289 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1215-5_0_3_load_6 | 6 | 0.0022664 | 0.000568 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1215-5_0_3_load_7 | 7 | 0.0022504 | 0.00056401 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1215-5_0_3_load_8 | 8 | 0.010741 | 0.0026919 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1215-5_0_3_load_29 | 13 | 0.0024888 | 0.00062375 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1215-5_0_3_load_20 | 15 | 0.0032012 | 0.0008023 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1215-5_0_3_load_9 | 16 | 0.0014655 | 0.0003673 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1215-5_0_3_load_10 | 17 | 0.0028642 | 0.00071783 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1215-5_0_3_load_11 | 18 | 0.002701 | 0.00067694 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1215-5_0_3_load_14 | 20 | 0.0019655 | 0.0004926 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1215-5_0_3_load_17 | 22 | 0.0016276 | 0.00040792 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1215-5_0_3_load_41 | 23 | 0.0022678 | 0.00056836 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1215-5_0_3_load_32 | 25 | 0.0016419 | 0.0004115 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1215-5_0_3_load_26 | 26 | 0.0027203 | 0.00068178 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1215-5_0_3_load_42 | 27 | 0.0024341 | 0.00061005 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1215-5_0_3_load_24 | 28 | 0.0033058 | 0.00082852 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1215-5_0_3_load_33 | 29 | 0.010582 | 0.0026522 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1215-5_0_3_load_39 | 30 | 0.0059124 | 0.0014818 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1215-5_0_3_load_19 | 31 | 0.0040612 | 0.0010178 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1215-5_0_3_load_23 | 33 | 0.0010003 | 0.00025069 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1215-5_0_3_load_91 | 35 | 0.0010511 | 0.00026342 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1215-5_0_3_load_30 | 36 | 0.0023362 | 0.00058552 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1215-5_0_3_load_31 | 37 | 0.0008563 | 0.00021461 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1215-5_0_3_load_92 | 38 | 0.002591 | 0.00064937 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1215-5_0_3_load_40 | 39 | 0.0048713 | 0.0012209 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1215-5_0_3_load_35 | 40 | 0.0024058 | 0.00060296 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1215-5_0_3_load_36 | 41 | 0.0028827 | 0.00072247 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1215-5_0_3_load_37 | 42 | 0.0016399 | 0.00041099 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1215-5_0_3_load_44 | 43 | 0.0033491 | 0.00083936 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1215-5_0_3_load_48 | 44 | 0.0070799 | 0.0017744 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1215-5_0_3_load_38 | 45 | 0.0020855 | 0.00052266 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1215-5_0_3_load_34 | 46 | 0.0011101 | 0.00027822 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1215-5_0_3_load_79 | 48 | 0.0032464 | 0.00081362 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1215-5_0_3_load_86 | 49 | 0.0028931 | 0.00072507 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1215-5_0_3_load_61 | 52 | 0.0018461 | 0.00046268 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1215-5_0_3_load_62 | 53 | 0.0032637 | 0.00081796 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1215-5_0_3_load_63 | 54 | 0.0030564 | 0.000766 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1215-5_0_3_load_47 | 56 | 0.0072804 | 0.0018246 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1215-5_0_3_load_83 | 57 | 0.0033837 | 0.00084803 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1215-5_0_3_load_75 | 58 | 0.0028987 | 0.00072649 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1215-5_0_3_load_84 | 59 | 0.0028902 | 0.00072435 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1215-5_0_3_load_51 | 60 | 0.001972 | 0.00049422 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1215-5_0_3_load_73 | 61 | 0.00065993 | 0.00016539 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1215-5_0_3_load_85 | 62 | 0.00046009 | 0.00011531 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1215-5_0_3_load_50 | 63 | 0.0035026 | 0.00087784 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1215-5_0_3_load_52 | 64 | 0.0032784 | 0.00082164 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1215-5_0_3_load_55 | 67 | 0.00087875 | 0.00022023 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1215-5_0_3_load_82 | 69 | 0.00076984 | 0.00019294 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1215-5_0_3_load_59 | 71 | 0.0014435 | 0.00036178 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1215-5_0_3_load_66 | 72 | 0.0048371 | 0.0012123 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1215-5_0_3_load_67 | 73 | 0.0030251 | 0.00075815 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1215-5_0_3_load_81 | 74 | 0.0004765 | 0.00011942 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1215-5_0_3_load_64 | 76 | 0.0020162 | 0.00050531 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1215-5_0_3_load_70 | 77 | 0.0034803 | 0.00087224 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1215-5_0_3_load_65 | 78 | 0.0058809 | 0.0014739 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1215-5_0_3_load_71 | 79 | 0.00089929 | 0.00022538 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1215-5_0_3_load_69 | 80 | 0.0013245 | 0.00033195 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1215-5_0_3_load_78 | 81 | 0.0042479 | 0.0010646 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1215-5_0_3_load_76 | 82 | 0.0022286 | 0.00055853 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1215-5_0_3_load_72 | 84 | 0.0080109 | 0.0020077 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1215-5_0_3_load_77 | 86 | 0.00045922 | 0.00011509 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1215-5_0_3_load_87 | 87 | 0.0028429 | 0.0007125 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1215-5_0_3_load_96 | 88 | 0.00096309 | 0.00024137 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1215-5_0_3_load_95 | 89 | 0.0007229 | 0.00018117 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1215-5_0_3_load_88 | 90 | 0.0035022 | 0.00087772 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1215-5_0_3_load_89 | 91 | 0.0044925 | 0.0011259 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1215-5_0_3_load_90 | 92 | 0.0013172 | 0.00033013 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1215-5_0_3_load_115 | 93 | 0.0014442 | 0.00036196 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1215-5_0_3_load_116 | 94 | 0.00098988 | 0.00024809 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1215-5_0_3_load_109 | 95 | 0.0023845 | 0.00059761 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1215-5_0_3_load_117 | 96 | 0.0012609 | 0.000316 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1215-5_0_3_load_118 | 98 | 0.00099915 | 0.00025041 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1215-5_0_3_load_94 | 100 | 0.00081594 | 0.00020449 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1215-5_0_3_load_97 | 102 | 0.00061349 | 0.00015375 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1215-5_0_3_load_98 | 103 | 0.00072521 | 0.00018175 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1215-5_0_3_load_101 | 104 | 0.0021912 | 0.00054917 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1215-5_0_3_load_105 | 106 | 0.0014664 | 0.00036753 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1215-5_0_3_load_106 | 107 | 0.0072845 | 0.0018257 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1215-5_0_3_load_107 | 108 | 0.0007668 | 0.00019218 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1215-5_0_3_load_108 | 111 | 0.0025526 | 0.00063973 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1215-5_0_3_load_110 | 112 | 0.0017362 | 0.00043514 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1215-5_0_3_load_111 | 113 | 0.00075646 | 0.00018959 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1215-5_0_3_load_112 | 114 | 0.0015873 | 0.00039781 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1215-5_0_3_load_114 | 115 | 0.00059359 | 0.00014877 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1215-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1215-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0090087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_1215-5_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0005949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1215-5_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.026627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1215-5_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.025716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1215-5_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.016271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1215-5_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.026349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1215-5_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.030008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1215-5_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.0097648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1215-5_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.0063608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1215-5_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.0074327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1215-5_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.003371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1215-5_0_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.0093537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1215-5_0_3_line_13 | NAYY 4x150 SE | 10 | 14 | 0.009927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1215-5_0_3_line_14 | NAYY 4x150 SE | 11 | 15 | 0.01877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1215-5_0_3_line_15 | NAYY 4x150 SE | 12 | 40 | 0.0059451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1215-5_0_3_line_16 | NAYY 4x150 SE | 12 | 41 | 0.0091587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1215-5_0_3_line_17 | NAYY 4x150 SE | 13 | 42 | 0.026619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1215-5_0_3_line_18 | NAYY 4x150 SE | 14 | 22 | 0.04764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1215-5_0_3_line_19 | NAYY 4x150 SE | 14 | 18 | 0.0083055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1215-5_0_3_line_20 | NAYY 4x150 SE | 15 | 31 | 0.0017147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1215-5_0_3_line_21 | NAYY 4x150 SE | 16 | 17 | 0.0187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1215-5_0_3_line_22 | NAYY 4x150 SE | 16 | 18 | 0.014431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1215-5_0_3_line_23 | NAYY 4x150 SE | 17 | 19 | 0.030925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1215-5_0_3_line_24 | NAYY 4x150 SE | 19 | 20 | 0.0069201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1215-5_0_3_line_25 | NAYY 4x150 SE | 19 | 21 | 0.043857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1215-5_0_3_line_26 | NAYY 4x150 SE | 20 | 23 | 0.030602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1215-5_0_3_line_27 | NAYY 4x150 SE | 21 | 24 | 0.034291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1215-5_0_3_line_28 | NAYY 4x150 SE | 21 | 25 | 0.015325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1215-5_0_3_line_29 | NAYY 4x150 SE | 22 | 26 | 0.0031483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1215-5_0_3_line_30 | NAYY 4x150 SE | 23 | 27 | 0.047517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1215-5_0_3_line_31 | NAYY 4x150 SE | 24 | 28 | 0.0065111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1215-5_0_3_line_32 | NAYY 4x150 SE | 25 | 29 | 0.0034317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1215-5_0_3_line_33 | NAYY 4x150 SE | 26 | 30 | 0.035061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1215-5_0_3_line_34 | NAYY 4x150 SE | 27 | 50 | 0.022794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1215-5_0_3_line_35 | NAYY 4x150 SE | 28 | 35 | 0.026618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1215-5_0_3_line_36 | NAYY 4x150 SE | 29 | 46 | 0.014407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1215-5_0_3_line_37 | NAYY 4x150 SE | 30 | 39 | 0.021163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1215-5_0_3_line_38 | NAYY 4x150 SE | 31 | 32 | 0.023462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1215-5_0_3_line_39 | NAYY 4x150 SE | 32 | 33 | 0.036083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1215-5_0_3_line_40 | NAYY 4x150 SE | 33 | 34 | 0.056801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1215-5_0_3_line_41 | NAYY 4x150 SE | 34 | 36 | 0.029514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1215-5_0_3_line_42 | NAYY 4x150 SE | 34 | 37 | 0.036518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1215-5_0_3_line_43 | NAYY 4x150 SE | 35 | 38 | 0.028372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1215-5_0_3_line_44 | NAYY 4x150 SE | 39 | 48 | 0.024694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1215-5_0_3_line_45 | NAYY 4x150 SE | 40 | 43 | 0.026622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1215-5_0_3_line_46 | NAYY 4x150 SE | 41 | 44 | 0.023709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1215-5_0_3_line_47 | NAYY 4x150 SE | 42 | 45 | 0.038163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1215-5_0_3_line_48 | NAYY 4x150 SE | 44 | 47 | 0.022308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1215-5_0_3_line_49 | NAYY 4x150 SE | 47 | 63 | 0.013257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1215-5_0_3_line_50 | NAYY 4x150 SE | 48 | 49 | 0.020747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1215-5_0_3_line_51 | NAYY 4x150 SE | 49 | 87 | 0.01399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1215-5_0_3_line_52 | NAYY 4x150 SE | 50 | 51 | 0.009452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1215-5_0_3_line_53 | NAYY 4x150 SE | 50 | 52 | 0.059397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1215-5_0_3_line_54 | NAYY 4x150 SE | 51 | 53 | 0.021288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1215-5_0_3_line_55 | NAYY 4x150 SE | 52 | 54 | 0.039005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1215-5_0_3_line_56 | NAYY 4x150 SE | 53 | 76 | 0.011306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1215-5_0_3_line_57 | NAYY 4x150 SE | 54 | 77 | 0.012525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1215-5_0_3_line_58 | NAYY 4x150 SE | 55 | 56 | 0.050853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_1215-5_0_3_line_59 | NAYY 4x150 SE | 55 | 57 | 0.041363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1215-5_0_3_line_60 | NAYY 4x150 SE | 56 | 58 | 0.024743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1215-5_0_3_line_61 | NAYY 4x150 SE | 57 | 59 | 0.060052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1215-5_0_3_line_62 | NAYY 4x150 SE | 57 | 60 | 0.030357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_1215-5_0_3_line_63 | NAYY 4x150 SE | 58 | 61 | 0.0075283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_1215-5_0_3_line_64 | NAYY 4x150 SE | 59 | 62 | 0.017168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1215-5_0_3_line_65 | NAYY 4x150 SE | 60 | 63 | 0.034945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_1215-5_0_3_line_66 | NAYY 4x150 SE | 61 | 84 | 0.024071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_1215-5_0_3_line_67 | NAYY 4x150 SE | 64 | 65 | 0.012316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1215-5_0_3_line_68 | NAYY 4x150 SE | 64 | 66 | 0.025243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1215-5_0_3_line_69 | NAYY 4x150 SE | 65 | 67 | 0.038062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1215-5_0_3_line_70 | NAYY 4x150 SE | 66 | 68 | 0.001813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1215-5_0_3_line_71 | NAYY 4x150 SE | 68 | 71 | 0.050535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1215-5_0_3_line_72 | NAYY 4x150 SE | 69 | 70 | 0.0068033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1215-5_0_3_line_73 | NAYY 4x150 SE | 70 | 74 | 0.033651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_1215-5_0_3_line_74 | NAYY 4x150 SE | 70 | 75 | 0.058022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_1215-5_0_3_line_75 | NAYY 4x150 SE | 71 | 72 | 0.023612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1215-5_0_3_line_76 | NAYY 4x150 SE | 72 | 73 | 0.028192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1215-5_0_3_line_77 | NAYY 4x150 SE | 73 | 75 | 0.0084326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1215-5_0_3_line_78 | NAYY 4x150 SE | 74 | 83 | 0.0255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_1215-5_0_3_line_79 | NAYY 4x150 SE | 75 | 80 | 0.03212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_1215-5_0_3_line_80 | NAYY 4x150 SE | 76 | 78 | 0.022871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1215-5_0_3_line_81 | NAYY 4x150 SE | 77 | 79 | 0.029377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1215-5_0_3_line_82 | NAYY 4x150 SE | 80 | 81 | 0.020738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1215-5_0_3_line_83 | NAYY 4x150 SE | 81 | 82 | 0.00080496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_1215-5_0_3_line_84 | NAYY 4x150 SE | 82 | 85 | 0.015982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_1215-5_0_3_line_85 | NAYY 4x150 SE | 83 | 88 | 0.015218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_1215-5_0_3_line_86 | NAYY 4x150 SE | 83 | 89 | 0.053621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1215-5_0_3_line_87 | NAYY 4x150 SE | 84 | 85 | 0.026481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1215-5_0_3_line_88 | NAYY 4x150 SE | 85 | 86 | 0.0011739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1215-5_0_3_line_89 | NAYY 4x150 SE | 87 | 90 | 0.028557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1215-5_0_3_line_90 | NAYY 4x150 SE | 88 | 99 | 0.041847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1215-5_0_3_line_91 | NAYY 4x150 SE | 89 | 100 | 0.00034084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1215-5_0_3_line_92 | NAYY 4x150 SE | 90 | 91 | 0.03734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1215-5_0_3_line_93 | NAYY 4x150 SE | 91 | 92 | 0.022772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1215-5_0_3_line_94 | NAYY 4x150 SE | 92 | 96 | 0.012107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1215-5_0_3_line_95 | NAYY 4x150 SE | 93 | 94 | 0.036955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1215-5_0_3_line_96 | NAYY 4x150 SE | 93 | 95 | 0.013256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1215-5_0_3_line_97 | NAYY 4x150 SE | 94 | 97 | 0.075332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1215-5_0_3_line_98 | NAYY 4x150 SE | 95 | 110 | 0.036511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1215-5_0_3_line_99 | NAYY 4x150 SE | 96 | 98 | 0.016367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1215-5_0_3_line_100 | NAYY 4x150 SE | 97 | 115 | 0.034076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1215-5_0_3_line_101 | NAYY 4x150 SE | 97 | 114 | 0.073399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1215-5_0_3_line_102 | NAYY 4x150 SE | 99 | 101 | 0.004701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_1215-5_0_3_line_103 | NAYY 4x150 SE | 101 | 104 | 0.014713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_1215-5_0_3_line_104 | NAYY 4x150 SE | 101 | 103 | 0.013579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1215-5_0_3_line_105 | NAYY 4x150 SE | 102 | 103 | 0.053614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1215-5_0_3_line_106 | NAYY 4x150 SE | 104 | 105 | 0.066902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_1215-5_0_3_line_107 | NAYY 4x150 SE | 105 | 106 | 0.089391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_1215-5_0_3_line_108 | NAYY 4x150 SE | 106 | 107 | 0.007033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_1215-5_0_3_line_109 | NAYY 4x150 SE | 107 | 108 | 0.13487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_1215-5_0_3_line_110 | NAYY 4x150 SE | 108 | 111 | 0.0019919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1215-5_0_3_line_111 | NAYY 4x150 SE | 108 | 109 | 0.13151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_1215-5_0_3_line_112 | NAYY 4x150 SE | 109 | 110 | 0.016956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1215-5_0_3_line_113 | NAYY 4x150 SE | 112 | 113 | 0.027589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1215-5_0_3_line_114 | NAYY 4x150 SE | 113 | 114 | 0.0086828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1215-5_0_3_trafo_38 | 0.25 MVA 20/0.4 kV | 116 | 45 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2687224.8456 | 1202482.2203 | 2687238.0901 | 1202497.4662
1 | 2687218.9375 | 1202475.4194 | 2687224.8456 | 1202482.2203
2 | 2687238.0901 | 1202497.4662 | 2687238.4802 | 1202497.9153
3 | 2687218.9375 | 1202475.4194 | 2687202.0447 | 1202454.8373
4 | 2687218.9375 | 1202475.4194 | 2687219.2478 | 1202465.6398 | 2687216.1915 | 1202456.0335 | 2687216.4702 | 1202450.1893
5 | 2687249.1509 | 1202510.1985 | 2687238.4802 | 1202497.9153
6 | 2687202.0447 | 1202454.8373 | 2687202.0447 | 1202454.8373 | 2687191.7434 | 1202441.0003 | 2687186.4492 | 1202433.6007
7 | 2687217.8998 | 1202420.2154 | 2687216.4702 | 1202450.1893
8 | 2687255.5549 | 1202517.5701 | 2687249.1509 | 1202510.1985
9 | 2687182.748 | 1202428.4276 | 2687186.4492 | 1202433.6007
10 | 2687218.254 | 1202412.7912 | 2687217.8998 | 1202420.2154
11 | 2687255.5549 | 1202517.5701 | 2687257.6935 | 1202520.1808
12 | 2687255.5549 | 1202517.5701 | 2687250.51 | 1202518.5304 | 2687247.6694 | 1202515.412
13 | 2687177.3671 | 1202420.077 | 2687182.748 | 1202428.4276
14 | 2687218.254 | 1202412.7912 | 2687218.2675 | 1202397.2703 | 2687218.0757 | 1202394.0271
15 | 2687257.6935 | 1202520.1808 | 2687263.1618 | 1202517.8481
16 | 2687257.6935 | 1202520.1808 | 2687263.1536 | 1202527.5339
17 | 2687232.357 | 1202525.5136 | 2687234.0282 | 1202524.527 | 2687235.1239 | 1202523.509 | 2687235.4838 | 1202522.3135 | 2687235.8904 | 1202517.9277 | 2687236.7836 | 1202514.6164 | 2687241.4772 | 1202511.1382 | 2687243.4686 | 1202510.8004 | 2687247.6694 | 1202515.412
18 | 2687177.3671 | 1202420.077 | 2687166.9322 | 1202422.682 | 2687130.0962 | 1202424.5762
19 | 2687177.3671 | 1202420.077 | 2687173.1169 | 1202412.9414
20 | 2687217.9744 | 1202392.3154 | 2687218.0757 | 1202394.0271
21 | 2687165.7318 | 1202400.5429 | 2687156.1623 | 1202384.4768
22 | 2687165.7318 | 1202400.5429 | 2687173.1169 | 1202412.9414
23 | 2687139.9334 | 1202358.1576 | 2687147.4649 | 1202369.875 | 2687156.1623 | 1202384.4768
24 | 2687139.9334 | 1202358.1576 | 2687134.7886 | 1202353.5295
25 | 2687139.9334 | 1202358.1576 | 2687148.6072 | 1202352.1024 | 2687157.8707 | 1202347.3678 | 2687179.9161 | 1202340.8853
26 | 2687134.7886 | 1202353.5295 | 2687126.5535 | 1202346.1214 | 2687115.6824 | 1202340.5371 | 2687108.6146 | 1202338.6955
27 | 2687210.6377 | 1202326.1129 | 2687201.5745 | 1202332.2402 | 2687191.3056 | 1202337.5493 | 2687179.9161 | 1202340.8853
28 | 2687179.9161 | 1202340.8853 | 2687187.1965 | 1202354.3701
29 | 2687130.0962 | 1202424.5762 | 2687126.9521 | 1202424.7379
30 | 2687061.8523 | 1202330.8574 | 2687061.8523 | 1202330.8574 | 2687092.3589 | 1202334.4598 | 2687108.6146 | 1202338.6955
31 | 2687210.6377 | 1202326.1129 | 2687215.4903 | 1202321.7717
32 | 2687187.1965 | 1202354.3701 | 2687188.8268 | 1202357.3898
33 | 2687126.9521 | 1202424.7379 | 2687118.4282 | 1202425.1762 | 2687100.6788 | 1202424.6727 | 2687092.0692 | 1202426.3371
34 | 2687039.6575 | 1202325.664 | 2687061.8523 | 1202330.8574
35 | 2687231.7483 | 1202300.8441 | 2687227.6334 | 1202307.3711 | 2687219.1363 | 1202318.5099 | 2687215.4903 | 1202321.7717
36 | 2687188.8268 | 1202357.3898 | 2687195.6715 | 1202370.0673
37 | 2687092.0692 | 1202426.3371 | 2687092.0692 | 1202426.3371 | 2687073.2721 | 1202434.0015 | 2687072.4369 | 1202434.2215
38 | 2687216.5889 | 1202368.8941 | 2687217.9744 | 1202392.3154
39 | 2687216.5889 | 1202368.8941 | 2687222.988 | 1202364.3401 | 2687242.473 | 1202353.8956 | 2687247.5137 | 1202350.422
40 | 2687292.7423 | 1202316.6057 | 2687288.8434 | 1202321.9411 | 2687247.5137 | 1202350.422
41 | 2687292.7423 | 1202316.6057 | 2687322.2018 | 1202313.7343
42 | 2687292.7423 | 1202316.6057 | 2687314.2853 | 1202287.1189
43 | 2687231.7483 | 1202300.8441 | 2687235.3707 | 1202295.0984 | 2687239.6196 | 1202278.3051 | 2687240.3369 | 1202274.1091
44 | 2687048.2838 | 1202438.9916 | 2687051.5329 | 1202437.7871 | 2687067.9926 | 1202435.3921 | 2687072.4369 | 1202434.2215
45 | 2687287.1088 | 1202527.4198 | 2687281.1106 | 1202523.4361 | 2687265.8148 | 1202520.6775 | 2687263.1618 | 1202517.8481
46 | 2687263.1536 | 1202527.5339 | 2687277.2883 | 1202546.5689
47 | 2687232.357 | 1202525.5136 | 2687222.5048 | 1202531.3298 | 2687206.6516 | 1202550.0549 | 2687204.4652 | 1202550.1319
48 | 2687290.5876 | 1202564.4788 | 2687277.2883 | 1202546.5689
49 | 2687290.5876 | 1202564.4788 | 2687292.6639 | 1202577.5725
50 | 2687028.2506 | 1202443.7757 | 2687038.5467 | 1202442.6011 | 2687048.2838 | 1202438.9916
51 | 2687028.2506 | 1202443.7757 | 2687019.9675 | 1202444.7207 | 2687014.3195 | 1202444.9576
52 | 2687030.8331 | 1202322.211 | 2687039.6575 | 1202325.664
53 | 2687039.6575 | 1202325.664 | 2687041.7466 | 1202321.236 | 2687062.0495 | 1202284.964 | 2687067.6767 | 1202273.3194
54 | 2687030.8331 | 1202322.211 | 2687029.3562 | 1202324.8468 | 2687027.0488 | 1202326.492 | 2687012.1378 | 1202330.4699
55 | 2687082.7307 | 1202237.3791 | 2687079.2921 | 1202247.1797 | 2687073.8138 | 1202260.6197 | 2687067.6767 | 1202273.3194
56 | 2687001.8663 | 1202335.1183 | 2687010.254 | 1202330.9725 | 2687012.1378 | 1202330.4699
57 | 2687082.7307 | 1202237.3791 | 2687082.7307 | 1202237.3791 | 2687083.1166 | 1202233.8824 | 2687082.7331 | 1202231.4753 | 2687080.7707 | 1202226.6881 | 2687080.1498 | 1202225.4384
58 | 2687317.6712 | 1202663.105 | 2687320.3539 | 1202707.6063 | 2687321.4547 | 1202713.78
59 | 2687284.4927 | 1202638.4048 | 2687317.6712 | 1202663.105
60 | 2687321.4547 | 1202713.78 | 2687325.7981 | 1202738.1389 | 2687325.7981 | 1202738.1389
61 | 2687284.4927 | 1202638.4048 | 2687256.1058 | 1202691.3238 | 2687256.1058 | 1202691.3238
62 | 2687284.4927 | 1202638.4048 | 2687292.2215 | 1202623.9967 | 2687297.4596 | 1202617.1021 | 2687298.1226 | 1202611.7956
63 | 2687325.7981 | 1202738.1389 | 2687328.0323 | 1202745.328
64 | 2687256.1058 | 1202691.3238 | 2687252.7598 | 1202698.9465 | 2687253.7232 | 1202707.7371
65 | 2687298.1226 | 1202611.7956 | 2687298.8129 | 1202606.2704 | 2687296.8081 | 1202594.5113 | 2687293.0475 | 1202579.9914 | 2687292.6639 | 1202577.5725
66 | 2687335.5197 | 1202768.1962 | 2687333.452 | 1202762.7667 | 2687328.0323 | 1202745.328
67 | 2687405.9489 | 1202984.9373 | 2687403.1929 | 1202972.9332
68 | 2687398.404 | 1202948.2254 | 2687398.4727 | 1202952.3735 | 2687403.1929 | 1202972.9332
69 | 2687405.9489 | 1202984.9373 | 2687400.8281 | 1202988.5091 | 2687394.633 | 1202993.1993 | 2687390.229 | 1203000.3173 | 2687383.9193 | 1203014.6692
70 | 2687398.404 | 1202948.2254 | 2687397.8662 | 1202946.4942
71 | 2687397.8662 | 1202946.4942 | 2687388.4852 | 1202918.2275 | 2687379.8745 | 1202907.0054 | 2687375.0242 | 1202902.5183
72 | 2687304.6755 | 1202904.3711 | 2687304.8467 | 1202910.8778 | 2687304.9688 | 1202911.1456
73 | 2687304.6755 | 1202904.3711 | 2687302.595 | 1202898.3145 | 2687299.0327 | 1202894.1931 | 2687290.1686 | 1202889.3605 | 2687285.7962 | 1202886.5059 | 2687280.9034 | 1202882.2545
74 | 2687304.6755 | 1202904.3711 | 2687342.6318 | 1202860.4863
75 | 2687361.7761 | 1202883.5922 | 2687366.5763 | 1202894.703 | 2687375.0242 | 1202902.5183
76 | 2687361.7761 | 1202883.5922 | 2687350.595 | 1202857.7121
77 | 2687342.6318 | 1202860.4863 | 2687350.595 | 1202857.7121
78 | 2687260.9978 | 1202866.4196 | 2687266.8732 | 1202870.0633 | 2687280.9034 | 1202882.2545
79 | 2687342.6318 | 1202860.4863 | 2687342.3515 | 1202851.5542 | 2687342.3499 | 1202839.1795 | 2687342.5487 | 1202828.709 | 2687342.5985 | 1202828.3765
80 | 2686980.2603 | 1202342.3209 | 2686995.5268 | 1202338.2517 | 2687001.8663 | 1202335.1183
81 | 2687072.2446 | 1202197.545 | 2687073.4271 | 1202208.8473 | 2687074.6999 | 1202214.4695 | 2687080.1498 | 1202225.4384
82 | 2687342.5985 | 1202828.3765 | 2687344.0163 | 1202818.913 | 2687344.1197 | 1202811.8433 | 2687343.2245 | 1202807.844
83 | 2687343.2245 | 1202807.844 | 2687343.0487 | 1202807.0585
84 | 2687344.9441 | 1202792.9431 | 2687341.7653 | 1202795.376 | 2687341.0836 | 1202798.279 | 2687343.0487 | 1202807.0585
85 | 2687260.9978 | 1202866.4196 | 2687247.3201 | 1202859.7488
86 | 2687260.9978 | 1202866.4196 | 2687261.9536 | 1202876.0064 | 2687261.714 | 1202882.5071 | 2687258.2417 | 1202892.007 | 2687256.4901 | 1202895.7393 | 2687258.0746 | 1202908.6486 | 2687256.0434 | 1202918.6831
87 | 2687344.9441 | 1202792.9431 | 2687335.5197 | 1202768.1962
88 | 2687344.9441 | 1202792.9431 | 2687345.5203 | 1202793.9659
89 | 2687014.3195 | 1202444.9576 | 2687003.8374 | 1202445.3974 | 2686986.4068 | 1202440.6485
90 | 2687214.6628 | 1202833.7219 | 2687237.7288 | 1202853.6381 | 2687247.3201 | 1202859.7488
91 | 2687256.0434 | 1202918.6831 | 2687255.9758 | 1202919.0171
92 | 2686986.4068 | 1202440.6485 | 2686960.9819 | 1202433.7215 | 2686951.0187 | 1202429.0876
93 | 2686928.9982 | 1202423.8223 | 2686939.8054 | 1202425.5192 | 2686946.6937 | 1202427.0759 | 2686951.0187 | 1202429.0876
94 | 2686928.9982 | 1202423.8223 | 2686921.8538 | 1202422.7006 | 2686917.2943 | 1202420.9752
95 | 2686942.0486 | 1202613.5328 | 2686934.4716 | 1202603.1562 | 2686918.1895 | 1202585.3789
96 | 2686942.0486 | 1202613.5328 | 2686949.8658 | 1202624.2382
97 | 2686918.1895 | 1202585.3789 | 2686845.3644 | 1202604.6502
98 | 2686967.9515 | 1202655.9553 | 2686949.8658 | 1202624.2382 | 2686949.8658 | 1202624.2382
99 | 2686903.1713 | 1202412.9685 | 2686911.0674 | 1202418.6188 | 2686917.2943 | 1202420.9752
100 | 2686845.3644 | 1202604.6502 | 2686817.6904 | 1202584.7667
101 | 2686845.3644 | 1202604.6502 | 2686842.5521 | 1202614.8603 | 2686851.0231 | 1202632.6394 | 2686875.8093 | 1202664.7093 | 2686877.1374 | 1202666.924
102 | 2687214.6628 | 1202833.7219 | 2687211.3555 | 1202830.3714
103 | 2687211.3555 | 1202830.3714 | 2687201.0287 | 1202819.8917
104 | 2687211.3555 | 1202830.3714 | 2687203.7601 | 1202841.6278
105 | 2687203.3726 | 1202891.1671 | 2687206.0914 | 1202884.9187 | 2687208.1535 | 1202863.5795 | 2687199.6326 | 1202847.7449 | 2687203.7601 | 1202841.6278
106 | 2687174.685 | 1202762.2589 | 2687183.4897 | 1202765.445 | 2687187.0892 | 1202771.7238 | 2687191.5839 | 1202794.3596 | 2687201.0287 | 1202819.8917
107 | 2687174.685 | 1202762.2589 | 2687123.714 | 1202688.8238
108 | 2687118.2228 | 1202684.4295 | 2687123.714 | 1202688.8238
109 | 2687118.2228 | 1202684.4295 | 2687030.6612 | 1202787.0067
110 | 2687031.9595 | 1202788.5173 | 2687030.6612 | 1202787.0067
111 | 2686982.583 | 1202664.5961 | 2687030.6612 | 1202787.0067
112 | 2686967.9515 | 1202655.9553 | 2686982.583 | 1202664.5961
113 | 2686895.4417 | 1202698.2263 | 2686892.5502 | 1202692.6263 | 2686881.6028 | 1202674.3705
114 | 2686877.1374 | 1202666.924 | 2686881.6028 | 1202674.3705

## bus_geodata
| x | y | coords
0 | 2687224.8456 | 1202482.2203
1 | 2687238.0901 | 1202497.4662
2 | 2687218.9375 | 1202475.4194
3 | 2687238.4802 | 1202497.9153
4 | 2687202.0447 | 1202454.8373
5 | 2687216.4702 | 1202450.1893
6 | 2687249.1509 | 1202510.1985
7 | 2687186.4492 | 1202433.6007
8 | 2687217.8998 | 1202420.2154
9 | 2687255.5549 | 1202517.5701
10 | 2687182.748 | 1202428.4276
11 | 2687218.254 | 1202412.7912
12 | 2687257.6935 | 1202520.1808
13 | 2687247.6694 | 1202515.412
14 | 2687177.3671 | 1202420.077
15 | 2687218.0757 | 1202394.0271
16 | 2687165.7318 | 1202400.5429
17 | 2687156.1623 | 1202384.4768
18 | 2687173.1169 | 1202412.9414
19 | 2687139.9334 | 1202358.1576
20 | 2687134.7886 | 1202353.5295
21 | 2687179.9161 | 1202340.8853
22 | 2687130.0962 | 1202424.5762
23 | 2687108.6146 | 1202338.6955
24 | 2687210.6377 | 1202326.1129
25 | 2687187.1965 | 1202354.3701
26 | 2687126.9521 | 1202424.7379
27 | 2687061.8523 | 1202330.8574
28 | 2687215.4903 | 1202321.7717
29 | 2687188.8268 | 1202357.3898
30 | 2687092.0692 | 1202426.3371
31 | 2687217.9744 | 1202392.3154
32 | 2687216.5889 | 1202368.8941
33 | 2687247.5137 | 1202350.422
34 | 2687292.7423 | 1202316.6057
35 | 2687231.7483 | 1202300.8441
36 | 2687322.2018 | 1202313.7343
37 | 2687314.2853 | 1202287.1189
38 | 2687240.3369 | 1202274.1091
39 | 2687072.4369 | 1202434.2215
40 | 2687263.1618 | 1202517.8481
41 | 2687263.1536 | 1202527.5339
42 | 2687232.357 | 1202525.5136
43 | 2687287.1088 | 1202527.4198
44 | 2687277.2883 | 1202546.5689
45 | 2687204.4652 | 1202550.1319
46 | 2687195.6715 | 1202370.0673
47 | 2687290.5876 | 1202564.4788
48 | 2687048.2838 | 1202438.9916
49 | 2687028.2506 | 1202443.7757
50 | 2687039.6575 | 1202325.664
51 | 2687030.8331 | 1202322.211
52 | 2687067.6767 | 1202273.3194
53 | 2687012.1378 | 1202330.4699
54 | 2687082.7307 | 1202237.3791
55 | 2687317.6712 | 1202663.105
56 | 2687321.4547 | 1202713.78
57 | 2687284.4927 | 1202638.4048
58 | 2687325.7981 | 1202738.1389
59 | 2687256.1058 | 1202691.3238
60 | 2687298.1226 | 1202611.7956
61 | 2687328.0323 | 1202745.328
62 | 2687253.7232 | 1202707.7371
63 | 2687292.6639 | 1202577.5725
64 | 2687403.1929 | 1202972.9332
65 | 2687405.9489 | 1202984.9373
66 | 2687398.404 | 1202948.2254
67 | 2687383.9193 | 1203014.6692
68 | 2687397.8662 | 1202946.4942
69 | 2687304.9688 | 1202911.1456
70 | 2687304.6755 | 1202904.3711
71 | 2687375.0242 | 1202902.5183
72 | 2687361.7761 | 1202883.5922
73 | 2687350.595 | 1202857.7121
74 | 2687280.9034 | 1202882.2545
75 | 2687342.6318 | 1202860.4863
76 | 2687001.8663 | 1202335.1183
77 | 2687080.1498 | 1202225.4384
78 | 2686980.2603 | 1202342.3209
79 | 2687072.2446 | 1202197.545
80 | 2687342.5985 | 1202828.3765
81 | 2687343.2245 | 1202807.844
82 | 2687343.0487 | 1202807.0585
83 | 2687260.9978 | 1202866.4196
84 | 2687335.5197 | 1202768.1962
85 | 2687344.9441 | 1202792.9431
86 | 2687345.5203 | 1202793.9659
87 | 2687014.3195 | 1202444.9576
88 | 2687247.3201 | 1202859.7488
89 | 2687256.0434 | 1202918.6831
90 | 2686986.4068 | 1202440.6485
91 | 2686951.0187 | 1202429.0876
92 | 2686928.9982 | 1202423.8223
93 | 2686942.0486 | 1202613.5328
94 | 2686918.1895 | 1202585.3789
95 | 2686949.8658 | 1202624.2382
96 | 2686917.2943 | 1202420.9752
97 | 2686845.3644 | 1202604.6502
98 | 2686903.1713 | 1202412.9685
99 | 2687214.6628 | 1202833.7219
100 | 2687255.9758 | 1202919.0171
101 | 2687211.3555 | 1202830.3714
102 | 2687203.3726 | 1202891.1671
103 | 2687203.7601 | 1202841.6278
104 | 2687201.0287 | 1202819.8917
105 | 2687174.685 | 1202762.2589
106 | 2687123.714 | 1202688.8238
107 | 2687118.2228 | 1202684.4295
108 | 2687030.6612 | 1202787.0067
109 | 2686982.583 | 1202664.5961
110 | 2686967.9515 | 1202655.9553
111 | 2687031.9595 | 1202788.5173
112 | 2686895.4417 | 1202698.2263
113 | 2686881.6028 | 1202674.3705
114 | 2686877.1374 | 1202666.924
115 | 2686817.6904 | 1202584.7667
116 | 2687147.0704 | 1202545.5383

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98852 | -0.079814 | 0.0059081 | 0.0014807
1 | 0.98978 | -0.070958 | 0.0016609 | 0.00041627
2 | 0.98771 | -0.085479 | 0 | 0
3 | 0.98982 | -0.070694 | 0.0028977 | 0.00072624
4 | 0.98586 | -0.09846 | 0.0026814 | 0.00067202
5 | 0.98667 | -0.092833 | 0.0057016 | 0.0014289
6 | 0.99087 | -0.063324 | 0.0022664 | 0.000568
7 | 0.98408 | -0.11099 | 0.0022504 | 0.00056401
8 | 0.98571 | -0.099674 | 0.010741 | 0.0026919
9 | 0.99152 | -0.058834 | 0 | 0
10 | 0.98325 | -0.11691 | 0 | 0
11 | 0.98559 | -0.10055 | 0 | 0
12 | 0.99136 | -0.059949 | 0 | 0
13 | 0.99257 | -0.051451 | 0.0024888 | 0.00062375
14 | 0.98194 | -0.12616 | 0 | 0
15 | 0.98528 | -0.10276 | 0.0032012 | 0.0008023
16 | 0.98019 | -0.1386 | 0.0014655 | 0.0003673
17 | 0.97881 | -0.14839 | 0.0028642 | 0.00071783
18 | 0.98128 | -0.13085 | 0.002701 | 0.00067694
19 | 0.97666 | -0.1637 | 0 | 0
20 | 0.97639 | -0.16567 | 0.0019655 | 0.0004926
21 | 0.97536 | -0.17303 | 0 | 0
22 | 0.97946 | -0.14381 | 0.0016276 | 0.00040792
23 | 0.97526 | -0.17374 | 0.0022678 | 0.00056836
24 | 0.97502 | -0.17553 | 0 | 0
25 | 0.97507 | -0.17517 | 0.0016419 | 0.0004115
26 | 0.9793 | -0.14493 | 0.0027203 | 0.00068178
27 | 0.97367 | -0.18518 | 0.0024341 | 0.00061005
28 | 0.97495 | -0.17601 | 0.0033058 | 0.00082852
29 | 0.97501 | -0.17559 | 0.010582 | 0.0026522
30 | 0.9777 | -0.15639 | 0.0059124 | 0.0014818
31 | 0.98526 | -0.10291 | 0.0040612 | 0.0010178
32 | 0.98511 | -0.10393 | 0 | 0
33 | 0.98489 | -0.10549 | 0.0010003 | 0.00025069
34 | 0.98463 | -0.10736 | 0 | 0
35 | 0.97481 | -0.17702 | 0.0010511 | 0.00026342
36 | 0.98453 | -0.10807 | 0.0023362 | 0.00058552
37 | 0.98459 | -0.10768 | 0.0008563 | 0.00021461
38 | 0.9747 | -0.1778 | 0.002591 | 0.00064937
39 | 0.97691 | -0.16202 | 0.0048713 | 0.0012209
40 | 0.99131 | -0.060296 | 0.0024058 | 0.00060296
41 | 0.99095 | -0.0628 | 0.0028827 | 0.00072247
42 | 0.99561 | -0.030304 | 0.0016399 | 0.00041099
43 | 0.99118 | -0.061202 | 0.0033491 | 0.00083936
44 | 0.98993 | -0.06996 | 0.0070799 | 0.0017744
45 | 1 | 0 | -0.2426 | -0.061158
46 | 0.97498 | -0.17576 | 0.0011101 | 0.00027822
47 | 0.98905 | -0.076172 | 0 | 0
48 | 0.97617 | -0.16733 | 0.0032464 | 0.00081362
49 | 0.97564 | -0.1711 | 0.0028931 | 0.00072507
50 | 0.97299 | -0.19009 | 0 | 0
51 | 0.97283 | -0.1912 | 0 | 0
52 | 0.97218 | -0.19591 | 0.0018461 | 0.00046268
53 | 0.97248 | -0.19371 | 0.0032637 | 0.00081796
54 | 0.97175 | -0.19898 | 0.0030564 | 0.000766
55 | 0.98468 | -0.10703 | 0 | 0
56 | 0.98297 | -0.11921 | 0.0072804 | 0.0018246
57 | 0.98608 | -0.097146 | 0.0033837 | 0.00084803
58 | 0.98222 | -0.12453 | 0.0028987 | 0.00072649
59 | 0.98579 | -0.099215 | 0.0028902 | 0.00072435
60 | 0.9872 | -0.089214 | 0.001972 | 0.00049422
61 | 0.982 | -0.12607 | 0.00065993 | 0.00016539
62 | 0.98577 | -0.099296 | 0.00046009 | 0.00011531
63 | 0.98852 | -0.079869 | 0.0035026 | 0.00087784
64 | 0.9779 | -0.15543 | 0.0032784 | 0.00082164
65 | 0.97788 | -0.15554 | 0 | 0
66 | 0.97805 | -0.15433 | 0 | 0
67 | 0.97783 | -0.15589 | 0.00087875 | 0.00022023
68 | 0.97806 | -0.15426 | 0 | 0
69 | 0.97833 | -0.15233 | 0.00076984 | 0.00019294
70 | 0.97834 | -0.15228 | 0 | 0
71 | 0.97837 | -0.15206 | 0.0014435 | 0.00036178
72 | 0.97856 | -0.15068 | 0.0048371 | 0.0012123
73 | 0.97899 | -0.14761 | 0.0030251 | 0.00075815
74 | 0.97788 | -0.15559 | 0.0004765 | 0.00011942
75 | 0.97916 | -0.14642 | 0 | 0
76 | 0.97235 | -0.19465 | 0.0020162 | 0.00050531
77 | 0.97167 | -0.19956 | 0.0034803 | 0.00087224
78 | 0.97215 | -0.19607 | 0.0058809 | 0.0014739
79 | 0.97163 | -0.19984 | 0.00089929 | 0.00022538
80 | 0.97982 | -0.14169 | 0.0013245 | 0.00033195
81 | 0.98026 | -0.13853 | 0.0042479 | 0.0010646
82 | 0.98028 | -0.1384 | 0.0022286 | 0.00055853
83 | 0.97754 | -0.15805 | 0 | 0
84 | 0.98132 | -0.13096 | 0.0080109 | 0.0020077
85 | 0.98067 | -0.13562 | 0 | 0
86 | 0.98066 | -0.13562 | 0.00045922 | 0.00011509
87 | 0.97535 | -0.17322 | 0.0028429 | 0.0007125
88 | 0.97734 | -0.15944 | 0.00096309 | 0.00024137
89 | 0.97742 | -0.15891 | 0.0007229 | 0.00018117
90 | 0.97486 | -0.17669 | 0.0035022 | 0.00087772
91 | 0.97442 | -0.17986 | 0.0044925 | 0.0011259
92 | 0.9743 | -0.18071 | 0.0013172 | 0.00033013
93 | 0.97255 | -0.19397 | 0.0014442 | 0.00036196
94 | 0.97225 | -0.19618 | 0.00098988 | 0.00024809
95 | 0.97269 | -0.19297 | 0.0023845 | 0.00059761
96 | 0.97426 | -0.181 | 0.0012609 | 0.000316
97 | 0.97173 | -0.19992 | 0 | 0
98 | 0.97424 | -0.18117 | 0.00099915 | 0.00025041
99 | 0.97683 | -0.16312 | 0 | 0
100 | 0.97742 | -0.15892 | 0.00081594 | 0.00020449
101 | 0.97677 | -0.16354 | 0 | 0
102 | 0.9767 | -0.16407 | 0.00061349 | 0.00015375
103 | 0.97675 | -0.16373 | 0.00072521 | 0.00018175
104 | 0.9766 | -0.16476 | 0.0021912 | 0.00054917
105 | 0.9759 | -0.16983 | 0 | 0
106 | 0.97496 | -0.17661 | 0.0014664 | 0.00036753
107 | 0.97489 | -0.17711 | 0.0072845 | 0.0018257
108 | 0.97405 | -0.1832 | 0.0007668 | 0.00019218
109 | 0.97344 | -0.1876 | 0 | 0
110 | 0.9732 | -0.1893 | 0 | 0
111 | 0.97404 | -0.18325 | 0.0025526 | 0.00063973
112 | 0.97119 | -0.20382 | 0.0017362 | 0.00043514
113 | 0.97126 | -0.20332 | 0.00075646 | 0.00018959
114 | 0.97129 | -0.20309 | 0.0015873 | 0.00039781
115 | 0.9717 | -0.20013 | 0.00059359 | 0.00014877
116 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13013 | -0.032772 | 0.1303 | 0.032833 | 0.00016128 | 6.1255e-05 | 0.19595 | 0.19595 | 0.19595 | 0.98852 | -0.079814 | 0.98978 | -0.070958 | 24.191
1 | 0.12423 | 0.031291 | -0.12413 | -0.031253 | 9.8345e-05 | 3.7594e-05 | 0.18705 | 0.18705 | 0.18705 | 0.98852 | -0.079814 | 0.98771 | -0.085479 | 34.6396
2 | -0.13196 | -0.033249 | 0.13196 | 0.033251 | 4.8728e-06 | 1.8512e-06 | 0.19844 | 0.19844 | 0.19844 | 0.98978 | -0.070958 | 0.98982 | -0.070694 | 24.4993
3 | 0.096173 | 0.024243 | -0.095999 | -0.024176 | 0.00017452 | 6.6442e-05 | 0.14494 | 0.14494 | 0.14494 | 0.98771 | -0.085479 | 0.98586 | -0.09846 | 26.8403
4 | 0.027955 | 0.0070104 | -0.027926 | -0.0069998 | 2.8464e-05 | 1.0619e-05 | 0.042116 | 0.042116 | 0.042116 | 0.98771 | -0.085479 | 0.98667 | -0.092833 | 15.5986
5 | -0.13486 | -0.033977 | 0.135 | 0.03403 | 0.00013919 | 5.2907e-05 | 0.2028 | 0.2028 | 0.2028 | 0.98982 | -0.070694 | 0.99087 | -0.063324 | 25.0371
6 | 0.093317 | 0.023504 | -0.093154 | -0.023442 | 0.00016319 | 6.2093e-05 | 0.14089 | 0.14089 | 0.14089 | 0.98586 | -0.09846 | 0.98408 | -0.11099 | 26.0909
7 | 0.022225 | 0.0055708 | -0.022204 | -0.0055631 | 2.1036e-05 | 7.708e-06 | 0.033518 | 0.033518 | 0.033518 | 0.98667 | -0.092833 | 0.98571 | -0.099674 | 12.414
8 | -0.13726 | -0.034598 | 0.13735 | 0.034631 | 8.6361e-05 | 3.2838e-05 | 0.2062 | 0.2062 | 0.2062 | 0.99087 | -0.063324 | 0.99152 | -0.058834 | 25.4572
9 | 0.090904 | 0.022878 | -0.090829 | -0.02285 | 7.5029e-05 | 2.8776e-05 | 0.13749 | 0.13749 | 0.13749 | 0.98408 | -0.11099 | 0.98325 | -0.11691 | 50.9215
10 | 0.011463 | 0.0028712 | -0.011461 | -0.0028708 | 1.3887e-06 | 4.3938e-07 | 0.017304 | 0.017304 | 0.017304 | 0.98571 | -0.099674 | 0.98559 | -0.10055 | 6.4088
11 | 0.098342 | 0.024734 | -0.098327 | -0.024728 | 1.5279e-05 | 5.7462e-06 | 0.14762 | 0.14762 | 0.14762 | 0.99152 | -0.058834 | 0.99136 | -0.059949 | 18.2245
12 | -0.23569 | -0.059365 | 0.23594 | 0.059458 | 0.00024356 | 9.3316e-05 | 0.35382 | 0.35382 | 0.35382 | 0.99152 | -0.058834 | 0.99257 | -0.051451 | 43.6816
13 | 0.090829 | 0.02285 | -0.090712 | -0.022805 | 0.00011709 | 4.491e-05 | 0.13749 | 0.13749 | 0.13749 | 0.98325 | -0.11691 | 0.98194 | -0.12616 | 50.9216
14 | 0.011461 | 0.0028708 | -0.011458 | -0.0028697 | 3.5069e-06 | 1.1097e-06 | 0.017304 | 0.017304 | 0.017304 | 0.98559 | -0.10055 | 0.98528 | -0.10276 | 6.4088
15 | 0.0057556 | 0.0014422 | -0.0057553 | -0.0014421 | 2.7687e-07 | 2.9839e-08 | 0.008639 | 0.008639 | 0.008639 | 0.99136 | -0.059949 | 0.99131 | -0.060296 | 3.1996
16 | 0.092572 | 0.023286 | -0.092535 | -0.023272 | 3.6796e-05 | 1.3798e-05 | 0.13898 | 0.13898 | 0.13898 | 0.99136 | -0.059949 | 0.99095 | -0.0628 | 17.1579
17 | -0.23843 | -0.060082 | 0.23913 | 0.060353 | 0.00070783 | 0.00027121 | 0.35755 | 0.35755 | 0.35755 | 0.99257 | -0.051451 | 0.99561 | -0.030304 | 44.1423
18 | 0.035887 | 0.0090175 | -0.035799 | -0.0089843 | 8.7945e-05 | 3.3224e-05 | 0.054391 | 0.054391 | 0.054391 | 0.98194 | -0.12616 | 0.97946 | -0.14381 | 20.1449
19 | 0.054825 | 0.013787 | -0.054789 | -0.013774 | 3.5787e-05 | 1.3659e-05 | 0.083097 | 0.083097 | 0.083097 | 0.98194 | -0.12616 | 0.98128 | -0.13085 | 30.7768
20 | 0.0082568 | 0.0020674 | -0.0082566 | -0.0020673 | 1.6636e-07 | 4.2146e-08 | 0.012469 | 0.012469 | 0.012469 | 0.98528 | -0.10276 | 0.98526 | -0.10291 | 4.6182
21 | 0.050566 | 0.012708 | -0.050497 | -0.012682 | 6.8784e-05 | 2.622e-05 | 0.076777 | 0.076777 | 0.076777 | 0.98019 | -0.1386 | 0.97881 | -0.14839 | 28.4358
22 | -0.052032 | -0.013075 | 0.052088 | 0.013097 | 5.6203e-05 | 2.1434e-05 | 0.079002 | 0.079001 | 0.079002 | 0.98019 | -0.1386 | 0.98128 | -0.13085 | 29.2598
23 | 0.047633 | 0.011964 | -0.047532 | -0.011925 | 0.00010121 | 3.8541e-05 | 0.072423 | 0.072423 | 0.072423 | 0.97881 | -0.14839 | 0.97666 | -0.1637 | 26.8232
24 | 0.027215 | 0.0068309 | -0.027208 | -0.0068281 | 7.4254e-06 | 2.7693e-06 | 0.041468 | 0.041468 | 0.041468 | 0.97666 | -0.1637 | 0.97639 | -0.16567 | 15.3584
25 | 0.020317 | 0.0050944 | -0.020291 | -0.0050848 | 2.6223e-05 | 9.5378e-06 | 0.030955 | 0.030955 | 0.030955 | 0.97666 | -0.1637 | 0.97536 | -0.17303 | 11.4649
26 | 0.025242 | 0.0063355 | -0.025214 | -0.006325 | 2.8264e-05 | 1.0488e-05 | 0.038472 | 0.038472 | 0.038472 | 0.97639 | -0.16567 | 0.97526 | -0.17374 | 14.249
27 | 0.0069516 | 0.0017415 | -0.0069492 | -0.001741 | 2.4066e-06 | 4.9778e-07 | 0.010605 | 0.010605 | 0.010605 | 0.97536 | -0.17303 | 0.97502 | -0.17553 | 3.9279
28 | 0.013339 | 0.0033433 | -0.013335 | -0.003342 | 3.9601e-06 | 1.3319e-06 | 0.02035 | 0.02035 | 0.02035 | 0.97536 | -0.17303 | 0.97507 | -0.17517 | 7.5371
29 | 0.034171 | 0.0085764 | -0.034166 | -0.0085744 | 5.2954e-06 | 1.9971e-06 | 0.051918 | 0.051918 | 0.051918 | 0.97946 | -0.14381 | 0.9793 | -0.14493 | 19.2291
30 | 0.022946 | 0.0057567 | -0.02291 | -0.0057433 | 3.6348e-05 | 1.3388e-05 | 0.035012 | 0.035013 | 0.035013 | 0.97526 | -0.17374 | 0.97367 | -0.18518 | 12.9676
31 | 0.0069492 | 0.001741 | -0.0069487 | -0.0017409 | 4.5696e-07 | 9.4554e-08 | 0.010605 | 0.010605 | 0.010605 | 0.97502 | -0.17553 | 0.97495 | -0.17601 | 3.9279
32 | 0.011693 | 0.0029305 | -0.011693 | -0.0029302 | 6.8187e-07 | 2.1946e-07 | 0.017845 | 0.017845 | 0.017845 | 0.97507 | -0.17517 | 0.97501 | -0.17559 | 6.6091
33 | 0.031446 | 0.0078926 | -0.031396 | -0.0078738 | 4.9956e-05 | 1.8774e-05 | 0.047785 | 0.047785 | 0.047785 | 0.9793 | -0.14493 | 0.9777 | -0.15639 | 17.6982
34 | 0.020476 | 0.0051332 | -0.020462 | -0.0051282 | 1.3928e-05 | 5.0737e-06 | 0.031293 | 0.031293 | 0.031293 | 0.97367 | -0.18518 | 0.97299 | -0.19009 | 11.5899
35 | 0.0036429 | 0.00091241 | -0.0036424 | -0.00091255 | 5.1342e-07 | -1.3441e-07 | 0.0055597 | 0.0055599 | 0.0055599 | 0.97495 | -0.17601 | 0.97481 | -0.17702 | 2.0592
36 | 0.0011101 | 0.00027805 | -0.0011101 | -0.00027822 | 2.5805e-08 | -1.6975e-07 | 0.0016942 | 0.0016943 | 0.0016943 | 0.97501 | -0.17559 | 0.97498 | -0.17576 | 0.6275
37 | 0.025483 | 0.006392 | -0.025464 | -0.0063847 | 1.9867e-05 | 7.376e-06 | 0.038787 | 0.038787 | 0.038787 | 0.9777 | -0.15639 | 0.97691 | -0.16202 | 14.3655
38 | 0.0041954 | 0.0010495 | -0.0041948 | -0.0010496 | 5.8767e-07 | -7.2728e-08 | 0.0063356 | 0.0063357 | 0.0063357 | 0.98526 | -0.10291 | 0.98511 | -0.10393 | 2.3465
39 | 0.0041948 | 0.0010496 | -0.0041939 | -0.0010497 | 9.0384e-07 | -1.1167e-07 | 0.0063357 | 0.0063358 | 0.0063358 | 0.98511 | -0.10393 | 0.98489 | -0.10549 | 2.3466
40 | 0.0031936 | 0.00079899 | -0.0031928 | -0.00079939 | 8.2505e-07 | -4.0532e-07 | 0.0048246 | 0.0048248 | 0.0048248 | 0.98489 | -0.10549 | 0.98463 | -0.10736 | 1.787
41 | 0.0023365 | 0.00058523 | -0.0023362 | -0.00058552 | 2.2961e-07 | -2.8704e-07 | 0.0035309 | 0.003531 | 0.003531 | 0.98463 | -0.10736 | 0.98453 | -0.10807 | 1.3078
42 | 0.00085634 | 0.00021416 | -0.0008563 | -0.00021461 | 3.8159e-08 | -4.4978e-07 | 0.001294 | 0.0012941 | 0.0012941 | 0.98463 | -0.10736 | 0.98459 | -0.10768 | 0.47931
43 | 0.0025913 | 0.00064913 | -0.002591 | -0.00064937 | 2.7699e-07 | -2.4712e-07 | 0.0039554 | 0.0039556 | 0.0039556 | 0.97481 | -0.17702 | 0.9747 | -0.1778 | 1.465
44 | 0.020592 | 0.0051638 | -0.020577 | -0.0051583 | 1.5161e-05 | 5.5221e-06 | 0.031367 | 0.031367 | 0.031367 | 0.97691 | -0.16202 | 0.97617 | -0.16733 | 11.6174
45 | 0.0033495 | 0.00083918 | -0.0033491 | -0.00083936 | 4.1993e-07 | -1.8166e-07 | 0.0050277 | 0.0050278 | 0.0050278 | 0.99131 | -0.060296 | 0.99118 | -0.061202 | 1.8622
46 | 0.089652 | 0.02255 | -0.089563 | -0.022516 | 8.9412e-05 | 3.3474e-05 | 0.13465 | 0.13465 | 0.13465 | 0.99095 | -0.0628 | 0.98993 | -0.06996 | 16.6236
47 | -0.24077 | -0.060764 | 0.2418 | 0.061158 | 0.0010288 | 0.00039419 | 0.36 | 0.36 | 0.36 | 0.99561 | -0.030304 | 1 | 0 | 44.4448
48 | 0.082483 | 0.020742 | -0.082411 | -0.020715 | 7.1355e-05 | 2.6585e-05 | 0.12401 | 0.12401 | 0.12401 | 0.98993 | -0.06996 | 0.98905 | -0.076172 | 15.3098
49 | 0.082411 | 0.020715 | -0.082369 | -0.0207 | 4.2406e-05 | 1.58e-05 | 0.12401 | 0.12401 | 0.12401 | 0.98905 | -0.076172 | 0.98852 | -0.079869 | 15.3098
50 | 0.017331 | 0.0043447 | -0.017322 | -0.0043415 | 9.0358e-06 | 3.2161e-06 | 0.026418 | 0.026419 | 0.026419 | 0.97617 | -0.16733 | 0.97564 | -0.1711 | 9.7847
51 | 0.014429 | 0.0036164 | -0.014424 | -0.0036149 | 4.2275e-06 | 1.4513e-06 | 0.022006 | 0.022006 | 0.022006 | 0.97564 | -0.1711 | 0.97535 | -0.17322 | 8.1505
52 | 0.011169 | 0.0027993 | -0.011167 | -0.0027988 | 1.7207e-06 | 5.4444e-07 | 0.017081 | 0.017081 | 0.017081 | 0.97299 | -0.19009 | 0.97283 | -0.1912 | 6.3261
53 | 0.0092931 | 0.0023288 | -0.0092856 | -0.0023267 | 7.4864e-06 | 2.1423e-06 | 0.014212 | 0.014212 | 0.014212 | 0.97299 | -0.19009 | 0.97218 | -0.19591 | 5.2638
54 | 0.011167 | 0.0027988 | -0.011163 | -0.0027976 | 3.8754e-06 | 1.2263e-06 | 0.017081 | 0.017081 | 0.017081 | 0.97283 | -0.1912 | 0.97248 | -0.19371 | 6.3262
55 | 0.0074395 | 0.001864 | -0.0074363 | -0.0018633 | 3.1558e-06 | 7.3033e-07 | 0.011387 | 0.011387 | 0.011387 | 0.97218 | -0.19591 | 0.97175 | -0.19898 | 4.2174
56 | 0.0078993 | 0.0019796 | -0.0078983 | -0.0019794 | 1.0307e-06 | 2.5616e-07 | 0.012087 | 0.012087 | 0.012087 | 0.97248 | -0.19371 | 0.97235 | -0.19465 | 4.4766
57 | 0.00438 | 0.0010973 | -0.0043796 | -0.0010973 | 3.5154e-07 | -1.9941e-08 | 0.0067067 | 0.0067068 | 0.0067068 | 0.97175 | -0.19898 | 0.97167 | -0.19956 | 2.484
58 | 0.069876 | 0.017536 | -0.069758 | -0.017492 | 0.00011796 | 4.3432e-05 | 0.1056 | 0.1056 | 0.1056 | 0.98468 | -0.10703 | 0.98297 | -0.11921 | 13.0375
59 | -0.069876 | -0.017536 | 0.069972 | 0.017571 | 9.5946e-05 | 3.5322e-05 | 0.1056 | 0.1056 | 0.1056 | 0.98468 | -0.10703 | 0.98608 | -0.097146 | 13.0374
60 | 0.062478 | 0.015668 | -0.062432 | -0.015651 | 4.6041e-05 | 1.6768e-05 | 0.094583 | 0.094583 | 0.094583 | 0.98297 | -0.11921 | 0.98222 | -0.12453 | 11.6769
61 | 0.0033513 | 0.00083905 | -0.0033503 | -0.00083945 | 9.5828e-07 | -3.9726e-07 | 0.0050568 | 0.0050571 | 0.0050571 | 0.98608 | -0.097146 | 0.98579 | -0.099215 | 1.873
62 | -0.076707 | -0.019258 | 0.076792 | 0.019289 | 8.462e-05 | 3.1383e-05 | 0.11577 | 0.11576 | 0.11577 | 0.98608 | -0.097146 | 0.9872 | -0.089214 | 14.292
63 | 0.059533 | 0.014924 | -0.059521 | -0.01492 | 1.2738e-05 | 4.6133e-06 | 0.090192 | 0.090192 | 0.090192 | 0.98222 | -0.12453 | 0.982 | -0.12607 | 11.1348
64 | 0.0004601 | 0.00011509 | -0.00046009 | -0.00011531 | 5.1666e-09 | -2.1688e-07 | 0.00069443 | 0.0006945 | 0.0006945 | 0.98579 | -0.099215 | 0.98577 | -0.099296 | 0.25722
65 | -0.078764 | -0.019784 | 0.078866 | 0.019822 | 0.00010248 | 3.8072e-05 | 0.11874 | 0.11874 | 0.11874 | 0.9872 | -0.089214 | 0.98852 | -0.079869 | 14.6589
66 | 0.058861 | 0.014754 | -0.058821 | -0.01474 | 3.983e-05 | 1.4406e-05 | 0.089192 | 0.089192 | 0.089192 | 0.982 | -0.12607 | 0.98132 | -0.13096 | 11.0114
67 | 0.0008788 | 0.00021962 | -0.00087879 | -0.00021977 | 1.3739e-08 | -1.4923e-07 | 0.001337 | 0.0013371 | 0.0013371 | 0.9779 | -0.15543 | 0.97788 | -0.15554 | 0.49521
68 | -0.0041572 | -0.0010413 | 0.0041578 | 0.0010412 | 6.3026e-07 | -7.4339e-08 | 0.0063256 | 0.0063254 | 0.0063256 | 0.9779 | -0.15543 | 0.97805 | -0.15433 | 2.3428
69 | 0.00087879 | 0.00021977 | -0.00087875 | -0.00022023 | 4.2465e-08 | -4.6114e-07 | 0.0013371 | 0.0013372 | 0.0013372 | 0.97788 | -0.15554 | 0.97783 | -0.15589 | 0.49527
70 | -0.0041578 | -0.0010412 | 0.0041579 | 0.0010412 | 4.5265e-08 | -5.3432e-09 | 0.0063254 | 0.0063254 | 0.0063254 | 0.97805 | -0.15433 | 0.97806 | -0.15426 | 2.3428
71 | -0.0041579 | -0.0010412 | 0.0041591 | 0.001041 | 1.2617e-06 | -1.4916e-07 | 0.0063254 | 0.0063252 | 0.0063254 | 0.97806 | -0.15426 | 0.97837 | -0.15206 | 2.3428
72 | -0.00076984 | -0.00019294 | 0.00076984 | 0.00019286 | 5.8201e-09 | -8.3191e-08 | 0.0011709 | 0.0011709 | 0.0011709 | 0.97833 | -0.15233 | 0.97834 | -0.15228 | 0.43367
73 | 0.028184 | 0.0070521 | -0.028171 | -0.0070484 | 1.286e-05 | 3.6789e-06 | 0.042863 | 0.042863 | 0.042863 | 0.97834 | -0.15228 | 0.97788 | -0.15559 | 5.2917
74 | -0.028954 | -0.0072449 | 0.028977 | 0.0072517 | 2.34e-05 | 6.8124e-06 | 0.044034 | 0.044033 | 0.044034 | 0.97834 | -0.15228 | 0.97916 | -0.14642 | 5.4362
75 | -0.0056027 | -0.0014028 | 0.0056037 | 0.0014029 | 1.0697e-06 | 1.1485e-07 | 0.0085207 | 0.0085206 | 0.0085207 | 0.97837 | -0.15206 | 0.97856 | -0.15068 | 3.1558
76 | -0.010441 | -0.0026152 | 0.010445 | 0.0026166 | 4.434e-06 | 1.351e-06 | 0.015876 | 0.015876 | 0.015876 | 0.97856 | -0.15068 | 0.97899 | -0.14761 | 5.88
77 | -0.01347 | -0.0033747 | 0.013473 | 0.0033755 | 2.2057e-06 | 7.423e-07 | 0.020474 | 0.020474 | 0.020474 | 0.97899 | -0.14761 | 0.97916 | -0.14642 | 7.5829
78 | 0.027695 | 0.006929 | -0.027685 | -0.0069263 | 9.4181e-06 | 2.663e-06 | 0.042138 | 0.042138 | 0.042138 | 0.97788 | -0.15559 | 0.97754 | -0.15805 | 5.2023
79 | -0.04245 | -0.010627 | 0.042478 | 0.010637 | 2.78e-05 | 9.4794e-06 | 0.064507 | 0.064506 | 0.064507 | 0.97916 | -0.14642 | 0.97982 | -0.14169 | 7.9638
80 | 0.0058821 | 0.0014741 | -0.0058809 | -0.0014739 | 1.1564e-06 | 1.6113e-07 | 0.0090014 | 0.0090015 | 0.0090015 | 0.97235 | -0.19465 | 0.97215 | -0.19607 | 3.3339
81 | 0.00089932 | 0.00022503 | -0.00089929 | -0.00022538 | 3.4766e-08 | -3.5049e-07 | 0.0013771 | 0.0013772 | 0.0013772 | 0.97167 | -0.19956 | 0.97163 | -0.19984 | 0.51008
82 | -0.043802 | -0.010969 | 0.043821 | 0.010975 | 1.9085e-05 | 6.5565e-06 | 0.066518 | 0.066517 | 0.066518 | 0.97982 | -0.14169 | 0.98026 | -0.13853 | 8.2121
83 | -0.048069 | -0.01204 | 0.04807 | 0.01204 | 8.9141e-07 | 3.1241e-07 | 0.072966 | 0.072966 | 0.072966 | 0.98026 | -0.13853 | 0.98028 | -0.1384 | 9.0081
84 | -0.050299 | -0.012599 | 0.050318 | 0.012606 | 1.9377e-05 | 6.848e-06 | 0.076349 | 0.076348 | 0.076349 | 0.98028 | -0.1384 | 0.98067 | -0.13562 | 9.4257
85 | 0.026146 | 0.0065412 | -0.026141 | -0.0065399 | 5.0129e-06 | 1.3558e-06 | 0.039796 | 0.039796 | 0.039796 | 0.97754 | -0.15805 | 0.97734 | -0.15944 | 4.9131
86 | 0.001539 | 0.00038506 | -0.0015388 | -0.00038566 | 1.8362e-07 | -6.0152e-07 | 0.0023425 | 0.0023427 | 0.0023427 | 0.97754 | -0.15805 | 0.97742 | -0.15891 | 0.86767
87 | 0.05081 | 0.012732 | -0.050777 | -0.012721 | 3.2695e-05 | 1.1572e-05 | 0.077045 | 0.077045 | 0.077045 | 0.98132 | -0.13096 | 0.98067 | -0.13562 | 9.5117
88 | 0.00045922 | 0.00011508 | -0.00045922 | -0.00011509 | 3.556e-10 | -1.4674e-08 | 0.00069679 | 0.0006968 | 0.0006968 | 0.98067 | -0.13562 | 0.98066 | -0.13562 | 0.25807
89 | 0.011582 | 0.0029024 | -0.011576 | -0.0029007 | 5.5633e-06 | 1.7835e-06 | 0.017669 | 0.017669 | 0.017669 | 0.97535 | -0.17322 | 0.97486 | -0.17669 | 6.5441
90 | 0.025178 | 0.0062985 | -0.025165 | -0.0062951 | 1.2788e-05 | 3.3461e-06 | 0.03833 | 0.03833 | 0.03833 | 0.97734 | -0.15944 | 0.97683 | -0.16312 | 4.7321
91 | 0.00081594 | 0.00020449 | -0.00081594 | -0.00020449 | 3.2789e-10 | -4.1457e-09 | 0.0012422 | 0.0012422 | 0.0012422 | 0.97742 | -0.15891 | 0.97742 | -0.15892 | 0.46007
92 | 0.0080738 | 0.0020229 | -0.0080703 | -0.002022 | 3.5386e-06 | 8.9566e-07 | 0.012324 | 0.012324 | 0.012324 | 0.97486 | -0.17669 | 0.97442 | -0.17986 | 4.5643
93 | 0.0035778 | 0.00089612 | -0.0035774 | -0.00089624 | 4.2414e-07 | -1.205e-07 | 0.0054634 | 0.0054635 | 0.0054635 | 0.97442 | -0.17986 | 0.9743 | -0.18071 | 2.0235
94 | 0.0022601 | 0.0005661 | -0.00226 | -0.00056622 | 9.0011e-08 | -1.1615e-07 | 0.0034517 | 0.0034518 | 0.0034518 | 0.9743 | -0.18071 | 0.97426 | -0.181 | 1.2784
95 | 0.0056696 | 0.0014186 | -0.0056679 | -0.0014184 | 1.7349e-06 | 2.0884e-07 | 0.0086737 | 0.0086739 | 0.0086739 | 0.97255 | -0.19397 | 0.97225 | -0.19618 | 3.2125
96 | -0.0071139 | -0.0017806 | 0.0071148 | 0.0017808 | 9.7976e-07 | 2.1232e-07 | 0.010883 | 0.010883 | 0.010883 | 0.97255 | -0.19397 | 0.97269 | -0.19297 | 4.0309
97 | 0.004678 | 0.0011703 | -0.0046756 | -0.0011703 | 2.4092e-06 | -7.0924e-09 | 0.0071589 | 0.0071592 | 0.0071592 | 0.97225 | -0.19618 | 0.97173 | -0.19992 | 2.6516
98 | -0.0094993 | -0.0023784 | 0.0095041 | 0.0023798 | 4.8106e-06 | 1.3968e-06 | 0.014531 | 0.014531 | 0.014531 | 0.97269 | -0.19297 | 0.9732 | -0.1893 | 5.3819
99 | 0.00099918 | 0.00025022 | -0.00099915 | -0.00025041 | 2.3784e-08 | -1.9466e-07 | 0.001526 | 0.0015261 | 0.0015261 | 0.97426 | -0.181 | 0.97424 | -0.18117 | 0.56521
100 | 0.00059361 | 0.00014835 | -0.00059359 | -0.00014877 | 1.7567e-08 | -4.1537e-07 | 0.00090885 | 0.000909 | 0.000909 | 0.97173 | -0.19992 | 0.9717 | -0.20013 | 0.33667
101 | 0.004082 | 0.0010219 | -0.0040802 | -0.0010222 | 1.7894e-06 | -2.2062e-07 | 0.0062504 | 0.0062507 | 0.0062507 | 0.97173 | -0.19992 | 0.97129 | -0.20309 | 2.3151
102 | 0.025165 | 0.0062951 | -0.025164 | -0.0062948 | 1.4366e-06 | 3.7601e-07 | 0.03833 | 0.03833 | 0.03833 | 0.97683 | -0.16312 | 0.97677 | -0.16354 | 4.7322
103 | 0.023825 | 0.0059601 | -0.023821 | -0.0059591 | 4.0306e-06 | 9.9784e-07 | 0.036291 | 0.036291 | 0.036291 | 0.97677 | -0.16354 | 0.9766 | -0.16476 | 4.4804
104 | 0.0013388 | 0.00033469 | -0.0013387 | -0.00033485 | 3.5235e-08 | -1.5641e-07 | 0.0020392 | 0.0020392 | 0.0020392 | 0.97677 | -0.16354 | 0.97675 | -0.16373 | 0.75527
105 | -0.00061349 | -0.00015375 | 0.00061352 | 0.0001531 | 2.9219e-08 | -6.5977e-07 | 0.00093466 | 0.00093442 | 0.00093466 | 0.9767 | -0.16407 | 0.97675 | -0.16373 | 0.34617
106 | 0.02163 | 0.0054099 | -0.021615 | -0.0054066 | 1.5111e-05 | 3.3024e-06 | 0.032953 | 0.032954 | 0.032954 | 0.9766 | -0.16476 | 0.9759 | -0.16983 | 4.0684
107 | 0.021615 | 0.0054066 | -0.021595 | -0.0054022 | 2.0192e-05 | 4.4187e-06 | 0.032954 | 0.032955 | 0.032955 | 0.9759 | -0.16983 | 0.97496 | -0.17661 | 4.0685
108 | 0.020128 | 0.0050347 | -0.020127 | -0.0050344 | 1.3802e-06 | 2.6777e-07 | 0.030717 | 0.030717 | 0.030717 | 0.97496 | -0.17661 | 0.97489 | -0.17711 | 3.7922
109 | 0.012842 | 0.0032087 | -0.012832 | -0.0032096 | 1.0776e-05 | -8.9601e-07 | 0.019598 | 0.0196 | 0.0196 | 0.97489 | -0.17711 | 0.97405 | -0.1832 | 2.4198
110 | 0.0025526 | 0.00063972 | -0.0025526 | -0.00063973 | 1.89e-08 | -1.7524e-08 | 0.0038995 | 0.0038995 | 0.0038995 | 0.97405 | -0.1832 | 0.97404 | -0.18325 | 1.4443
111 | 0.0095121 | 0.0023777 | -0.0095064 | -0.0023804 | 5.7752e-06 | -2.6866e-06 | 0.014529 | 0.014531 | 0.014531 | 0.97405 | -0.1832 | 0.97344 | -0.1876 | 1.7939
112 | 0.0095064 | 0.0023804 | -0.0095041 | -0.0023798 | 2.2341e-06 | 6.4851e-07 | 0.014531 | 0.014531 | 0.014531 | 0.97344 | -0.1876 | 0.9732 | -0.1893 | 5.3818
113 | -0.0017362 | -0.00043514 | 0.0017364 | 0.00043485 | 1.2182e-07 | -2.9456e-07 | 0.0026602 | 0.0026601 | 0.0026602 | 0.97119 | -0.20382 | 0.97126 | -0.20332 | 0.98526
114 | -0.0024928 | -0.00062443 | 0.0024929 | 0.00062436 | 7.902e-08 | -7.7069e-08 | 0.003819 | 0.003819 | 0.003819 | 0.97126 | -0.20332 | 0.97129 | -0.20309 | 1.4144

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24469 | 0.061681

## res_load
| p_mw | q_mvar
0 | 0.0059081 | 0.0014807
1 | 0.0016609 | 0.00041627
2 | 0.0028977 | 0.00072624
3 | 0.0026814 | 0.00067202
4 | 0.0057016 | 0.0014289
5 | 0.0022664 | 0.000568
6 | 0.0022504 | 0.00056401
7 | 0.010741 | 0.0026919
8 | 0.0024888 | 0.00062375
9 | 0.0032012 | 0.0008023
10 | 0.0014655 | 0.0003673
11 | 0.0028642 | 0.00071783
12 | 0.002701 | 0.00067694
13 | 0.0019655 | 0.0004926
14 | 0.0016276 | 0.00040792
15 | 0.0022678 | 0.00056836
16 | 0.0016419 | 0.0004115
17 | 0.0027203 | 0.00068178
18 | 0.0024341 | 0.00061005
19 | 0.0033058 | 0.00082852
20 | 0.010582 | 0.0026522
21 | 0.0059124 | 0.0014818
22 | 0.0040612 | 0.0010178
23 | 0.0010003 | 0.00025069
24 | 0.0010511 | 0.00026342
25 | 0.0023362 | 0.00058552
26 | 0.0008563 | 0.00021461
27 | 0.002591 | 0.00064937
28 | 0.0048713 | 0.0012209
29 | 0.0024058 | 0.00060296
30 | 0.0028827 | 0.00072247
31 | 0.0016399 | 0.00041099
32 | 0.0033491 | 0.00083936
33 | 0.0070799 | 0.0017744
34 | 0.0020855 | 0.00052266
35 | 0.0011101 | 0.00027822
36 | 0.0032464 | 0.00081362
37 | 0.0028931 | 0.00072507
38 | 0.0018461 | 0.00046268
39 | 0.0032637 | 0.00081796
40 | 0.0030564 | 0.000766
41 | 0.0072804 | 0.0018246
42 | 0.0033837 | 0.00084803
43 | 0.0028987 | 0.00072649
44 | 0.0028902 | 0.00072435
45 | 0.001972 | 0.00049422
46 | 0.00065993 | 0.00016539
47 | 0.00046009 | 0.00011531
48 | 0.0035026 | 0.00087784
49 | 0.0032784 | 0.00082164
50 | 0.00087875 | 0.00022023
51 | 0.00076984 | 0.00019294
52 | 0.0014435 | 0.00036178
53 | 0.0048371 | 0.0012123
54 | 0.0030251 | 0.00075815
55 | 0.0004765 | 0.00011942
56 | 0.0020162 | 0.00050531
57 | 0.0034803 | 0.00087224
58 | 0.0058809 | 0.0014739
59 | 0.00089929 | 0.00022538
60 | 0.0013245 | 0.00033195
61 | 0.0042479 | 0.0010646
62 | 0.0022286 | 0.00055853
63 | 0.0080109 | 0.0020077
64 | 0.00045922 | 0.00011509
65 | 0.0028429 | 0.0007125
66 | 0.00096309 | 0.00024137
67 | 0.0007229 | 0.00018117
68 | 0.0035022 | 0.00087772
69 | 0.0044925 | 0.0011259
70 | 0.0013172 | 0.00033013
71 | 0.0014442 | 0.00036196
72 | 0.00098988 | 0.00024809
73 | 0.0023845 | 0.00059761
74 | 0.0012609 | 0.000316
75 | 0.00099915 | 0.00025041
76 | 0.00081594 | 0.00020449
77 | 0.00061349 | 0.00015375
78 | 0.00072521 | 0.00018175
79 | 0.0021912 | 0.00054917
80 | 0.0014664 | 0.00036753
81 | 0.0072845 | 0.0018257
82 | 0.0007668 | 0.00019218
83 | 0.0025526 | 0.00063973
84 | 0.0017362 | 0.00043514
85 | 0.00075646 | 0.00018959
86 | 0.0015873 | 0.00039781
87 | 0.00059359 | 0.00014877

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1