## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1217-2_1_3_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_1217-2_1_3_node_10 | 0.4 | n |  | TRUE
2 | bus_LV_1217-2_1_3_node_37 | 0.4 | n |  | TRUE
3 | bus_LV_1217-2_1_3_node_42 | 0.4 | n |  | TRUE
4 | bus_LV_1217-2_1_3_node_47 | 0.4 | n |  | TRUE
5 | bus_LV_1217-2_1_3_node_45 | 0.4 | n |  | TRUE
6 | bus_LV_1217-2_1_3_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_1217-2_1_3_node_41 | 0.4 | n |  | TRUE
8 | bus_LV_1217-2_1_3_node_40 | 0.4 | n |  | TRUE
9 | bus_LV_1217-2_1_3_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_1217-2_1_3_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1217-2_1_3_node_43 | 0.4 | n |  | TRUE
12 | bus_LV_1217-2_1_3_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1217-2_1_3_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_1217-2_1_3_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_1217-2_1_3_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1217-2_1_3_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_1217-2_1_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1217-2_1_3_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_1217-2_1_3_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1217-2_1_3_node_48 | 0.4 | n |  | TRUE
21 | bus_LV_1217-2_1_3_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1217-2_1_3_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_1217-2_1_3_node_46 | 0.4 | n |  | TRUE
24 | bus_LV_1217-2_1_3_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1217-2_1_3_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1217-2_1_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1217-2_1_3_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_1217-2_1_3_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_1217-2_1_3_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1217-2_1_3_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_1217-2_1_3_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_1217-2_1_3_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_1217-2_1_3_node_44 | 0.4 | n |  | TRUE
34 | bus_MV_133_0_node_240 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1217-2_1_3_load_37 | 2 | 0.0083204 | 0.0020853 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1217-2_1_3_load_42 | 3 | 0.014817 | 0.0037134 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1217-2_1_3_load_47 | 4 | 0.0064238 | 0.00161 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1217-2_1_3_load_45 | 5 | 0.0070628 | 0.0017701 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1217-2_1_3_load_41 | 7 | 0.0058554 | 0.0014675 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1217-2_1_3_load_40 | 8 | 0.0039122 | 0.00098048 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1217-2_1_3_load_50 | 9 | 0.00378 | 0.00094736 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1217-2_1_3_load_17 | 12 | 0.005147 | 0.00129 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1217-2_1_3_load_21 | 16 | 0.005838 | 0.0014631 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1217-2_1_3_load_31 | 18 | 0.0041311 | 0.0010353 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1217-2_1_3_load_48 | 20 | 0.0077256 | 0.0019362 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1217-2_1_3_load_29 | 22 | 0.010482 | 0.0026272 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1217-2_1_3_load_46 | 23 | 0.0051036 | 0.0012791 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1217-2_1_3_load_24 | 24 | 0.0052217 | 0.0013087 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1217-2_1_3_load_27 | 26 | 0.0040298 | 0.00101 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1217-2_1_3_load_32 | 27 | 0.0084154 | 0.0021091 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1217-2_1_3_load_34 | 28 | 0.016522 | 0.0041408 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1217-2_1_3_load_36 | 30 | 0.0034555 | 0.00086602 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1217-2_1_3_load_33 | 31 | 0.0063731 | 0.0015973 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1217-2_1_3_load_49 | 32 | 0.0091409 | 0.0022909 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1217-2_1_3_load_44 | 33 | 0.011715 | 0.002936 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1217-2_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.004235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1217-2_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.030731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1217-2_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.065785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1217-2_1_3_line_3 | NAYY 4x150 SE | 2 | 6 | 0.016528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1217-2_1_3_line_4 | NAYY 4x150 SE | 3 | 11 | 0.043626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1217-2_1_3_line_5 | NAYY 4x150 SE | 4 | 5 | 0.015096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1217-2_1_3_line_6 | NAYY 4x150 SE | 5 | 23 | 0.0098534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1217-2_1_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0064265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1217-2_1_3_line_8 | NAYY 4x150 SE | 6 | 10 | 0.052917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1217-2_1_3_line_9 | NAYY 4x150 SE | 7 | 8 | 0.014947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1217-2_1_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.013616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1217-2_1_3_line_11 | NAYY 4x150 SE | 10 | 15 | 0.008403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1217-2_1_3_line_12 | NAYY 4x150 SE | 11 | 33 | 0.02973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1217-2_1_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.014468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1217-2_1_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.0070954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1217-2_1_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.017923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1217-2_1_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.021605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1217-2_1_3_line_17 | NAYY 4x150 SE | 14 | 17 | 0.011773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1217-2_1_3_line_18 | NAYY 4x150 SE | 15 | 18 | 0.017966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1217-2_1_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.014807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1217-2_1_3_line_20 | NAYY 4x150 SE | 17 | 20 | 0.010844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1217-2_1_3_line_21 | NAYY 4x150 SE | 18 | 21 | 0.0058089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1217-2_1_3_line_22 | NAYY 4x150 SE | 19 | 22 | 0.0079659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1217-2_1_3_line_23 | NAYY 4x150 SE | 20 | 23 | 0.019202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1217-2_1_3_line_24 | NAYY 4x150 SE | 21 | 26 | 0.02262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1217-2_1_3_line_25 | NAYY 4x150 SE | 22 | 27 | 0.0084155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1217-2_1_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.010946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1217-2_1_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.01494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1217-2_1_3_line_28 | NAYY 4x150 SE | 27 | 31 | 0.015477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1217-2_1_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.047734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1217-2_1_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.012359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1217-2_1_3_line_31 | NAYY 4x150 SE | 30 | 32 | 0.0031876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1217-2_1_3_line_32 | NAYY 4x150 SE | 31 | 32 | 0.0011236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1217-2_1_3_trafo_22 | 0.25 MVA 20/0.4 kV | 34 | 17 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2690056.7208 | 1200448.4976 | 2690052.9902 | 1200446.4734
1 | 2690052.9902 | 1200446.4734 | 2690028.2878 | 1200428.1925
2 | 2690056.7208 | 1200448.4976 | 2690062.7052 | 1200425.2727 | 2690068.1745 | 1200397.8373 | 2690065.5147 | 1200384.2692
3 | 2690015.0024 | 1200418.3607 | 2690028.2878 | 1200428.1925
4 | 2690048.1915 | 1200344.5905 | 2690056.7237 | 1200359.4287 | 2690063.6779 | 1200374.8991 | 2690065.5147 | 1200384.2692
5 | 2689993.6228 | 1200307.1888 | 2690002.4328 | 1200294.9299
6 | 2689993.6228 | 1200307.1888 | 2689993.6228 | 1200307.1888 | 2689991.0689 | 1200316.7055
7 | 2690015.0024 | 1200418.3607 | 2690013.9325 | 1200424.6974
8 | 2690015.0024 | 1200418.3607 | 2690005.1541 | 1200401.4236 | 2690001.5033 | 1200397.1325 | 2689995.6127 | 1200393.9306 | 2689992.7187 | 1200392.4639 | 2689977.7742 | 1200388.3251 | 2689975.6567 | 1200387.3704
9 | 2690011.4439 | 1200439.4354 | 2690013.9325 | 1200424.6974
10 | 2689975.6567 | 1200387.3704 | 2689974.0193 | 1200400.8877
11 | 2689967.6324 | 1200384.8035 | 2689975.6567 | 1200387.3704
12 | 2690048.1915 | 1200344.5905 | 2690046.8227 | 1200339.4221 | 2690039.1833 | 1200326.4652 | 2690034.5623 | 1200318.3459
13 | 2689961.957 | 1200367.8181 | 2689974.8242 | 1200361.2024
14 | 2689980.6718 | 1200357.204 | 2689975.907 | 1200360.6457 | 2689974.8242 | 1200361.2024
15 | 2689967.6324 | 1200384.8035 | 2689965.9225 | 1200378.5181 | 2689961.957 | 1200367.8181
16 | 2689961.957 | 1200367.8181 | 2689955.6592 | 1200354.7482 | 2689951.6824 | 1200348.8707
17 | 2689980.6718 | 1200357.204 | 2689983.2812 | 1200345.7248
18 | 2689967.6324 | 1200384.8035 | 2689963.5651 | 1200385.9096 | 2689953.3817 | 1200384.133 | 2689950.0834 | 1200383.252
19 | 2689943.3847 | 1200336.6072 | 2689951.6824 | 1200348.8707
20 | 2689983.2812 | 1200345.7248 | 2689986.0919 | 1200335.2514
21 | 2689944.4713 | 1200381.7529 | 2689950.0834 | 1200383.252
22 | 2689943.3847 | 1200336.6072 | 2689939.9987 | 1200329.3968
23 | 2689991.0689 | 1200316.7055 | 2689986.0919 | 1200335.2514
24 | 2689944.4713 | 1200381.7529 | 2689926.7193 | 1200371.4124 | 2689924.8253 | 1200370.5634
25 | 2689936.4216 | 1200321.7793 | 2689939.9987 | 1200329.3968
26 | 2689911.1928 | 1200364.4521 | 2689917.3214 | 1200355.3828
27 | 2689911.1928 | 1200364.4521 | 2689924.8253 | 1200370.5634
28 | 2689929.8429 | 1200307.7701 | 2689936.4216 | 1200321.7793
29 | 2689921.2712 | 1200293.8023 | 2689892.6851 | 1200311.228 | 2689883.8806 | 1200322.4388
30 | 2689921.2712 | 1200293.8023 | 2689924.6757 | 1200296.7665 | 2689928.0104 | 1200303.8677
31 | 2689929.3653 | 1200306.7531 | 2689928.0104 | 1200303.8677
32 | 2689929.3653 | 1200306.7531 | 2689929.8429 | 1200307.7701

## bus_geodata
| x | y | coords
0 | 2690052.9902 | 1200446.4734
1 | 2690056.7208 | 1200448.4976
2 | 2690028.2878 | 1200428.1925
3 | 2690065.5147 | 1200384.2692
4 | 2690002.4328 | 1200294.9299
5 | 2689993.6228 | 1200307.1888
6 | 2690015.0024 | 1200418.3607
7 | 2690011.4439 | 1200439.4354
8 | 2690013.9325 | 1200424.6974
9 | 2689974.0193 | 1200400.8877
10 | 2689975.6567 | 1200387.3704
11 | 2690048.1915 | 1200344.5905
12 | 2689974.8242 | 1200361.2024
13 | 2689961.957 | 1200367.8181
14 | 2689980.6718 | 1200357.204
15 | 2689967.6324 | 1200384.8035
16 | 2689951.6824 | 1200348.8707
17 | 2689983.2812 | 1200345.7248
18 | 2689950.0834 | 1200383.252
19 | 2689943.3847 | 1200336.6072
20 | 2689986.0919 | 1200335.2514
21 | 2689944.4713 | 1200381.7529
22 | 2689939.9987 | 1200329.3968
23 | 2689991.0689 | 1200316.7055
24 | 2689917.3214 | 1200355.3828
25 | 2689911.1928 | 1200364.4521
26 | 2689924.8253 | 1200370.5634
27 | 2689936.4216 | 1200321.7793
28 | 2689883.8806 | 1200322.4388
29 | 2689921.2712 | 1200293.8023
30 | 2689928.0104 | 1200303.8677
31 | 2689929.8429 | 1200307.7701
32 | 2689929.3653 | 1200306.7531
33 | 2690034.5623 | 1200318.3459
34 | 2689980.6718 | 1200357.204

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98941 | -0.074164 | 0 | 0
1 | 0.98925 | -0.075311 | 0 | 0
2 | 0.99059 | -0.065857 | 0.0083204 | 0.0020853
3 | 0.98672 | -0.093163 | 0.014817 | 0.0037134
4 | 0.99876 | -0.0087172 | 0.0064238 | 0.00161
5 | 0.99889 | -0.007747 | 0.0070628 | 0.0017701
6 | 0.99142 | -0.06 | 0 | 0
7 | 0.9912 | -0.061527 | 0.0058554 | 0.0014675
8 | 0.99133 | -0.060638 | 0.0039122 | 0.00098048
9 | 0.99475 | -0.036615 | 0.00378 | 0.00094736
10 | 0.99482 | -0.036096 | 0 | 0
11 | 0.98598 | -0.098408 | 0 | 0
12 | 0.99828 | -0.011998 | 0.005147 | 0.00129
13 | 0.99701 | -0.020853 | 0 | 0
14 | 0.99892 | -0.0074816 | 0 | 0
15 | 0.99541 | -0.031995 | 0 | 0
16 | 0.99514 | -0.033944 | 0.005838 | 0.0014631
17 | 1 | 0 | -0.15537 | -0.038878
18 | 0.99507 | -0.034418 | 0.0041311 | 0.0010353
19 | 0.99398 | -0.042071 | 0 | 0
20 | 0.99959 | -0.0028497 | 0.0077256 | 0.0019362
21 | 0.99499 | -0.03496 | 0 | 0
22 | 0.99336 | -0.046451 | 0.010482 | 0.0026272
23 | 0.99908 | -0.0064178 | 0.0051036 | 0.0012791
24 | 0.9945 | -0.038436 | 0.0052217 | 0.0013087
25 | 0.99458 | -0.037859 | 0 | 0
26 | 0.99469 | -0.037071 | 0.0040298 | 0.00101
27 | 0.99283 | -0.050191 | 0.0084154 | 0.0021091
28 | 0.99047 | -0.066824 | 0.016522 | 0.0041408
29 | 0.9916 | -0.058809 | 0 | 0
30 | 0.9919 | -0.056736 | 0.0034555 | 0.00086602
31 | 0.99204 | -0.055758 | 0.0063731 | 0.0015973
32 | 0.99199 | -0.05609 | 0.0091409 | 0.0022909
33 | 0.98548 | -0.10199 | 0.011715 | 0.002936
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.026616 | 0.00668 | -0.026611 | -0.0066784 | 4.235e-06 | 1.5745e-06 | 0.040032 | 0.040032 | 0.040032 | 0.98941 | -0.074164 | 0.98925 | -0.075311 | 14.8266
1 | -0.026616 | -0.00668 | 0.026646 | 0.0066914 | 3.0731e-05 | 1.1424e-05 | 0.040032 | 0.040032 | 0.040032 | 0.98941 | -0.074164 | 0.99059 | -0.065857 | 14.8266
2 | 0.026611 | 0.0066784 | -0.026546 | -0.006654 | 6.5785e-05 | 2.446e-05 | 0.040032 | 0.040032 | 0.040032 | 0.98925 | -0.075311 | 0.98672 | -0.093163 | 14.8268
3 | -0.034967 | -0.0087767 | 0.034995 | 0.0087874 | 2.8459e-05 | 1.0733e-05 | 0.05253 | 0.05253 | 0.05253 | 0.99059 | -0.065857 | 0.99142 | -0.06 | 19.4556
4 | 0.011729 | 0.0029406 | -0.011721 | -0.0029378 | 8.5174e-06 | 2.7191e-06 | 0.017688 | 0.017688 | 0.017688 | 0.98672 | -0.093163 | 0.98598 | -0.098408 | 6.5512
5 | -0.0064238 | -0.00161 | 0.0064247 | 0.0016101 | 8.6284e-07 | 1.3428e-07 | 0.0095706 | 0.0095706 | 0.0095706 | 0.99876 | -0.0087172 | 0.99889 | -0.007747 | 3.5447
6 | -0.013487 | -0.0033802 | 0.01349 | 0.003381 | 2.482e-06 | 8.2562e-07 | 0.020092 | 0.020092 | 0.020092 | 0.99889 | -0.007747 | 0.99908 | -0.0064178 | 7.4414
7 | 0.0097692 | 0.0024483 | -0.0097683 | -0.0024481 | 8.6213e-07 | 2.4873e-07 | 0.014662 | 0.014663 | 0.014663 | 0.99142 | -0.06 | 0.99133 | -0.060638 | 5.4306
8 | -0.044764 | -0.011236 | 0.044913 | 0.011292 | 0.00014908 | 5.6654e-05 | 0.067193 | 0.067192 | 0.067193 | 0.99142 | -0.06 | 0.99482 | -0.036096 | 24.8862
9 | -0.0058554 | -0.0014675 | 0.0058561 | 0.0014676 | 7.2066e-07 | 8.4498e-08 | 0.0087903 | 0.0087902 | 0.0087903 | 0.9912 | -0.061527 | 0.99133 | -0.060638 | 3.2557
10 | -0.00378 | -0.00094736 | 0.0037803 | 0.00094728 | 2.7165e-07 | -7.2298e-08 | 0.0056544 | 0.0056543 | 0.0056544 | 0.99475 | -0.036615 | 0.99482 | -0.036096 | 2.0942
11 | -0.048694 | -0.01224 | 0.048722 | 0.01225 | 2.7825e-05 | 1.0593e-05 | 0.072847 | 0.072847 | 0.072847 | 0.99482 | -0.036096 | 0.99541 | -0.031995 | 26.9803
12 | 0.011721 | 0.0029378 | -0.011715 | -0.002936 | 5.8044e-06 | 1.8535e-06 | 0.017688 | 0.017689 | 0.017689 | 0.98598 | -0.098408 | 0.98548 | -0.10199 | 6.5513
13 | 0.12287 | 0.030902 | -0.12272 | -0.030844 | 0.00015148 | 5.7884e-05 | 0.18319 | 0.18319 | 0.18319 | 0.99828 | -0.011998 | 0.99701 | -0.020853 | 33.9233
14 | -0.12802 | -0.032192 | 0.1281 | 0.032223 | 8.0639e-05 | 3.083e-05 | 0.19086 | 0.19086 | 0.19086 | 0.99828 | -0.011998 | 0.99892 | -0.0074816 | 35.344
15 | 0.06221 | 0.015644 | -0.062113 | -0.015607 | 9.645e-05 | 3.6863e-05 | 0.092865 | 0.092865 | 0.092865 | 0.99701 | -0.020853 | 0.99541 | -0.031995 | 34.3946
16 | 0.060508 | 0.015201 | -0.060398 | -0.015159 | 0.00010998 | 4.2018e-05 | 0.09032 | 0.09032 | 0.09032 | 0.99701 | -0.020853 | 0.99514 | -0.033944 | 33.452
17 | -0.1281 | -0.032223 | 0.12823 | 0.032274 | 0.0001338 | 5.1153e-05 | 0.19086 | 0.19086 | 0.19086 | 0.99892 | -0.0074816 | 1 | 0 | 35.344
18 | 0.013391 | 0.0033565 | -0.013387 | -0.003355 | 4.4927e-06 | 1.4945e-06 | 0.020019 | 0.020019 | 0.020019 | 0.99541 | -0.031995 | 0.99507 | -0.034418 | 7.4143
19 | 0.05456 | 0.013696 | -0.054499 | -0.013672 | 6.1508e-05 | 2.3465e-05 | 0.081591 | 0.081591 | 0.081591 | 0.99514 | -0.033944 | 0.99398 | -0.042071 | 30.2189
20 | 0.026339 | 0.0066035 | -0.026328 | -0.0065996 | 1.0394e-05 | 3.8556e-06 | 0.039193 | 0.039193 | 0.039193 | 1 | 0 | 0.99959 | -0.0028497 | 14.5161
21 | 0.0092559 | 0.0023196 | -0.0092552 | -0.0023194 | 6.9442e-07 | 1.9163e-07 | 0.013841 | 0.013841 | 0.013841 | 0.99507 | -0.034418 | 0.99499 | -0.03496 | 5.1264
22 | 0.054499 | 0.013672 | -0.054466 | -0.013659 | 3.3091e-05 | 1.2624e-05 | 0.081591 | 0.081591 | 0.081591 | 0.99398 | -0.042071 | 0.99336 | -0.046451 | 30.2189
23 | 0.018603 | 0.0046634 | -0.018594 | -0.0046601 | 9.1891e-06 | 3.2827e-06 | 0.027693 | 0.027693 | 0.027693 | 0.99959 | -0.0028497 | 0.99908 | -0.0064178 | 10.2567
24 | 0.0092552 | 0.0023194 | -0.0092525 | -0.0023187 | 2.7041e-06 | 7.4634e-07 | 0.013841 | 0.013841 | 0.013841 | 0.99499 | -0.03496 | 0.99469 | -0.037071 | 5.1264
25 | 0.043983 | 0.011032 | -0.04396 | -0.011024 | 2.2798e-05 | 8.6594e-06 | 0.065889 | 0.065889 | 0.065889 | 0.99336 | -0.046451 | 0.99283 | -0.050191 | 24.4032
26 | -0.0052217 | -0.0013087 | 0.0052221 | 0.0013087 | 4.1693e-07 | 1.8322e-08 | 0.007813 | 0.007813 | 0.007813 | 0.9945 | -0.038436 | 0.99458 | -0.037859 | 2.8937
27 | -0.0052221 | -0.0013087 | 0.0052227 | 0.0013087 | 5.6905e-07 | 2.4967e-08 | 0.007813 | 0.0078129 | 0.007813 | 0.99458 | -0.037859 | 0.99469 | -0.037071 | 2.8937
28 | 0.035545 | 0.0089146 | -0.035518 | -0.0089042 | 2.7411e-05 | 1.0343e-05 | 0.053276 | 0.053276 | 0.053276 | 0.99283 | -0.050191 | 0.99204 | -0.055758 | 19.7318
29 | -0.016522 | -0.0041408 | 0.01654 | 0.0041472 | 1.8351e-05 | 6.4429e-06 | 0.024821 | 0.024821 | 0.024821 | 0.99047 | -0.066824 | 0.9916 | -0.058809 | 9.1931
30 | -0.01654 | -0.0041472 | 0.016545 | 0.0041489 | 4.7514e-06 | 1.668e-06 | 0.024821 | 0.024821 | 0.024821 | 0.9916 | -0.058809 | 0.9919 | -0.056736 | 9.193
31 | -0.02 | -0.0050149 | 0.020002 | 0.0050155 | 1.7908e-06 | 6.476e-07 | 0.030005 | 0.030005 | 0.030005 | 0.9919 | -0.056736 | 0.99199 | -0.05609 | 11.1129
32 | 0.029144 | 0.007307 | -0.029143 | -0.0073065 | 1.34e-06 | 5.0087e-07 | 0.043716 | 0.043717 | 0.043717 | 0.99204 | -0.055758 | 0.99199 | -0.05609 | 16.1913

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15537 | 0.038878

## res_load
| p_mw | q_mvar
0 | 0.0083204 | 0.0020853
1 | 0.014817 | 0.0037134
2 | 0.0064238 | 0.00161
3 | 0.0070628 | 0.0017701
4 | 0.0058554 | 0.0014675
5 | 0.0039122 | 0.00098048
6 | 0.00378 | 0.00094736
7 | 0.005147 | 0.00129
8 | 0.005838 | 0.0014631
9 | 0.0041311 | 0.0010353
10 | 0.0077256 | 0.0019362
11 | 0.010482 | 0.0026272
12 | 0.0051036 | 0.0012791
13 | 0.0052217 | 0.0013087
14 | 0.0040298 | 0.00101
15 | 0.0084154 | 0.0021091
16 | 0.016522 | 0.0041408
17 | 0.0034555 | 0.00086602
18 | 0.0063731 | 0.0015973
19 | 0.0091409 | 0.0022909
20 | 0.011715 | 0.002936

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1