## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1311-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1311-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1311-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1311-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1311-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1311-3_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1311-3_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1311-3_0_3_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1311-3_0_3_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_1311-3_0_3_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1311-3_0_3_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_1311-3_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1311-3_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1311-3_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1311-3_0_3_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_1311-3_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1311-3_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1311-3_0_3_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_1311-3_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1311-3_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1311-3_0_3_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1311-3_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1311-3_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1311-3_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1311-3_0_3_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1311-3_0_3_node_128 | 0.4 | n |  | TRUE
26 | bus_LV_1311-3_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1311-3_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1311-3_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1311-3_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1311-3_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1311-3_0_3_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1311-3_0_3_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1311-3_0_3_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_1311-3_0_3_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_1311-3_0_3_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_1311-3_0_3_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_1311-3_0_3_node_49 | 0.4 | n |  | TRUE
38 | bus_LV_1311-3_0_3_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_1311-3_0_3_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_1311-3_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1311-3_0_3_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_1311-3_0_3_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1311-3_0_3_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_1311-3_0_3_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_1311-3_0_3_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1311-3_0_3_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_1311-3_0_3_node_57 | 0.4 | n |  | TRUE
48 | bus_LV_1311-3_0_3_node_71 | 0.4 | n |  | TRUE
49 | bus_LV_1311-3_0_3_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_1311-3_0_3_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_1311-3_0_3_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_1311-3_0_3_node_55 | 0.4 | n |  | TRUE
53 | bus_LV_1311-3_0_3_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_1311-3_0_3_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_1311-3_0_3_node_73 | 0.4 | n |  | TRUE
56 | bus_LV_1311-3_0_3_node_74 | 0.4 | n |  | TRUE
57 | bus_LV_1311-3_0_3_node_75 | 0.4 | n |  | TRUE
58 | bus_LV_1311-3_0_3_node_84 | 0.4 | n |  | TRUE
59 | bus_LV_1311-3_0_3_node_80 | 0.4 | n |  | TRUE
60 | bus_LV_1311-3_0_3_node_76 | 0.4 | n |  | TRUE
61 | bus_LV_1311-3_0_3_node_77 | 0.4 | n |  | TRUE
62 | bus_LV_1311-3_0_3_node_78 | 0.4 | n |  | TRUE
63 | bus_LV_1311-3_0_3_node_79 | 0.4 | n |  | TRUE
64 | bus_LV_1311-3_0_3_node_89 | 0.4 | n |  | TRUE
65 | bus_LV_1311-3_0_3_node_90 | 0.4 | n |  | TRUE
66 | bus_LV_1311-3_0_3_node_91 | 0.4 | n |  | TRUE
67 | bus_LV_1311-3_0_3_node_92 | 0.4 | n |  | TRUE
68 | bus_LV_1311-3_0_3_node_200 | 0.4 | n |  | TRUE
69 | bus_LV_1311-3_0_3_node_113 | 0.4 | n |  | TRUE
70 | bus_LV_1311-3_0_3_node_111 | 0.4 | n |  | TRUE
71 | bus_LV_1311-3_0_3_node_93 | 0.4 | n |  | TRUE
72 | bus_LV_1311-3_0_3_node_107 | 0.4 | n |  | TRUE
73 | bus_LV_1311-3_0_3_node_199 | 0.4 | n |  | TRUE
74 | bus_LV_1311-3_0_3_node_100 | 0.4 | n |  | TRUE
75 | bus_LV_1311-3_0_3_node_101 | 0.4 | n |  | TRUE
76 | bus_LV_1311-3_0_3_node_102 | 0.4 | n |  | TRUE
77 | bus_LV_1311-3_0_3_node_114 | 0.4 | n |  | TRUE
78 | bus_LV_1311-3_0_3_node_115 | 0.4 | n |  | TRUE
79 | bus_LV_1311-3_0_3_node_103 | 0.4 | n |  | TRUE
80 | bus_LV_1311-3_0_3_node_104 | 0.4 | n |  | TRUE
81 | bus_LV_1311-3_0_3_node_105 | 0.4 | n |  | TRUE
82 | bus_LV_1311-3_0_3_node_106 | 0.4 | n |  | TRUE
83 | bus_LV_1311-3_0_3_node_108 | 0.4 | n |  | TRUE
84 | bus_LV_1311-3_0_3_node_117 | 0.4 | n |  | TRUE
85 | bus_LV_1311-3_0_3_node_112 | 0.4 | n |  | TRUE
86 | bus_LV_1311-3_0_3_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_1311-3_0_3_node_119 | 0.4 | n |  | TRUE
88 | bus_LV_1311-3_0_3_node_118 | 0.4 | n |  | TRUE
89 | bus_LV_1311-3_0_3_node_121 | 0.4 | n |  | TRUE
90 | bus_LV_1311-3_0_3_node_127 | 0.4 | n |  | TRUE
91 | bus_LV_1311-3_0_3_node_122 | 0.4 | n |  | TRUE
92 | bus_LV_1311-3_0_3_node_123 | 0.4 | n |  | TRUE
93 | bus_LV_1311-3_0_3_node_124 | 0.4 | n |  | TRUE
94 | bus_LV_1311-3_0_3_node_125 | 0.4 | n |  | TRUE
95 | bus_LV_1311-3_0_3_node_126 | 0.4 | n |  | TRUE
96 | bus_LV_1311-3_0_3_node_198 | 0.4 | n |  | TRUE
97 | bus_MV_0_node_127 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1311-3_0_3_load_0 | 0 | 0.00055285 | 0.00013856 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1311-3_0_3_load_5 | 5 | 0.00039767 | 9.9666e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1311-3_0_3_load_6 | 6 | 0.00022021 | 5.5191e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1311-3_0_3_load_11 | 7 | 0.00069493 | 0.00017417 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1311-3_0_3_load_30 | 8 | 0.00020074 | 5.031e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1311-3_0_3_load_20 | 9 | 0.0002193 | 5.4962e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1311-3_0_3_load_41 | 10 | 0.00014447 | 3.6207e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1311-3_0_3_load_7 | 11 | 0.00022045 | 5.525e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1311-3_0_3_load_10 | 13 | 0.00054973 | 0.00013777 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1311-3_0_3_load_27 | 14 | 0.00051621 | 0.00012937 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1311-3_0_3_load_12 | 15 | 0.00026981 | 6.7621e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1311-3_0_3_load_50 | 17 | 0.00016606 | 4.1618e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1311-3_0_3_load_14 | 18 | 0.00011917 | 2.9867e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1311-3_0_3_load_15 | 19 | 0.000169 | 4.2357e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1311-3_0_3_load_21 | 20 | 0.00012783 | 3.2037e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1311-3_0_3_load_17 | 21 | 0.00022552 | 5.652e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1311-3_0_3_load_18 | 22 | 0.00082591 | 0.00020699 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1311-3_0_3_load_22 | 24 | 0.00039056 | 9.7884e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1311-3_0_3_load_128 | 25 | 0.0001656 | 4.1504e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1311-3_0_3_load_23 | 26 | 0.00027206 | 6.8184e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1311-3_0_3_load_25 | 27 | 0.00021471 | 5.3811e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1311-3_0_3_load_26 | 28 | 0.00040603 | 0.00010176 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1311-3_0_3_load_28 | 29 | 0.00014121 | 3.539e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1311-3_0_3_load_29 | 30 | 0.00042839 | 0.00010737 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1311-3_0_3_load_31 | 31 | 0.0012606 | 0.00031594 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1311-3_0_3_load_32 | 32 | 0.00010644 | 2.6676e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1311-3_0_3_load_34 | 34 | 0.00015358 | 3.849e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1311-3_0_3_load_36 | 36 | 0.00011246 | 2.8185e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1311-3_0_3_load_49 | 37 | 0.00027588 | 6.9141e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1311-3_0_3_load_46 | 38 | 0.00027581 | 6.9124e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1311-3_0_3_load_37 | 40 | 0.00019857 | 4.9766e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1311-3_0_3_load_38 | 41 | 0.00023815 | 5.9686e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1311-3_0_3_load_42 | 45 | 0.00035608 | 8.9243e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1311-3_0_3_load_71 | 48 | 0.00031843 | 7.9807e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1311-3_0_3_load_47 | 50 | 0.00039738 | 9.9592e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1311-3_0_3_load_48 | 51 | 0.00041462 | 0.00010391 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1311-3_0_3_load_55 | 52 | 0.00013172 | 3.3012e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1311-3_0_3_load_56 | 53 | 0.00026325 | 6.5976e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1311-3_0_3_load_73 | 55 | 0.00052564 | 0.00013174 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1311-3_0_3_load_74 | 56 | 0.00014969 | 3.7517e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1311-3_0_3_load_75 | 57 | 0.00032879 | 8.2403e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1311-3_0_3_load_84 | 58 | 0.00029432 | 7.3763e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1311-3_0_3_load_80 | 59 | 0.00026881 | 6.7369e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1311-3_0_3_load_76 | 60 | 0.00020154 | 5.051e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1311-3_0_3_load_77 | 61 | 0.00043698 | 0.00010952 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1311-3_0_3_load_79 | 63 | 0.00076108 | 0.00019074 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1311-3_0_3_load_89 | 64 | 0.00065282 | 0.00016361 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1311-3_0_3_load_90 | 65 | 0.0013015 | 0.00032618 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1311-3_0_3_load_91 | 66 | 0.00091421 | 0.00022912 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1311-3_0_3_load_113 | 69 | 0.00072983 | 0.00018291 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1311-3_0_3_load_111 | 70 | 0.00063534 | 0.00015923 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1311-3_0_3_load_107 | 72 | 0.0010886 | 0.00027284 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1311-3_0_3_load_100 | 74 | 0.00073181 | 0.00018341 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1311-3_0_3_load_101 | 75 | 0.0031623 | 0.00079255 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1311-3_0_3_load_115 | 78 | 0.0010238 | 0.00025658 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1311-3_0_3_load_103 | 79 | 0.0013214 | 0.00033118 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1311-3_0_3_load_104 | 80 | 0.00073987 | 0.00018543 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1311-3_0_3_load_105 | 81 | 0.00095912 | 0.00024038 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1311-3_0_3_load_106 | 82 | 0.00012578 | 3.1522e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1311-3_0_3_load_108 | 83 | 0.00022167 | 5.5556e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1311-3_0_3_load_120 | 86 | 0.0015803 | 0.00039606 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1311-3_0_3_load_119 | 87 | 0.00080994 | 0.00020299 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1311-3_0_3_load_118 | 88 | 0.00015851 | 3.9726e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1311-3_0_3_load_121 | 89 | 0.00058145 | 0.00014572 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1311-3_0_3_load_127 | 90 | 0.0002211 | 5.5413e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1311-3_0_3_load_122 | 91 | 0.00016577 | 4.1547e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1311-3_0_3_load_123 | 92 | 0.00014942 | 3.7449e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1311-3_0_3_load_124 | 93 | 0.00022889 | 5.7365e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1311-3_0_3_load_125 | 94 | 0.00022414 | 5.6174e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1311-3_0_3_load_198 | 96 | 0.00045917 | 0.00011508 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 90 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1311-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.02438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1311-3_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.021992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1311-3_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.22847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1311-3_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.17005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1311-3_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.34595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1311-3_0_3_line_5 | NAYY 4x150 SE | 2 | 6 | 0.063194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1311-3_0_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.030323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1311-3_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.10274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1311-3_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.0040819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1311-3_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.0047215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1311-3_0_3_line_10 | NAYY 4x150 SE | 7 | 15 | 0.069939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1311-3_0_3_line_11 | NAYY 4x150 SE | 8 | 30 | 0.0079663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1311-3_0_3_line_12 | NAYY 4x150 SE | 9 | 20 | 0.0058848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1311-3_0_3_line_13 | NAYY 4x150 SE | 11 | 12 | 0.033726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1311-3_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.020886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1311-3_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.011915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1311-3_0_3_line_16 | NAYY 4x150 SE | 14 | 28 | 0.0056174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1311-3_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.081768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1311-3_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.16532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1311-3_0_3_line_19 | NAYY 4x150 SE | 17 | 49 | 0.057709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1311-3_0_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.077372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1311-3_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.28367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1311-3_0_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.014252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1311-3_0_3_line_23 | NAYY 4x150 SE | 20 | 25 | 0.08303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1311-3_0_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.026981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1311-3_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.32758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1311-3_0_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.18342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1311-3_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.00035434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1311-3_0_3_line_28 | NAYY 4x150 SE | 25 | 95 | 0.12981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1311-3_0_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.15245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1311-3_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 1.4081e-06 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1311-3_0_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.031704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1311-3_0_3_line_32 | NAYY 4x150 SE | 31 | 32 | 0.11379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1311-3_0_3_line_33 | NAYY 4x150 SE | 31 | 33 | 0.014457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1311-3_0_3_line_34 | NAYY 4x150 SE | 32 | 34 | 0.25122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1311-3_0_3_line_35 | NAYY 4x150 SE | 33 | 35 | 0.30359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1311-3_0_3_line_36 | NAYY 4x150 SE | 33 | 36 | 0.0015989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1311-3_0_3_line_37 | NAYY 4x150 SE | 35 | 37 | 0.22088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1311-3_0_3_line_38 | NAYY 4x150 SE | 35 | 38 | 0.015449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1311-3_0_3_line_39 | NAYY 4x150 SE | 36 | 39 | 0.02653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1311-3_0_3_line_40 | NAYY 4x150 SE | 38 | 50 | 0.010008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1311-3_0_3_line_41 | NAYY 4x150 SE | 39 | 46 | 0.26202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1311-3_0_3_line_42 | NAYY 4x150 SE | 39 | 45 | 0.009997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1311-3_0_3_line_43 | NAYY 4x150 SE | 40 | 41 | 0.14271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1311-3_0_3_line_44 | NAYY 4x150 SE | 40 | 42 | 0.0044202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1311-3_0_3_line_45 | NAYY 4x150 SE | 42 | 43 | 0.29784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1311-3_0_3_line_46 | NAYY 4x150 SE | 43 | 44 | 0.35077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1311-3_0_3_line_47 | NAYY 4x150 SE | 43 | 45 | 0.026426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1311-3_0_3_line_48 | NAYY 4x150 SE | 44 | 47 | 0.31625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1311-3_0_3_line_49 | NAYY 4x150 SE | 44 | 48 | 0.018589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1311-3_0_3_line_50 | NAYY 4x150 SE | 46 | 49 | 0.12821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1311-3_0_3_line_51 | NAYY 4x150 SE | 47 | 53 | 0.043733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1311-3_0_3_line_52 | NAYY 4x150 SE | 48 | 54 | 0.27924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1311-3_0_3_line_53 | NAYY 4x150 SE | 50 | 51 | 0.00021511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1311-3_0_3_line_54 | NAYY 4x150 SE | 52 | 53 | 0.015487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1311-3_0_3_line_55 | NAYY 4x150 SE | 54 | 55 | 0.040715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1311-3_0_3_line_56 | NAYY 4x150 SE | 54 | 56 | 0.047988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1311-3_0_3_line_57 | NAYY 4x150 SE | 54 | 57 | 0.061452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1311-3_0_3_line_58 | NAYY 4x150 SE | 56 | 58 | 0.16505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1311-3_0_3_line_59 | NAYY 4x150 SE | 57 | 59 | 0.00073296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1311-3_0_3_line_60 | NAYY 4x150 SE | 59 | 62 | 0.033288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1311-3_0_3_line_61 | NAYY 4x150 SE | 60 | 61 | 0.015482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1311-3_0_3_line_62 | NAYY 4x150 SE | 60 | 62 | 0.11228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1311-3_0_3_line_63 | NAYY 4x150 SE | 61 | 63 | 0.045063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1311-3_0_3_line_64 | NAYY 4x150 SE | 64 | 65 | 0.020259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1311-3_0_3_line_65 | NAYY 4x150 SE | 64 | 66 | 0.003999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1311-3_0_3_line_66 | NAYY 4x150 SE | 65 | 67 | 0.14644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1311-3_0_3_line_67 | NAYY 4x150 SE | 66 | 68 | 0.19311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1311-3_0_3_line_68 | NAYY 4x150 SE | 67 | 69 | 0.021113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1311-3_0_3_line_69 | NAYY 4x150 SE | 67 | 70 | 0.039435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1311-3_0_3_line_70 | NAYY 4x150 SE | 68 | 73 | 0.089901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1311-3_0_3_line_71 | NAYY 4x150 SE | 69 | 86 | 0.041145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1311-3_0_3_line_72 | NAYY 4x150 SE | 70 | 85 | 0.33317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1311-3_0_3_line_73 | NAYY 4x150 SE | 71 | 72 | 0.080489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1311-3_0_3_line_74 | NAYY 4x150 SE | 71 | 73 | 0.1467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1311-3_0_3_line_75 | NAYY 4x150 SE | 72 | 81 | 0.003166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1311-3_0_3_line_76 | NAYY 4x150 SE | 73 | 96 | 0.038649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1311-3_0_3_line_77 | NAYY 4x150 SE | 74 | 75 | 0.034285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1311-3_0_3_line_78 | NAYY 4x150 SE | 75 | 76 | 0.038406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1311-3_0_3_line_79 | NAYY 4x150 SE | 76 | 77 | 0.12439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1311-3_0_3_line_80 | NAYY 4x150 SE | 76 | 78 | 0.15675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1311-3_0_3_line_81 | NAYY 4x150 SE | 77 | 79 | 0.054704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1311-3_0_3_line_82 | NAYY 4x150 SE | 77 | 85 | 0.092659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1311-3_0_3_line_83 | NAYY 4x150 SE | 78 | 87 | 0.024129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1311-3_0_3_line_84 | NAYY 4x150 SE | 80 | 81 | 0.13289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1311-3_0_3_line_85 | NAYY 4x150 SE | 80 | 82 | 0.083934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1311-3_0_3_line_86 | NAYY 4x150 SE | 82 | 83 | 0.021097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1311-3_0_3_line_87 | NAYY 4x150 SE | 83 | 84 | 0.089534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1311-3_0_3_line_88 | NAYY 4x150 SE | 84 | 88 | 0.14078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1311-3_0_3_line_89 | NAYY 4x150 SE | 86 | 89 | 0.040595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1311-3_0_3_line_90 | NAYY 4x150 SE | 89 | 90 | 0.27315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1311-3_0_3_line_91 | NAYY 4x150 SE | 90 | 95 | 0.17127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_1311-3_0_3_line_92 | NAYY 4x150 SE | 91 | 92 | 0.015179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1311-3_0_3_line_93 | NAYY 4x150 SE | 91 | 93 | 0.0045074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1311-3_0_3_line_94 | NAYY 4x150 SE | 92 | 94 | 0.045313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1311-3_0_3_line_95 | NAYY 4x150 SE | 93 | 95 | 0.0068608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1311-3_0_3_trafo_127 | 0.25 MVA 20/0.4 kV | 97 | 90 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26
0 | 2683654.0199 | 1207277.0481 | 2683652.228 | 1207264.3704 | 2683646.3708 | 1207256.8835 | 2683644.3255 | 1207256.5625
1 | 2683623.5984 | 1207259.8442 | 2683633.7669 | 1207254.9056 | 2683644.3255 | 1207256.5625
2 | 2683654.0199 | 1207277.0481 | 2683667.4463 | 1207275.1461 | 2683681.7003 | 1207268.4527 | 2683701.5853 | 1207255.0116 | 2683710.2232 | 1207257.8123 | 2683721.2312 | 1207258.6227 | 2683744.0442 | 1207250.6042 | 2683751.581 | 1207244.0723 | 2683753.8373 | 1207238.8228 | 2683753.9581 | 1207235.6336 | 2683754.4349 | 1207224.4219 | 2683756.466 | 1207214.0882 | 2683760.499 | 1207206.8734 | 2683775.0425 | 1207187.1647 | 2683777.144 | 1207173.4409 | 2683774.0603 | 1207165.5815 | 2683766.3754 | 1207157.1904 | 2683746.4971 | 1207143.5695
3 | 2683654.0199 | 1207277.0481 | 2683648.1563 | 1207285.2045 | 2683639.5435 | 1207295.813 | 2683635.4574 | 1207309.5424 | 2683641.0069 | 1207320.5272 | 2683649.9874 | 1207324.9225 | 2683688.6698 | 1207313.7463 | 2683734.1488 | 1207302.7324 | 2683754.0049 | 1207302.1883 | 2683756.2634 | 1207304.3659
4 | 2683623.5984 | 1207259.8442 | 2683621.6612 | 1207260.7843 | 2683613.1702 | 1207277.8986 | 2683595.2538 | 1207310.9691 | 2683586.2826 | 1207318.3927 | 2683574.3649 | 1207318.4704 | 2683570.2516 | 1207316.7784 | 2683563.8816 | 1207307.3498 | 2683549.6743 | 1207293.3419 | 2683535.4267 | 1207284.926 | 2683524.5353 | 1207279.0476 | 2683518.8034 | 1207277.2663 | 2683512.1147 | 1207278.6403 | 2683487.0048 | 1207293.7767 | 2683474.5388 | 1207298.2497 | 2683465.9326 | 1207301.3425 | 2683459.7569 | 1207303.5576 | 2683450.0549 | 1207301.2649 | 2683444.4424 | 1207296.3833 | 2683441.6626 | 1207293.954 | 2683444.0904 | 1207280.2235 | 2683449.8096 | 1207260.0794 | 2683452.6991 | 1207250.3135 | 2683451.5688 | 1207242.5037 | 2683446.0536 | 1207236.6451 | 2683434.4401 | 1207232.3578 | 2683404.989 | 1207216.968
5 | 2683623.5984 | 1207259.8442 | 2683618.0698 | 1207236.5072 | 2683601.7285 | 1207208.716 | 2683597.9864 | 1207202.8343
6 | 2683746.4971 | 1207143.5695 | 2683760.1703 | 1207116.5043
7 | 2683756.2634 | 1207304.3659 | 2683761.9804 | 1207309.9052 | 2683764.1139 | 1207316.6506 | 2683760.1341 | 1207327.6686 | 2683745.2731 | 1207347.8064 | 2683739.8777 | 1207364.864 | 2683743.2593 | 1207388.8825 | 2683745.1091 | 1207397.5023
8 | 2683401.7589 | 1207214.4755 | 2683404.8829 | 1207216.9126 | 2683404.989 | 1207216.968
9 | 2683597.9864 | 1207202.8343 | 2683595.452 | 1207198.8507
10 | 2683760.1703 | 1207116.5043 | 2683760.8198 | 1207115.2187 | 2683767.5053 | 1207104.3388 | 2683766.9639 | 1207084.3961 | 2683764.7515 | 1207068.099 | 2683762.5029 | 1207053.8361 | 2683764.0303 | 1207049.1874
11 | 2683745.1091 | 1207397.5023 | 2683746.7807 | 1207405.2912
12 | 2683401.7589 | 1207214.4755 | 2683397.1191 | 1207210.8557
13 | 2683798.4669 | 1207446.4388 | 2683781.5401 | 1207475.609
14 | 2683798.4669 | 1207446.4388 | 2683779.2425 | 1207438.275
15 | 2683779.2425 | 1207438.275 | 2683778.1318 | 1207437.8034 | 2683768.698 | 1207432.7365
16 | 2683763.7493 | 1207430.0786 | 2683768.698 | 1207432.7365
17 | 2683827.5786 | 1207071.2384 | 2683818.5982 | 1207068.4438 | 2683799.639 | 1207052.7231 | 2683781.0863 | 1207037.8309 | 2683772.114 | 1207037.7049 | 2683766.7611 | 1207040.8763 | 2683764.0303 | 1207049.1874
18 | 2683827.5786 | 1207071.2384 | 2683833.6493 | 1207071.1013 | 2683844.0089 | 1207070.4575 | 2683855.5933 | 1207064.3718 | 2683864.6347 | 1207043.8855 | 2683871.9066 | 1207019.9834 | 2683868.4682 | 1207003.2687 | 2683867.045 | 1206988.1945 | 2683871.0837 | 1206979.5123 | 2683881.5991 | 1206968.8754 | 2683904.3444 | 1206946.8363
19 | 2683907.9296 | 1206889.8277 | 2683908.1614 | 1206897.6804 | 2683906.3967 | 1206917.1682 | 2683908.2229 | 1206932.2481 | 2683904.3444 | 1206946.8363
20 | 2683207.1352 | 1207421.51 | 2683214.8404 | 1207429.3311 | 2683227.3228 | 1207444.9041 | 2683253.4831 | 1207483.2686
21 | 2683397.1191 | 1207210.8557 | 2683207.1352 | 1207421.51
22 | 2683261.3788 | 1207495.1319 | 2683257.5112 | 1207489.1758 | 2683253.4831 | 1207483.2686
23 | 2683397.1191 | 1207210.8557 | 2683387.5127 | 1207203.3613 | 2683368.5052 | 1207195.9466 | 2683359.2491 | 1207186.7559 | 2683347.0041 | 1207162.8806 | 2683341.5033 | 1207153.8584
24 | 2683265.8969 | 1207520.6044 | 2683265.001 | 1207515.9197 | 2683266.0501 | 1207502.3256 | 2683261.3788 | 1207495.1319
25 | 2683422.0105 | 1207607.8709 | 2683409.8758 | 1207608.2794 | 2683400.5451 | 1207611.5512 | 2683389.3322 | 1207613.4736 | 2683379.9531 | 1207619.6688 | 2683371.4649 | 1207630.1348 | 2683356.0552 | 1207647.7866 | 2683333.3367 | 1207658.9877 | 2683302.465 | 1207670.8423 | 2683290.5723 | 1207674.0785 | 2683279.6036 | 1207672.1353 | 2683273.6899 | 1207667.6055 | 2683271.6051 | 1207661.15 | 2683276.4627 | 1207646.008 | 2683282.6116 | 1207633.1521 | 2683281.4935 | 1207617.9156 | 2683280.7206 | 1207592.1104 | 2683276.1344 | 1207574.1904 | 2683278.4167 | 1207567.0398 | 2683282.7215 | 1207557.1824 | 2683283.2244 | 1207548.3948 | 2683276.283 | 1207536.3013 | 2683266.5957 | 1207524.2584 | 2683265.8969 | 1207520.6044
26 | 2683422.0105 | 1207607.8709 | 2683446.5627 | 1207789.6436
27 | 2683446.7484 | 1207789.9454 | 2683446.5627 | 1207789.6436
28 | 2683282.2125 | 1207059.1763 | 2683284.2357 | 1207070.6008 | 2683289.7812 | 1207078.6723 | 2683294.3014 | 1207087.73 | 2683296.807 | 1207095.6479 | 2683295.3881 | 1207103.044 | 2683290.6108 | 1207115.1296 | 2683291.9606 | 1207122.4865 | 2683294.469 | 1207126.3906 | 2683302.5242 | 1207132.2735 | 2683325.5147 | 1207137.6755 | 2683331.4563 | 1207139.7042 | 2683334.841 | 1207142.9313 | 2683341.5033 | 1207153.8584
29 | 2683326.7495 | 1207843.1481 | 2683333.5818 | 1207833.615 | 2683338.7066 | 1207821.6678 | 2683346.8533 | 1207813.3094 | 2683368.0212 | 1207794.9487 | 2683383.0095 | 1207787.8312 | 2683391.5843 | 1207786.9393 | 2683395.279 | 1207785.3677 | 2683399.6419 | 1207779.5248 | 2683405.6021 | 1207776.3616 | 2683416.4217 | 1207775.9014 | 2683425.3757 | 1207777.2496 | 2683437.4863 | 1207783.9787 | 2683446.7484 | 1207789.9454 | 2683446.7484 | 1207789.9454
30 | 2683763.7493 | 1207430.0786 | 2683763.748 | 1207430.0779
31 | 2683746.7807 | 1207405.2912 | 2683748.9553 | 1207415.424 | 2683754.1839 | 1207423.7916 | 2683759.8513 | 1207427.985 | 2683763.748 | 1207430.0779
32 | 2683629.3079 | 1206673.3901 | 2683626.4521 | 1206680.7105 | 2683625.2069 | 1206690.3326 | 2683631.0192 | 1206709.7488 | 2683634.6449 | 1206720.7511 | 2683641.2336 | 1206731.4391 | 2683641.3554 | 1206739.5683 | 2683637.2844 | 1206743.5138 | 2683624.0106 | 1206746.3853 | 2683612.9453 | 1206751.7672 | 2683608.6121 | 1206757.5991 | 2683607.5863 | 1206762.3609
33 | 2683634.562 | 1206659.9218 | 2683629.3079 | 1206673.3901
34 | 2683543.3578 | 1206861.853 | 2683547.8571 | 1206860.982 | 2683561.1591 | 1206864.2258 | 2683582.4487 | 1206871.1171 | 2683589.4712 | 1206875.8074 | 2683603.2389 | 1206880.0028 | 2683611.4843 | 1206881.5415 | 2683623.2154 | 1206879.1042 | 2683631.5842 | 1206880.5223 | 2683639.6106 | 1206880.8683 | 2683650.3624 | 1206881.019 | 2683653.5747 | 1206879.1851 | 2683656.1195 | 1206866.3792 | 2683654.5943 | 1206840.0964 | 2683650.555 | 1206824.9634 | 2683630.9779 | 1206805.4877 | 2683616.2323 | 1206795.6304 | 2683609.3981 | 1206785.6393 | 2683605.8301 | 1206770.513 | 2683607.5863 | 1206762.3609
35 | 2683431.4193 | 1206553.1111 | 2683438.4725 | 1206558.9023 | 2683450.4048 | 1206566.5962 | 2683474.327 | 1206577.3042 | 2683484.191 | 1206586.5925 | 2683492.9818 | 1206599.735 | 2683499.7462 | 1206612.0264 | 2683504.7234 | 1206621.0462 | 2683503.2972 | 1206635.4578 | 2683504.3743 | 1206645.446 | 2683511.012 | 1206652.6545 | 2683538.1846 | 1206664.2199 | 2683554.9462 | 1206676.251 | 2683565.9933 | 1206689.0139 | 2683570.4977 | 1206694.8473 | 2683577.6949 | 1206701.1966 | 2683586.4695 | 1206700.8081 | 2683592.1925 | 1206695.6627 | 2683594.6834 | 1206679.6428 | 2683599.5288 | 1206668.7369 | 2683607.9029 | 1206667.6312 | 2683615.2003 | 1206669.0009 | 2683623.4076 | 1206667.8485 | 2683634.562 | 1206659.9218
36 | 2683634.562 | 1206659.9218 | 2683635.8635 | 1206658.9929
37 | 2683431.4193 | 1206553.1111 | 2683421.8047 | 1206554.8112 | 2683407.524 | 1206554.6116 | 2683395.7505 | 1206550.7891 | 2683382.7566 | 1206546.1269 | 2683369.649 | 1206549.6016 | 2683364.6345 | 1206558.4818 | 2683366.4906 | 1206571.5272 | 2683370.4698 | 1206578.4984 | 2683382.5593 | 1206589.641 | 2683393.0913 | 1206594.6691 | 2683397.8974 | 1206601.2516 | 2683397.7838 | 1206609.3775 | 2683389.8533 | 1206622.2861 | 2683380.8122 | 1206627.0407 | 2683367.4644 | 1206631.3905 | 2683366.4634 | 1206631.7212 | 2683351.301 | 1206636.3903 | 2683341.4066 | 1206643.9793 | 2683331.1606 | 1206651.1567
38 | 2683431.4193 | 1206553.1111 | 2683432.4659 | 1206540.8178 | 2683431.6507 | 1206537.8153
39 | 2683660.9201 | 1206650.9075 | 2683653.4132 | 1206652.003 | 2683637.2355 | 1206658.0136 | 2683635.8635 | 1206658.9929
40 | 2683431.6507 | 1206537.8153 | 2683429.0286 | 1206528.1572
41 | 2683660.9201 | 1206650.9075 | 2683667.4817 | 1206658.104 | 2683675.0785 | 1206678.8016 | 2683674.0094 | 1206716.5332 | 2683678.6679 | 1206728.1838 | 2683687.5289 | 1206731.3989 | 2683699.8153 | 1206740.9106 | 2683712.3351 | 1206758.7198 | 2683723.2141 | 1206767.1667 | 2683735.4713 | 1206778.746 | 2683745.2055 | 1206792.8917 | 2683758.2206 | 1206800.8572 | 2683768.0931 | 1206805.1429 | 2683784.3384 | 1206810.5521 | 2683799.1179 | 1206819.065 | 2683808.9394 | 1206826.9746 | 2683819.1255 | 1206834.3779
42 | 2683660.9201 | 1206650.9075 | 2683661.2824 | 1206644.5974 | 2683661.9791 | 1206640.9875
43 | 2683433.2375 | 1206473.0669 | 2683413.8469 | 1206455.4027 | 2683409.6861 | 1206451.0751 | 2683406.0137 | 1206441.74 | 2683393.9171 | 1206428.9073 | 2683379.3101 | 1206417.1958 | 2683364.1638 | 1206410.3354 | 2683350.6481 | 1206399.9845 | 2683342.986 | 1206392.5728 | 2683334.7155 | 1206374.6096
44 | 2683436.5051 | 1206476.0437 | 2683433.2375 | 1206473.0669
45 | 2683669.0331 | 1206615.8096 | 2683655.315 | 1206612.3708 | 2683636.1158 | 1206606.587 | 2683621.9294 | 1206602.3745 | 2683611.0161 | 1206597.9744 | 2683600.7473 | 1206595.34 | 2683591.947 | 1206593.7491 | 2683579.3617 | 1206597.3975 | 2683570.6076 | 1206596.3076 | 2683555.2228 | 1206595.6585 | 2683547.5841 | 1206590.9597 | 2683533.8101 | 1206586.6198 | 2683518.5996 | 1206583.2938 | 2683512.0763 | 1206578.7774 | 2683498.5788 | 1206566.6364 | 2683484.9395 | 1206558.6405 | 2683480.1375 | 1206552.8585 | 2683476.1855 | 1206541.7739 | 2683471.1223 | 1206523.6693 | 2683464.4791 | 1206502.7073 | 2683453.7226 | 1206487.0691 | 2683444.7401 | 1206478.9161 | 2683436.5051 | 1206476.0437
46 | 2683783.1785 | 1206473.3628 | 2683749.3493 | 1206515.5154 | 2683749.3708 | 1206524.8217 | 2683753.4019 | 1206530.2373 | 2683762.6463 | 1206537.5828 | 2683767.776 | 1206545.4709 | 2683775.203 | 1206559.2841 | 2683784.4963 | 1206577.226 | 2683801.1829 | 1206601.0756 | 2683815.4159 | 1206626.3249 | 2683817.2311 | 1206633.0103 | 2683815.6053 | 1206636.6676 | 2683810.5916 | 1206643.2793 | 2683805.7418 | 1206644.7232 | 2683798.4019 | 1206644.7536 | 2683768.5426 | 1206631.1814 | 2683758.1958 | 1206628.1565 | 2683712.235 | 1206622.7307 | 2683698.3909 | 1206619.6013 | 2683678.0203 | 1206614.368 | 2683673.2699 | 1206614.1457 | 2683669.0331 | 1206615.8096
47 | 2683669.0331 | 1206615.8096 | 2683665.6811 | 1206621.622 | 2683663.628 | 1206632.4446 | 2683661.9791 | 1206640.9875
48 | 2683783.1785 | 1206473.3628 | 2683788.193 | 1206476.4462 | 2683800.0987 | 1206501.7185 | 2683810.5493 | 1206521.2 | 2683818.9122 | 1206534.9818 | 2683829.3355 | 1206550.9829 | 2683835.7445 | 1206560.9126 | 2683840.6193 | 1206569.6089 | 2683844.1217 | 1206574.2166 | 2683850.5066 | 1206575.5738 | 2683855.0741 | 1206572.0356 | 2683857.3574 | 1206563.262 | 2683873.1044 | 1206526.2482 | 2683886.9953 | 1206506.0303 | 2683895.8027 | 1206486.5637 | 2683898.1767 | 1206471.8876 | 2683900.2806 | 1206467.2253 | 2683903.7622 | 1206466.8184 | 2683908.5881 | 1206470.8777 | 2683909.5968 | 1206478.6524 | 2683910.2372 | 1206485.577 | 2683915.0354 | 1206498.097 | 2683925.3632 | 1206516.5429 | 2683933.811 | 1206523.733
49 | 2683783.1785 | 1206473.3628 | 2683783.6972 | 1206461.8738 | 2683782.658 | 1206454.8619
50 | 2683907.9296 | 1206889.8277 | 2683904.4874 | 1206890.691 | 2683889.1273 | 1206896.4566 | 2683878.018 | 1206897.9349 | 2683864.2758 | 1206892.4827 | 2683845.3502 | 1206887.3247 | 2683838.3436 | 1206881.5226 | 2683836.3947 | 1206877.8707 | 2683831.9173 | 1206854.9819 | 2683829.2031 | 1206841.9243 | 2683824.1269 | 1206836.216 | 2683819.1255 | 1206834.3779
51 | 2683933.811 | 1206523.733 | 2683935.72 | 1206525.3608 | 2683945.29 | 1206533.3338 | 2683950.5766 | 1206545.1825 | 2683951.7317 | 1206553.3596 | 2683947.4174 | 1206559.5377
52 | 2683704.3917 | 1206190.698 | 2683725.2711 | 1206233.496 | 2683756.2226 | 1206296.2149 | 2683766.929 | 1206325.6841 | 2683768.8392 | 1206368.9499 | 2683778.674 | 1206427.9814 | 2683782.658 | 1206454.8619
53 | 2683429.0286 | 1206528.1572 | 2683428.9722 | 1206527.9496
54 | 2683936.1591 | 1206570.0068 | 2683945.2349 | 1206562.6631 | 2683947.4174 | 1206559.5377
55 | 2683704.3917 | 1206190.698 | 2683701.9946 | 1206191.8651 | 2683699.205 | 1206197.1516 | 2683697.057 | 1206203.3366 | 2683694.4038 | 1206228.7269
56 | 2683704.3917 | 1206190.698 | 2683692.9371 | 1206153.7914 | 2683688.8621 | 1206145.3823
57 | 2683704.3917 | 1206190.698 | 2683704.9479 | 1206210.6964 | 2683712.4768 | 1206251.4527
58 | 2683603.1002 | 1206004.9147 | 2683630.3203 | 1206041.0527 | 2683651.2428 | 1206083.0283 | 2683681.9521 | 1206131.1229 | 2683688.8621 | 1206145.3823
59 | 2683712.4768 | 1206251.4527 | 2683712.6099 | 1206252.1735
60 | 2683715.7966 | 1206284.8073 | 2683717.4535 | 1206278.3931 | 2683712.6099 | 1206252.1735
61 | 2683694.4594 | 1206394.5122 | 2683694.4594 | 1206394.5122 | 2683679.9401 | 1206399.8858
62 | 2683715.7966 | 1206284.8073 | 2683714.5221 | 1206299.7547 | 2683712.2668 | 1206322.8046 | 2683709.6886 | 1206338.5119 | 2683706.1065 | 1206358.0075 | 2683700.5989 | 1206378.677 | 2683694.4594 | 1206394.5122
63 | 2683679.9401 | 1206399.8858 | 2683671.622 | 1206402.9643 | 2683659.6381 | 1206413.5921 | 2683657.3709 | 1206422.8663 | 2683652.9634 | 1206432.5381
64 | 2682813.3981 | 1206644.698 | 2682820.3253 | 1206642.8171 | 2682828.3355 | 1206643.2507 | 2682833.0763 | 1206645.0168
65 | 2682813.3981 | 1206644.698 | 2682811.9885 | 1206645.0807 | 2682809.684 | 1206646.1449
66 | 2682962.8793 | 1206692.9728 | 2682957.6319 | 1206696.2242 | 2682953.407 | 1206697.0438 | 2682950.6223 | 1206694.9371 | 2682942.0336 | 1206685.7786 | 2682938.0688 | 1206683.2107 | 2682932.3085 | 1206680.6846 | 2682909.4566 | 1206674.4633 | 2682896.3129 | 1206671.8236 | 2682880.5448 | 1206670.3037 | 2682865.7209 | 1206668.1632 | 2682857.6886 | 1206664.9386 | 2682850.8605 | 1206659.885 | 2682843.9559 | 1206651.028 | 2682839.8365 | 1206647.5353 | 2682833.0763 | 1206645.0168
67 | 2682809.684 | 1206646.1449 | 2682616.7128 | 1206653.4922
68 | 2682962.8793 | 1206692.9728 | 2682976.735 | 1206708.9029
69 | 2682962.8793 | 1206692.9728 | 2682940.8391 | 1206668.8511 | 2682936.2883 | 1206663.8518
70 | 2682616.7128 | 1206653.4922 | 2682621.8328 | 1206666.0266 | 2682628.3694 | 1206677.858 | 2682633.5038 | 1206688.2468 | 2682635.3772 | 1206699.6023 | 2682627.0768 | 1206712.4401 | 2682609.9122 | 1206729.9472
71 | 2682976.735 | 1206708.9029 | 2682999.7245 | 1206735.3343 | 2683004.2947 | 1206739.3957
72 | 2682780.5675 | 1206492.8361 | 2682780.6236 | 1206495.3719 | 2682778.3143 | 1206499.5536 | 2682773.7743 | 1206502.248 | 2682767.8612 | 1206501.9436 | 2682747.5546 | 1206493.112 | 2682740.4882 | 1206493.1586 | 2682734.5348 | 1206495.2108 | 2682729.2622 | 1206504.666 | 2682730.6847 | 1206512.3351 | 2682738.6996 | 1206516.282 | 2682756.0425 | 1206521.6369 | 2682774.2696 | 1206530.1394 | 2682794.7401 | 1206540.3075 | 2682816.9529 | 1206553.1683 | 2682863.8291 | 1206590.7984 | 2682875.2007 | 1206601.6632 | 2682880.942 | 1206609.9482 | 2682888.6994 | 1206624.7543 | 2682892.6856 | 1206630.1686 | 2682899.3163 | 1206635.7421 | 2682911.9394 | 1206643.022 | 2682927.5647 | 1206654.2684 | 2682936.2883 | 1206663.8518
73 | 2682722.0287 | 1206824.5491 | 2682735.552 | 1206820.0891 | 2682750.9257 | 1206813.8204 | 2682757.7435 | 1206810.2904 | 2682776.3013 | 1206793.7926 | 2682784.0184 | 1206796.1566 | 2682792.9153 | 1206794.4094
74 | 2682722.0287 | 1206824.5491 | 2682609.9122 | 1206729.9472
75 | 2682792.9153 | 1206794.4094 | 2682796.022 | 1206793.7993
76 | 2682609.9122 | 1206729.9472 | 2682609.8046 | 1206717.938 | 2682609.9104 | 1206710.3012 | 2682608.385 | 1206701.8191 | 2682600.8294 | 1206694.6961
77 | 2682836.9339 | 1206423.0307 | 2682838.242 | 1206430.3847 | 2682847.116 | 1206445.8733 | 2682854.4508 | 1206451.0284
78 | 2682879.3409 | 1206477.7076 | 2682876.2133 | 1206466.3236 | 2682854.4508 | 1206451.0284
79 | 2682765.0631 | 1206445.9466 | 2682785.5687 | 1206448.1212 | 2682796.2588 | 1206450.0373 | 2682806.6322 | 1206453.9392 | 2682820.9673 | 1206461.1982 | 2682843.6186 | 1206473.7205 | 2682864.559 | 1206483.4617 | 2682873.0609 | 1206483.5576 | 2682879.3409 | 1206477.7076
80 | 2682879.3409 | 1206477.7076 | 2682900.5694 | 1206486.419 | 2682947.5284 | 1206520.8266 | 2682976.3691 | 1206535.0698 | 2682997.756 | 1206553.1453 | 2683006.9366 | 1206565.5288
81 | 2682765.0631 | 1206445.9466 | 2682779.7552 | 1206437.3448 | 2682786.9012 | 1206432.1183 | 2682791.6607 | 1206413.0609 | 2682793.5255 | 1206404.0693
82 | 2682765.0631 | 1206445.9466 | 2682744.9905 | 1206448.748 | 2682739.1559 | 1206454.8489 | 2682737.7637 | 1206461.456 | 2682743.2994 | 1206468.6818 | 2682752.9331 | 1206472.729 | 2682766.9699 | 1206476.2703 | 2682777.3864 | 1206482.5521 | 2682780.4929 | 1206488.8881 | 2682780.5675 | 1206492.8361
83 | 2683018.6567 | 1206586.4795 | 2683012.4558 | 1206572.9735 | 2683006.9366 | 1206565.5288
84 | 2682854.568 | 1206866.6694 | 2682854.568 | 1206866.6694 | 2682853.2937 | 1206862.5936 | 2682854.2071 | 1206860.3492 | 2682851.6582 | 1206858.2347 | 2682846.3904 | 1206855.849 | 2682816.0477 | 1206841.9747 | 2682815.2123 | 1206839.695 | 2682816.5753 | 1206836.8343 | 2682827.6004 | 1206828.8043 | 2682826.4181 | 1206826.3196 | 2682805.4369 | 1206815.7662 | 2682787.9345 | 1206809.3639 | 2682786.0718 | 1206807.6703 | 2682787.1447 | 1206805.4393 | 2682796.022 | 1206793.7993
85 | 2682854.568 | 1206866.6694 | 2682852.4864 | 1206868.1526 | 2682838.459 | 1206873.8617 | 2682837.4285 | 1206876.3267 | 2682842.5896 | 1206882.5579 | 2682857.0928 | 1206896.2568 | 2682855.6618 | 1206899.0832 | 2682852.5213 | 1206903.4313 | 2682851.0404 | 1206909.8483 | 2682847.5075 | 1206923.8416 | 2682842.652 | 1206927.3158
86 | 2682842.652 | 1206927.3158 | 2682841.6848 | 1206928.0079 | 2682826.2927 | 1206940.6331
87 | 2682772.2311 | 1207008.2518 | 2682779.4561 | 1206995.088 | 2682799.1589 | 1206966.7429 | 2682811.7084 | 1206945.848 | 2682824.7299 | 1206941.915 | 2682826.2927 | 1206940.6331
88 | 2682772.2311 | 1207008.2518 | 2682784.8324 | 1207000.6105 | 2682796.074 | 1206998.8764 | 2682804.2054 | 1206999.8676 | 2682807.2851 | 1207002.6343 | 2682807.3989 | 1207007.5835 | 2682790.8041 | 1207028.4446 | 2682790.6812 | 1207030.7221 | 2682793.346 | 1207031.6041 | 2682827.6181 | 1207036.8272 | 2682836.3995 | 1207041.3853 | 2682850.3588 | 1207057.5338
89 | 2683034.6394 | 1206766.362 | 2683004.2947 | 1206739.3957
90 | 2683034.6394 | 1206766.362 | 2683038.7448 | 1206770.0103 | 2683075.8007 | 1206810.2738 | 2683117.0053 | 1206850.2286 | 2683170.7756 | 1206879.107 | 2683188.5658 | 1206898.1004 | 2683231.8354 | 1206924.5871 | 2683248.7797 | 1206929.8777
91 | 2683282.2125 | 1207059.1763 | 2683298.7964 | 1207012.5221 | 2683303.559 | 1206980.8014 | 2683304.4415 | 1206965.5261 | 2683304.7157 | 1206957.3246 | 2683296.2514 | 1206942.5971 | 2683270.7871 | 1206936.7492 | 2683248.7797 | 1206929.8777
92 | 2683277.8559 | 1207049.9248 | 2683277.9904 | 1207034.7461
93 | 2683277.8559 | 1207049.9248 | 2683277.816 | 1207054.4321
94 | 2683283.484 | 1206992.5956 | 2683288.2021 | 1206999.477 | 2683283.4915 | 1207023.1154 | 2683277.9904 | 1207034.7461 | 2683277.9904 | 1207034.7461
95 | 2683282.2125 | 1207059.1763 | 2683277.8052 | 1207055.6459 | 2683277.816 | 1207054.4321

## bus_geodata
| x | y | coords
0 | 2683644.3255 | 1207256.5625
1 | 2683654.0199 | 1207277.0481
2 | 2683623.5984 | 1207259.8442
3 | 2683746.4971 | 1207143.5695
4 | 2683756.2634 | 1207304.3659
5 | 2683404.989 | 1207216.968
6 | 2683597.9864 | 1207202.8343
7 | 2683760.1703 | 1207116.5043
8 | 2683745.1091 | 1207397.5023
9 | 2683401.7589 | 1207214.4754
10 | 2683595.452 | 1207198.8507
11 | 2683781.5401 | 1207475.609
12 | 2683798.4669 | 1207446.4388
13 | 2683779.2425 | 1207438.275
14 | 2683768.698 | 1207432.7365
15 | 2683764.0303 | 1207049.1874
16 | 2683827.5786 | 1207071.2384
17 | 2683904.3444 | 1206946.8363
18 | 2683207.1352 | 1207421.5101
19 | 2683253.4831 | 1207483.2686
20 | 2683397.1191 | 1207210.8557
21 | 2683261.3788 | 1207495.1319
22 | 2683265.8969 | 1207520.6044
23 | 2683422.0105 | 1207607.8709
24 | 2683446.5627 | 1207789.6436
25 | 2683341.5033 | 1207153.8584
26 | 2683446.7484 | 1207789.9454
27 | 2683326.7495 | 1207843.1481
28 | 2683763.7493 | 1207430.0786
29 | 2683763.748 | 1207430.0779
30 | 2683746.7807 | 1207405.2912
31 | 2683629.3079 | 1206673.3901
32 | 2683607.5863 | 1206762.3609
33 | 2683634.562 | 1206659.9218
34 | 2683543.3578 | 1206861.853
35 | 2683431.4193 | 1206553.1111
36 | 2683635.8635 | 1206658.9929
37 | 2683331.1606 | 1206651.1567
38 | 2683431.6507 | 1206537.8153
39 | 2683660.9201 | 1206650.9075
40 | 2683433.2375 | 1206473.0669
41 | 2683334.7155 | 1206374.6096
42 | 2683436.5051 | 1206476.0437
43 | 2683669.0331 | 1206615.8096
44 | 2683783.1785 | 1206473.3628
45 | 2683661.9791 | 1206640.9875
46 | 2683819.1255 | 1206834.3779
47 | 2683933.811 | 1206523.733
48 | 2683782.658 | 1206454.8619
49 | 2683907.9296 | 1206889.8277
50 | 2683429.0286 | 1206528.1572
51 | 2683428.9722 | 1206527.9496
52 | 2683936.1591 | 1206570.0068
53 | 2683947.4174 | 1206559.5377
54 | 2683704.3917 | 1206190.698
55 | 2683694.4038 | 1206228.7269
56 | 2683688.8621 | 1206145.3823
57 | 2683712.4768 | 1206251.4527
58 | 2683603.1002 | 1206004.9147
59 | 2683712.6099 | 1206252.1735
60 | 2683694.4594 | 1206394.5122
61 | 2683679.9401 | 1206399.8858
62 | 2683715.7967 | 1206284.8073
63 | 2683652.9634 | 1206432.5381
64 | 2682813.3981 | 1206644.698
65 | 2682833.0763 | 1206645.0168
66 | 2682809.684 | 1206646.1449
67 | 2682962.8793 | 1206692.9728
68 | 2682616.7128 | 1206653.4922
69 | 2682976.735 | 1206708.9029
70 | 2682936.2883 | 1206663.8518
71 | 2682722.0287 | 1206824.5491
72 | 2682792.9153 | 1206794.4094
73 | 2682609.9122 | 1206729.9472
74 | 2682836.9339 | 1206423.0307
75 | 2682854.4508 | 1206451.0284
76 | 2682879.3409 | 1206477.7076
77 | 2682765.0631 | 1206445.9466
78 | 2683006.9366 | 1206565.5288
79 | 2682793.5255 | 1206404.0693
80 | 2682854.568 | 1206866.6694
81 | 2682796.022 | 1206793.7993
82 | 2682842.652 | 1206927.3158
83 | 2682826.2927 | 1206940.6331
84 | 2682772.2312 | 1207008.2518
85 | 2682780.5675 | 1206492.8361
86 | 2683004.2947 | 1206739.3957
87 | 2683018.6567 | 1206586.4795
88 | 2682850.3588 | 1207057.5338
89 | 2683034.6394 | 1206766.362
90 | 2683248.7797 | 1206929.8777
91 | 2683277.8559 | 1207049.9248
92 | 2683277.9904 | 1207034.7461
93 | 2683277.816 | 1207054.4321
94 | 2683283.484 | 1206992.5956
95 | 2683282.2125 | 1207059.1763
96 | 2682600.8294 | 1206694.6961
97 | 2683248.7797 | 1206929.8777

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98679 | -0.095309 | 0.00055285 | 0.00013856
1 | 0.9864 | -0.098177 | 0 | 0
2 | 0.98716 | -0.092598 | 0 | 0
3 | 0.98353 | -0.11924 | 0 | 0
4 | 0.98579 | -0.10252 | 0 | 0
5 | 0.9932 | -0.048867 | 0.00039767 | 9.9666e-05
6 | 0.98713 | -0.092836 | 0.00022021 | 5.5191e-05
7 | 0.98315 | -0.12204 | 0.00069493 | 0.00017417
8 | 0.98543 | -0.10514 | 0.00020074 | 5.031e-05
9 | 0.99327 | -0.048338 | 0.0002193 | 5.4962e-05
10 | 0.98713 | -0.092843 | 0.00014447 | 3.6207e-05
11 | 0.98528 | -0.10622 | 0.00022045 | 5.525e-05
12 | 0.98529 | -0.10615 | 0 | 0
13 | 0.98529 | -0.1061 | 0.00054973 | 0.00013777
14 | 0.98531 | -0.106 | 0.00051621 | 0.00012937
15 | 0.98234 | -0.12801 | 0.00026981 | 6.7621e-05
16 | 0.98143 | -0.13476 | 0 | 0
17 | 0.97958 | -0.14842 | 0.00016606 | 4.1618e-05
18 | 0.99248 | -0.054182 | 0.00011917 | 2.9867e-05
19 | 0.99225 | -0.055883 | 0.000169 | 4.2357e-05
20 | 0.99338 | -0.047561 | 0.00012783 | 3.2037e-05
21 | 0.99221 | -0.056172 | 0.00022552 | 5.652e-05
22 | 0.99214 | -0.056656 | 0.00082591 | 0.00020699
23 | 0.99173 | -0.059731 | 0 | 0
24 | 0.9915 | -0.061408 | 0.00039056 | 9.7884e-05
25 | 0.99518 | -0.034565 | 0.0001656 | 4.1504e-05
26 | 0.9915 | -0.06141 | 0.00027206 | 6.8184e-05
27 | 0.99145 | -0.061753 | 0.00021471 | 5.3811e-05
28 | 0.98532 | -0.10593 | 0.00040603 | 0.00010176
29 | 0.98532 | -0.10593 | 0.00014121 | 3.539e-05
30 | 0.9854 | -0.10533 | 0.00042839 | 0.00010737
31 | 0.97453 | -0.18594 | 0.0012606 | 0.00031594
32 | 0.97449 | -0.18628 | 0.00010644 | 2.6676e-05
33 | 0.97456 | -0.1857 | 0 | 0
34 | 0.97443 | -0.18672 | 0.00015358 | 3.849e-05
35 | 0.97396 | -0.19017 | 0 | 0
36 | 0.97457 | -0.18565 | 0.00011246 | 2.8185e-05
37 | 0.97387 | -0.19084 | 0.00027588 | 6.9141e-05
38 | 0.97393 | -0.19035 | 0.00027581 | 6.9124e-05
39 | 0.97469 | -0.18479 | 0 | 0
40 | 0.97427 | -0.18795 | 0.00019857 | 4.9766e-05
41 | 0.97422 | -0.18832 | 0.00023815 | 5.9686e-05
42 | 0.97427 | -0.18793 | 0 | 0
43 | 0.97446 | -0.18648 | 0 | 0
44 | 0.97257 | -0.20054 | 0 | 0
45 | 0.97462 | -0.18528 | 0.00035608 | 8.9243e-05
46 | 0.97755 | -0.1635 | 0 | 0
47 | 0.97239 | -0.20193 | 0 | 0
48 | 0.97248 | -0.2012 | 0.00031843 | 7.9807e-05
49 | 0.97895 | -0.1531 | 0 | 0
50 | 0.97392 | -0.19044 | 0.00039738 | 9.9592e-05
51 | 0.97392 | -0.19044 | 0.00041462 | 0.00010391
52 | 0.97236 | -0.20213 | 0.00013172 | 3.3012e-05
53 | 0.97236 | -0.20211 | 0.00026325 | 6.5976e-05
54 | 0.97127 | -0.21013 | 0 | 0
55 | 0.97123 | -0.21036 | 0.00052564 | 0.00013174
56 | 0.97123 | -0.21037 | 0.00014969 | 3.7517e-05
57 | 0.97108 | -0.21145 | 0.00032879 | 8.2403e-05
58 | 0.97116 | -0.21089 | 0.00029432 | 7.3763e-05
59 | 0.97108 | -0.21146 | 0.00026881 | 6.7369e-05
60 | 0.97078 | -0.21363 | 0.00020154 | 5.051e-05
61 | 0.97076 | -0.21383 | 0.00043698 | 0.00010952
62 | 0.97101 | -0.21196 | 0 | 0
63 | 0.97071 | -0.2142 | 0.00076108 | 0.00019074
64 | 0.98937 | -0.075349 | 0.00065282 | 0.00016361
65 | 0.98952 | -0.07423 | 0.0013015 | 0.00032618
66 | 0.98934 | -0.075544 | 0.00091421 | 0.00022912
67 | 0.99092 | -0.064202 | 0 | 0
68 | 0.9883 | -0.083114 | 0 | 0
69 | 0.99136 | -0.06109 | 0.00072983 | 0.00018291
70 | 0.99048 | -0.067317 | 0.00063534 | 0.00015923
71 | 0.98711 | -0.091667 | 0 | 0
72 | 0.98673 | -0.094423 | 0.0010886 | 0.00027284
73 | 0.98781 | -0.086632 | 0 | 0
74 | 0.98486 | -0.10741 | 0.00073181 | 0.00018341
75 | 0.98489 | -0.10715 | 0.0031623 | 0.00079255
76 | 0.98511 | -0.10561 | 0 | 0
77 | 0.98614 | -0.098256 | 0 | 0
78 | 0.98469 | -0.10859 | 0.0010238 | 0.00025658
79 | 0.98604 | -0.098999 | 0.0013214 | 0.00033118
80 | 0.98648 | -0.096246 | 0.00073987 | 0.00018543
81 | 0.98672 | -0.094496 | 0.00095912 | 0.00024038
82 | 0.98642 | -0.096706 | 0.00012578 | 3.1522e-05
83 | 0.98641 | -0.096793 | 0.00022167 | 5.5556e-05
84 | 0.98639 | -0.096955 | 0 | 0
85 | 0.98709 | -0.091515 | 0 | 0
86 | 0.99225 | -0.054729 | 0.0015803 | 0.00039606
87 | 0.98467 | -0.10879 | 0.00080994 | 0.00020299
88 | 0.98635 | -0.097193 | 0.00015851 | 3.9726e-05
89 | 0.99322 | -0.047813 | 0.00058145 | 0.00014572
90 | 1 | 0 | -0.034378 | -0.0083685
91 | 0.99802 | -0.014189 | 0.00016577 | 4.1547e-05
92 | 0.99801 | -0.014247 | 0.00014942 | 3.7449e-05
93 | 0.99802 | -0.014164 | 0.00022889 | 5.7365e-05
94 | 0.99799 | -0.014349 | 0.00022414 | 5.6174e-05
95 | 0.99803 | -0.014111 | 0 | 0
96 | 0.98778 | -0.086814 | 0.00045917 | 0.00011508
97 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.011176 | 0.0027608 | -0.011172 | -0.0027595 | 4.3135e-06 | 1.3477e-06 | 0.016839 | 0.016839 | 0.016839 | 0.98679 | -0.095309 | 0.9864 | -0.098177 | 6.2365
1 | -0.011729 | -0.0028994 | 0.011733 | 0.0029008 | 4.2858e-06 | 1.3673e-06 | 0.017672 | 0.017672 | 0.017672 | 0.98679 | -0.095309 | 0.98716 | -0.092598 | 6.5452
2 | 0.0087063 | 0.0021462 | -0.0086818 | -0.0021396 | 2.4546e-05 | 6.533e-06 | 0.013121 | 0.013122 | 0.013122 | 0.9864 | -0.098177 | 0.98353 | -0.11924 | 4.8601
3 | 0.0024653 | 0.00061332 | -0.0024639 | -0.00061492 | 1.4667e-06 | -1.6052e-06 | 0.0037174 | 0.0037182 | 0.0037182 | 0.9864 | -0.098177 | 0.98579 | -0.10252 | 1.3771
4 | -0.012098 | -0.0029913 | 0.012169 | 0.0030144 | 7.1668e-05 | 2.3115e-05 | 0.018221 | 0.01822 | 0.018221 | 0.98716 | -0.092598 | 0.9932 | -0.048867 | 6.7487
5 | 0.00036469 | 9.0534e-05 | -0.00036468 | -9.1337e-05 | 1.1909e-08 | -8.033e-07 | 0.00054942 | 0.00054971 | 0.00054971 | 0.98716 | -0.092598 | 0.98713 | -0.092836 | 0.20359
6 | 0.0086818 | 0.0021396 | -0.0086785 | -0.0021388 | 3.2582e-06 | 8.6847e-07 | 0.013122 | 0.013122 | 0.013122 | 0.98353 | -0.11924 | 0.98315 | -0.12204 | 4.8601
7 | 0.0024639 | 0.00061492 | -0.002463 | -0.00061589 | 8.8643e-07 | -9.6842e-07 | 0.0037182 | 0.0037187 | 0.0037187 | 0.98579 | -0.10252 | 0.98543 | -0.10514 | 1.3773
8 | -0.012567 | -0.0031141 | 0.012568 | 0.0031144 | 9.0175e-07 | 2.94e-07 | 0.018816 | 0.018816 | 0.018816 | 0.9932 | -0.048867 | 0.99327 | -0.048338 | 6.9688
9 | 0.00014447 | 3.6147e-05 | -0.00014447 | -3.6207e-05 | 1.3971e-10 | -6.0305e-08 | 0.00021775 | 0.00021777 | 0.00021777 | 0.98713 | -0.092836 | 0.98713 | -0.092843 | 0.080657
10 | 0.0079836 | 0.0019646 | -0.0079773 | -0.0019631 | 6.3587e-06 | 1.5595e-06 | 0.012071 | 0.012071 | 0.012071 | 0.98315 | -0.12204 | 0.98234 | -0.12801 | 4.4707
11 | 0.0022623 | 0.00056558 | -0.0022622 | -0.00056566 | 5.7992e-08 | -7.918e-08 | 0.0034156 | 0.0034156 | 0.0034156 | 0.98543 | -0.10514 | 0.9854 | -0.10533 | 1.265
12 | -0.012787 | -0.0031693 | 0.012789 | 0.0031698 | 1.3458e-06 | 4.4145e-07 | 0.019144 | 0.019144 | 0.019144 | 0.99327 | -0.048338 | 0.99338 | -0.047561 | 7.0905
13 | -0.00022045 | -5.525e-05 | 0.00022045 | 5.4821e-05 | 2.3317e-09 | -4.2863e-07 | 0.00033294 | 0.00033278 | 0.00033294 | 0.98528 | -0.10622 | 0.98529 | -0.10615 | 0.12331
14 | -0.00022045 | -5.4821e-05 | 0.00022045 | 5.4556e-05 | 1.4429e-09 | -2.6545e-07 | 0.00033278 | 0.00033269 | 0.00033278 | 0.98529 | -0.10615 | 0.98529 | -0.1061 | 0.12325
15 | -0.00077018 | -0.00019233 | 0.00077019 | 0.00019218 | 1.0054e-08 | -1.4789e-07 | 0.0011629 | 0.0011628 | 0.0011629 | 0.98529 | -0.1061 | 0.98531 | -0.106 | 0.4307
16 | -0.0012864 | -0.00032156 | 0.0012864 | 0.00032149 | 1.3225e-08 | -6.646e-08 | 0.0019424 | 0.0019424 | 0.0019424 | 0.98531 | -0.106 | 0.98532 | -0.10593 | 0.71942
17 | 0.0077074 | 0.0018954 | -0.0077005 | -0.0018938 | 6.9397e-06 | 1.6349e-06 | 0.011662 | 0.011663 | 0.011663 | 0.98234 | -0.12801 | 0.98143 | -0.13476 | 4.3195
18 | 0.0077005 | 0.0018938 | -0.0076865 | -0.0018905 | 1.4032e-05 | 3.3119e-06 | 0.011663 | 0.011663 | 0.011663 | 0.98143 | -0.13476 | 0.97958 | -0.14842 | 4.3197
19 | 0.0075204 | 0.0018489 | -0.0075157 | -0.0018478 | 4.689e-06 | 1.0775e-06 | 0.011411 | 0.011411 | 0.011411 | 0.97958 | -0.14842 | 0.97895 | -0.1531 | 4.2264
20 | 0.002099 | 0.00051612 | -0.0020985 | -0.00051694 | 4.7714e-07 | -8.161e-07 | 0.0031435 | 0.0031439 | 0.0031439 | 0.99248 | -0.054182 | 0.99225 | -0.055883 | 1.1644
21 | -0.0022181 | -0.00054599 | 0.0022201 | 0.00054307 | 1.9529e-06 | -2.918e-06 | 0.0033222 | 0.0033209 | 0.0033222 | 0.99248 | -0.054182 | 0.99338 | -0.047561 | 1.2304
22 | 0.0019295 | 0.00047458 | -0.0019294 | -0.00047473 | 7.4297e-08 | -1.555e-07 | 0.0028904 | 0.0028905 | 0.0028905 | 0.99225 | -0.055883 | 0.99221 | -0.056172 | 1.0705
23 | -0.015137 | -0.0037449 | 0.015163 | 0.003754 | 2.6595e-05 | 9.1519e-06 | 0.022657 | 0.022656 | 0.022657 | 0.99338 | -0.047561 | 0.99518 | -0.034565 | 8.3913
24 | 0.0017039 | 0.00041822 | -0.0017038 | -0.00041852 | 1.0968e-07 | -3.0627e-07 | 0.0025523 | 0.0025524 | 0.0025524 | 0.99221 | -0.056172 | 0.99214 | -0.056656 | 0.94533
25 | 0.00087789 | 0.00021153 | -0.00087754 | -0.00021562 | 3.5317e-07 | -4.0927e-06 | 0.0013137 | 0.0013152 | 0.0013152 | 0.99214 | -0.056656 | 0.99173 | -0.059731 | 0.4871
26 | 0.00087754 | 0.00021562 | -0.00087734 | -0.00021791 | 1.981e-07 | -2.29e-06 | 0.0013152 | 0.001316 | 0.001316 | 0.99173 | -0.059731 | 0.9915 | -0.061408 | 0.48741
27 | 0.00048678 | 0.00012003 | -0.00048678 | -0.00012003 | 1.1784e-10 | -4.5247e-09 | 0.00072985 | 0.00072985 | 0.00072985 | 0.9915 | -0.061408 | 0.9915 | -0.06141 | 0.27032
28 | -0.015329 | -0.0037955 | 0.015371 | 0.0038102 | 4.2492e-05 | 1.4652e-05 | 0.022904 | 0.022903 | 0.022904 | 0.99518 | -0.034565 | 0.99803 | -0.014111 | 8.4829
29 | 0.00021472 | 5.1849e-05 | -0.00021471 | -5.3811e-05 | 9.8571e-09 | -1.9622e-06 | 0.00032156 | 0.00032225 | 0.00032225 | 0.9915 | -0.06141 | 0.99145 | -0.061753 | 0.11935
30 | -0.0016924 | -0.00042325 | 0.0016924 | 0.00042325 | 5.7384e-12 | 2.2071e-12 | 0.0025556 | 0.0025556 | 0.0025556 | 0.98532 | -0.10593 | 0.98532 | -0.10593 | 0.94652
31 | -0.0018337 | -0.00045864 | 0.0018338 | 0.0004583 | 1.5166e-07 | -3.4551e-07 | 0.0027688 | 0.0027687 | 0.0027688 | 0.98532 | -0.10593 | 0.9854 | -0.10533 | 1.0255
32 | 0.00026004 | 6.0626e-05 | -0.00026002 | -6.204e-05 | 1.1118e-08 | -1.4134e-06 | 0.00039547 | 0.00039595 | 0.00039595 | 0.97453 | -0.18594 | 0.97449 | -0.18628 | 0.14665
33 | -0.0015207 | -0.00037657 | 0.0015207 | 0.00037641 | 4.8565e-08 | -1.6145e-07 | 0.0023203 | 0.0023202 | 0.0023203 | 0.97453 | -0.18594 | 0.97456 | -0.1857 | 0.85936
34 | 0.00015359 | 3.5364e-05 | -0.00015358 | -3.849e-05 | 8.5813e-09 | -3.1263e-06 | 0.00023344 | 0.00023452 | 0.00023452 | 0.97449 | -0.18628 | 0.97443 | -0.18672 | 0.08686
35 | 0.0013646 | 0.00033526 | -0.0013637 | -0.00033873 | 8.2098e-07 | -3.4647e-06 | 0.0020811 | 0.0020824 | 0.0020824 | 0.97456 | -0.1857 | 0.97396 | -0.19017 | 0.77127
36 | -0.0028853 | -0.00071167 | 0.0028853 | 0.00071166 | 1.9328e-08 | -1.249e-08 | 0.0044013 | 0.0044013 | 0.0044013 | 0.97456 | -0.1857 | 0.97457 | -0.18565 | 1.6301
37 | 0.0002759 | 6.6402e-05 | -0.00027588 | -6.9141e-05 | 2.4433e-08 | -2.7392e-06 | 0.00042055 | 0.00042152 | 0.00042152 | 0.97396 | -0.19017 | 0.97387 | -0.19084 | 0.15612
38 | 0.0010878 | 0.00027232 | -0.0010878 | -0.00027251 | 2.6626e-08 | -1.8202e-07 | 0.0016619 | 0.001662 | 0.001662 | 0.97396 | -0.19017 | 0.97393 | -0.19035 | 0.61554
39 | -0.0029977 | -0.00073984 | 0.0029981 | 0.00073964 | 3.4619e-07 | -1.9747e-07 | 0.004573 | 0.0045729 | 0.004573 | 0.97457 | -0.18565 | 0.97469 | -0.18479 | 1.6937
40 | 0.00081201 | 0.00020338 | -0.000812 | -0.0002035 | 9.6112e-09 | -1.2084e-07 | 0.0012406 | 0.0012406 | 0.0012406 | 0.97393 | -0.19035 | 0.97392 | -0.19044 | 0.45949
41 | -0.007484 | -0.0018405 | 0.0075053 | 0.0018454 | 2.1295e-05 | 4.9151e-06 | 0.011413 | 0.011412 | 0.011413 | 0.97469 | -0.18479 | 0.97755 | -0.1635 | 4.227
42 | 0.0044859 | 0.0011008 | -0.0044856 | -0.0011008 | 2.9187e-07 | -1.2333e-08 | 0.0068401 | 0.0068402 | 0.0068402 | 0.97469 | -0.18479 | 0.97462 | -0.18528 | 2.5334
43 | 0.00023816 | 5.7913e-05 | -0.00023815 | -5.9686e-05 | 1.1762e-08 | -1.7725e-06 | 0.00036312 | 0.00036375 | 0.00036375 | 0.97427 | -0.18795 | 0.97422 | -0.18832 | 0.13472
44 | -0.00043673 | -0.00010768 | 0.00043673 | 0.00010763 | 1.2248e-09 | -5.4573e-08 | 0.00066639 | 0.00066637 | 0.00066639 | 0.97427 | -0.18795 | 0.97427 | -0.18793 | 0.24681
45 | -0.00043673 | -0.00010763 | 0.00043681 | 0.00010395 | 8.2367e-08 | -3.678e-06 | 0.00066637 | 0.00066508 | 0.00066637 | 0.97427 | -0.18793 | 0.97446 | -0.18648 | 0.2468
46 | 0.0036921 | 0.00090773 | -0.0036851 | -0.00090942 | 6.9436e-06 | -1.6907e-06 | 0.0056316 | 0.0056331 | 0.0056331 | 0.97446 | -0.18648 | 0.97257 | -0.20054 | 2.0863
47 | -0.0041289 | -0.0010117 | 0.0041295 | 0.0010116 | 6.5376e-07 | -7.7812e-08 | 0.0062966 | 0.0062965 | 0.0062966 | 0.97446 | -0.18648 | 0.97462 | -0.18528 | 2.3321
48 | 0.00039505 | 9.4361e-05 | -0.00039498 | -9.8257e-05 | 7.1865e-08 | -3.8961e-06 | 0.00060278 | 0.00060416 | 0.00060416 | 0.97257 | -0.20054 | 0.97239 | -0.20193 | 0.22376
49 | 0.0032901 | 0.00081506 | -0.0032898 | -0.00081518 | 2.9353e-07 | -1.1776e-07 | 0.0050304 | 0.0050304 | 0.0050304 | 0.97257 | -0.20054 | 0.97248 | -0.2012 | 1.8631
50 | -0.0075053 | -0.0018454 | 0.0075157 | 0.0018478 | 1.0419e-05 | 2.3975e-06 | 0.011412 | 0.011411 | 0.011412 | 0.97755 | -0.1635 | 0.97895 | -0.1531 | 4.2266
51 | 0.00039498 | 9.8257e-05 | -0.00039497 | -9.8796e-05 | 9.9641e-09 | -5.3865e-07 | 0.00060416 | 0.00060435 | 0.00060435 | 0.97239 | -0.20193 | 0.97236 | -0.20211 | 0.22383
52 | 0.0029713 | 0.00073537 | -0.0029677 | -0.00073745 | 3.5975e-06 | -2.0766e-06 | 0.0045432 | 0.0045444 | 0.0045444 | 0.97248 | -0.2012 | 0.97127 | -0.21013 | 1.6831
53 | 0.00041462 | 0.00010391 | -0.00041462 | -0.00010391 | 5.3825e-11 | -2.6561e-09 | 0.00063348 | 0.00063348 | 0.00063348 | 0.97392 | -0.19044 | 0.97392 | -0.19044 | 0.23462
54 | -0.00013172 | -3.3012e-05 | 0.00013172 | 3.282e-05 | 3.9253e-10 | -1.9195e-07 | 0.00020157 | 0.00020151 | 0.00020157 | 0.97236 | -0.20213 | 0.97236 | -0.20211 | 0.074657
55 | 0.00052565 | 0.00013124 | -0.00052564 | -0.00013174 | 1.6473e-08 | -4.9754e-07 | 0.00080514 | 0.00080532 | 0.00080532 | 0.97127 | -0.21013 | 0.97123 | -0.21036 | 0.29827
56 | 0.00044405 | 0.00010866 | -0.00044403 | -0.00010925 | 1.3824e-08 | -5.8857e-07 | 0.00067936 | 0.00067957 | 0.00067957 | 0.97127 | -0.21013 | 0.97123 | -0.21037 | 0.25169
57 | 0.001998 | 0.00049755 | -0.0019977 | -0.00049818 | 3.5907e-07 | -6.2229e-07 | 0.0030599 | 0.0030602 | 0.0030602 | 0.97127 | -0.21013 | 0.97108 | -0.21145 | 1.1334
58 | 0.00029434 | 7.1729e-05 | -0.00029432 | -7.3763e-05 | 2.0911e-08 | -2.0344e-06 | 0.00045023 | 0.00045096 | 0.00045096 | 0.97123 | -0.21037 | 0.97116 | -0.21089 | 0.16702
59 | 0.0016689 | 0.00041577 | -0.0016689 | -0.00041578 | 2.9888e-09 | -7.9181e-09 | 0.0025564 | 0.0025564 | 0.0025564 | 0.97108 | -0.21145 | 0.97108 | -0.21146 | 0.94681
60 | 0.0014001 | 0.00034841 | -0.0014 | -0.00034879 | 9.5533e-08 | -3.7505e-07 | 0.0021445 | 0.0021446 | 0.0021446 | 0.97108 | -0.21146 | 0.97101 | -0.21196 | 0.79431
61 | 0.0011981 | 0.00029954 | -0.0011981 | -0.00029972 | 3.2574e-08 | -1.7888e-07 | 0.0018362 | 0.0018363 | 0.0018363 | 0.97078 | -0.21363 | 0.97076 | -0.21383 | 0.68011
62 | -0.0013997 | -0.00035005 | 0.0014 | 0.00034879 | 3.2231e-07 | -1.2645e-06 | 0.0021451 | 0.0021446 | 0.0021451 | 0.97078 | -0.21363 | 0.97101 | -0.21196 | 0.7945
63 | 0.00076111 | 0.0001902 | -0.00076108 | -0.00019074 | 3.8267e-08 | -5.4238e-07 | 0.0011665 | 0.0011667 | 0.0011667 | 0.97076 | -0.21383 | 0.97071 | -0.2142 | 0.4321
64 | -0.0053294 | -0.0013239 | 0.0053302 | 0.0013239 | 8.1134e-07 | 5.1851e-08 | 0.0080113 | 0.0080112 | 0.0080113 | 0.98937 | -0.075349 | 0.98952 | -0.07423 | 2.9671
65 | 0.0046766 | 0.0011603 | -0.0046765 | -0.0011603 | 1.233e-07 | -3.9281e-09 | 0.0070294 | 0.0070295 | 0.0070295 | 0.98937 | -0.075349 | 0.98934 | -0.075544 | 2.6035
66 | -0.0066317 | -0.0016501 | 0.0066408 | 0.0016517 | 9.0796e-06 | 1.6083e-06 | 0.0099683 | 0.0099677 | 0.0099683 | 0.98952 | -0.07423 | 0.99092 | -0.064202 | 3.692
67 | 0.0037622 | 0.00093114 | -0.0037584 | -0.00093213 | 3.8534e-06 | -9.9508e-07 | 0.0056544 | 0.0056553 | 0.0056553 | 0.98934 | -0.075544 | 0.9883 | -0.083114 | 2.0946
68 | -0.014366 | -0.0035819 | 0.014372 | 0.003584 | 6.1276e-06 | 2.0847e-06 | 0.021567 | 0.021567 | 0.021567 | 0.99092 | -0.064202 | 0.99136 | -0.06109 | 7.9876
69 | 0.0077255 | 0.0019302 | -0.0077222 | -0.0019295 | 3.3106e-06 | 7.6554e-07 | 0.011599 | 0.011599 | 0.011599 | 0.99092 | -0.064202 | 0.99048 | -0.067317 | 4.296
70 | 0.0037584 | 0.00093213 | -0.0037566 | -0.00093259 | 1.7943e-06 | -4.6131e-07 | 0.0056553 | 0.0056557 | 0.0056557 | 0.9883 | -0.083114 | 0.98781 | -0.086632 | 2.0947
71 | -0.015102 | -0.0037669 | 0.015115 | 0.0037715 | 1.3185e-05 | 4.5403e-06 | 0.022662 | 0.022662 | 0.022662 | 0.99136 | -0.06109 | 0.99225 | -0.054729 | 8.3933
72 | 0.0070869 | 0.0017702 | -0.0070633 | -0.0017654 | 2.356e-05 | 4.7881e-06 | 0.010645 | 0.010646 | 0.010646 | 0.99048 | -0.067317 | 0.98709 | -0.091515 | 3.943
73 | 0.0032952 | 0.00081901 | -0.0032939 | -0.00081957 | 1.2381e-06 | -5.5231e-07 | 0.0049649 | 0.0049652 | 0.0049652 | 0.98711 | -0.091667 | 0.98673 | -0.094423 | 1.839
74 | -0.0032952 | -0.00081901 | 0.0032974 | 0.000818 | 2.2561e-06 | -1.0088e-06 | 0.0049649 | 0.0049642 | 0.0049649 | 0.98711 | -0.091667 | 0.98781 | -0.086632 | 1.8388
75 | 0.0022053 | 0.00054673 | -0.0022053 | -0.00054676 | 2.1822e-08 | -3.2047e-08 | 0.0033235 | 0.0033236 | 0.0033236 | 0.98673 | -0.094423 | 0.98672 | -0.094496 | 1.2309
76 | 0.00045918 | 0.00011459 | -0.00045917 | -0.00011508 | 1.1536e-08 | -4.9031e-07 | 0.00069152 | 0.0006917 | 0.0006917 | 0.98781 | -0.086632 | 0.98778 | -0.086814 | 0.25618
77 | -0.00073181 | -0.00018341 | 0.00073184 | 0.00018298 | 2.6152e-08 | -4.2624e-07 | 0.0011057 | 0.0011055 | 0.0011057 | 0.98486 | -0.10741 | 0.98489 | -0.10715 | 0.40951
78 | -0.0038941 | -0.00097553 | 0.003895 | 0.00097536 | 8.2947e-07 | -1.6983e-07 | 0.0058833 | 0.0058831 | 0.0058833 | 0.98489 | -0.10715 | 0.98511 | -0.10561 | 2.179
79 | -0.0057294 | -0.0014329 | 0.0057352 | 0.0014336 | 5.8117e-06 | 6.4993e-07 | 0.0086533 | 0.0086527 | 0.0086533 | 0.98511 | -0.10561 | 0.98614 | -0.098256 | 3.2049
80 | 0.0018345 | 0.00045756 | -0.0018337 | -0.00045927 | 7.5077e-07 | -1.706e-06 | 0.0027702 | 0.0027709 | 0.0027709 | 0.98511 | -0.10561 | 0.98469 | -0.10859 | 1.0263
81 | 0.0013216 | 0.00033053 | -0.0013214 | -0.00033118 | 1.3572e-07 | -6.4565e-07 | 0.0019939 | 0.0019941 | 0.0019941 | 0.98614 | -0.098256 | 0.98604 | -0.098999 | 0.73857
82 | -0.0070568 | -0.0017641 | 0.0070633 | 0.0017654 | 6.5535e-06 | 1.3373e-06 | 0.010647 | 0.010646 | 0.010647 | 0.98614 | -0.098256 | 0.98709 | -0.091515 | 3.9432
83 | 0.00080996 | 0.00020269 | -0.00080994 | -0.00020299 | 2.2554e-08 | -2.9826e-07 | 0.0012239 | 0.001224 | 0.001224 | 0.98469 | -0.10859 | 0.98467 | -0.10879 | 0.45332
84 | -0.0012459 | -0.00030797 | 0.0012462 | 0.00030638 | 2.9231e-07 | -1.5846e-06 | 0.0018778 | 0.0018772 | 0.0018778 | 0.98648 | -0.096246 | 0.98672 | -0.094496 | 0.69547
85 | 0.000506 | 0.00012254 | -0.00050597 | -0.0001236 | 3.0406e-08 | -1.0598e-06 | 0.00076176 | 0.00076213 | 0.00076213 | 0.98648 | -0.096246 | 0.98642 | -0.096706 | 0.28227
86 | 0.00038019 | 9.2078e-05 | -0.00038019 | -9.2346e-05 | 4.3139e-09 | -2.6765e-07 | 0.0005724 | 0.00057249 | 0.00057249 | 0.98642 | -0.096706 | 0.98641 | -0.096793 | 0.21203
87 | 0.00015852 | 3.6789e-05 | -0.00015851 | -3.7931e-05 | 3.1728e-09 | -1.1417e-06 | 0.00023812 | 0.0002385 | 0.0002385 | 0.98641 | -0.096793 | 0.98639 | -0.096955 | 0.088333
88 | 0.00015851 | 3.7931e-05 | -0.00015851 | -3.9726e-05 | 5.0097e-09 | -1.7949e-06 | 0.0002385 | 0.00023913 | 0.00023913 | 0.98639 | -0.096955 | 0.98635 | -0.097193 | 0.088565
89 | -0.016696 | -0.0041675 | 0.016712 | 0.0041731 | 1.5872e-05 | 5.5798e-06 | 0.025032 | 0.025032 | 0.025032 | 0.99225 | -0.054729 | 0.99322 | -0.047813 | 9.271
90 | -0.017293 | -0.0043188 | 0.017407 | 0.0043593 | 0.00011435 | 4.0423e-05 | 0.025903 | 0.025901 | 0.025903 | 0.99322 | -0.047813 | 1 | 0 | 9.5936
91 | 0.01617 | 0.0040092 | -0.01614 | -0.0040018 | 3.0901e-05 | 7.3999e-06 | 0.024047 | 0.024048 | 0.024048 | 1 | 0 | 0.99803 | -0.014111 | 4.4534
92 | 0.00037356 | 9.2834e-05 | -0.00037356 | -9.3031e-05 | 2.9358e-09 | -1.9722e-07 | 0.0005567 | 0.00055677 | 0.00055677 | 0.99802 | -0.014189 | 0.99801 | -0.014247 | 0.20621
93 | -0.00053934 | -0.00013438 | 0.00053934 | 0.00013432 | 1.8175e-09 | -5.8201e-08 | 0.00080386 | 0.00080384 | 0.00080386 | 0.99802 | -0.014189 | 0.99802 | -0.014164 | 0.29773
94 | 0.00022414 | 5.5583e-05 | -0.00022414 | -5.6174e-05 | 3.1558e-09 | -5.9088e-07 | 0.00033398 | 0.00033419 | 0.00033419 | 0.99801 | -0.014247 | 0.99799 | -0.014349 | 0.12377
95 | -0.00076823 | -0.00019169 | 0.00076823 | 0.0001916 | 5.6136e-09 | -8.7495e-08 | 0.0011451 | 0.0011451 | 0.0011451 | 0.99802 | -0.014164 | 0.99803 | -0.014111 | 0.42411

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.034599 | 0.0084239

## res_load
| p_mw | q_mvar
0 | 0.00055285 | 0.00013856
1 | 0.00039767 | 9.9666e-05
2 | 0.00022021 | 5.5191e-05
3 | 0.00069493 | 0.00017417
4 | 0.00020074 | 5.031e-05
5 | 0.0002193 | 5.4962e-05
6 | 0.00014447 | 3.6207e-05
7 | 0.00022045 | 5.525e-05
8 | 0.00054973 | 0.00013777
9 | 0.00051621 | 0.00012937
10 | 0.00026981 | 6.7621e-05
11 | 0.00016606 | 4.1618e-05
12 | 0.00011917 | 2.9867e-05
13 | 0.000169 | 4.2357e-05
14 | 0.00012783 | 3.2037e-05
15 | 0.00022552 | 5.652e-05
16 | 0.00082591 | 0.00020699
17 | 0.00039056 | 9.7884e-05
18 | 0.0001656 | 4.1504e-05
19 | 0.00027206 | 6.8184e-05
20 | 0.00021471 | 5.3811e-05
21 | 0.00040603 | 0.00010176
22 | 0.00014121 | 3.539e-05
23 | 0.00042839 | 0.00010737
24 | 0.0012606 | 0.00031594
25 | 0.00010644 | 2.6676e-05
26 | 0.00015358 | 3.849e-05
27 | 0.00011246 | 2.8185e-05
28 | 0.00027588 | 6.9141e-05
29 | 0.00027581 | 6.9124e-05
30 | 0.00019857 | 4.9766e-05
31 | 0.00023815 | 5.9686e-05
32 | 0.00035608 | 8.9243e-05
33 | 0.00031843 | 7.9807e-05
34 | 0.00039738 | 9.9592e-05
35 | 0.00041462 | 0.00010391
36 | 0.00013172 | 3.3012e-05
37 | 0.00026325 | 6.5976e-05
38 | 0.00052564 | 0.00013174
39 | 0.00014969 | 3.7517e-05
40 | 0.00032879 | 8.2403e-05
41 | 0.00029432 | 7.3763e-05
42 | 0.00026881 | 6.7369e-05
43 | 0.00020154 | 5.051e-05
44 | 0.00043698 | 0.00010952
45 | 0.00076108 | 0.00019074
46 | 0.00065282 | 0.00016361
47 | 0.0013015 | 0.00032618
48 | 0.00091421 | 0.00022912
49 | 0.00072983 | 0.00018291
50 | 0.00063534 | 0.00015923
51 | 0.0010886 | 0.00027284
52 | 0.00073181 | 0.00018341
53 | 0.0031623 | 0.00079255
54 | 0.0010238 | 0.00025658
55 | 0.0013214 | 0.00033118
56 | 0.00073987 | 0.00018543
57 | 0.00095912 | 0.00024038
58 | 0.00012578 | 3.1522e-05
59 | 0.00022167 | 5.5556e-05
60 | 0.0015803 | 0.00039606
61 | 0.00080994 | 0.00020299
62 | 0.00015851 | 3.9726e-05
63 | 0.00058145 | 0.00014572
64 | 0.0002211 | 5.5413e-05
65 | 0.00016577 | 4.1547e-05
66 | 0.00014942 | 3.7449e-05
67 | 0.00022889 | 5.7365e-05
68 | 0.00022414 | 5.6174e-05
69 | 0.00045917 | 0.00011508

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1