## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1311-3_1_5_node_52 | 0.4 | n |  | TRUE
1 | bus_LV_1311-3_1_5_node_53 | 0.4 | n |  | TRUE
2 | bus_LV_1311-3_1_5_node_116 | 0.4 | n |  | TRUE
3 | bus_LV_1311-3_1_5_node_195 | 0.4 | n |  | TRUE
4 | bus_LV_1311-3_1_5_node_54 | 0.4 | n |  | TRUE
5 | bus_LV_1311-3_1_5_node_211 | 0.4 | n |  | TRUE
6 | bus_LV_1311-3_1_5_node_210 | 0.4 | n |  | TRUE
7 | bus_LV_1311-3_1_5_node_97 | 0.4 | n |  | TRUE
8 | bus_LV_1311-3_1_5_node_98 | 0.4 | n |  | TRUE
9 | bus_LV_1311-3_1_5_node_194 | 0.4 | n |  | TRUE
10 | bus_LV_1311-3_1_5_node_209 | 0.4 | n |  | TRUE
11 | bus_LV_1311-3_1_5_node_208 | 0.4 | n |  | TRUE
12 | bus_LV_1311-3_1_5_node_109 | 0.4 | n |  | TRUE
13 | bus_LV_1311-3_1_5_node_110 | 0.4 | n |  | TRUE
14 | bus_LV_1311-3_1_5_node_173 | 0.4 | n |  | TRUE
15 | bus_LV_1311-3_1_5_node_141 | 0.4 | n |  | TRUE
16 | bus_LV_1311-3_1_5_node_58 | 0.4 | n |  | TRUE
17 | bus_LV_1311-3_1_5_node_59 | 0.4 | n |  | TRUE
18 | bus_LV_1311-3_1_5_node_61 | 0.4 | n |  | TRUE
19 | bus_LV_1311-3_1_5_node_66 | 0.4 | n |  | TRUE
20 | bus_LV_1311-3_1_5_node_62 | 0.4 | n |  | TRUE
21 | bus_LV_1311-3_1_5_node_70 | 0.4 | n |  | TRUE
22 | bus_LV_1311-3_1_5_node_67 | 0.4 | n |  | TRUE
23 | bus_LV_1311-3_1_5_node_86 | 0.4 | n |  | TRUE
24 | bus_LV_1311-3_1_5_node_85 | 0.4 | n |  | TRUE
25 | bus_LV_1311-3_1_5_node_83 | 0.4 | n |  | TRUE
26 | bus_LV_1311-3_1_5_node_68 | 0.4 | n |  | TRUE
27 | bus_LV_1311-3_1_5_node_63 | 0.4 | n |  | TRUE
28 | bus_LV_1311-3_1_5_node_64 | 0.4 | n |  | TRUE
29 | bus_LV_1311-3_1_5_node_65 | 0.4 | n |  | TRUE
30 | bus_LV_1311-3_1_5_node_81 | 0.4 | n |  | TRUE
31 | bus_LV_1311-3_1_5_node_82 | 0.4 | n |  | TRUE
32 | bus_LV_1311-3_1_5_node_205 | 0.4 | n |  | TRUE
33 | bus_LV_1311-3_1_5_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_1311-3_1_5_node_88 | 0.4 | n |  | TRUE
35 | bus_LV_1311-3_1_5_node_204 | 0.4 | n |  | TRUE
36 | bus_LV_1311-3_1_5_node_196 | 0.4 | n |  | TRUE
37 | bus_LV_1311-3_1_5_node_197 | 0.4 | n |  | TRUE
38 | bus_LV_1311-3_1_5_node_182 | 0.4 | n |  | TRUE
39 | bus_LV_1311-3_1_5_node_202 | 0.4 | n |  | TRUE
40 | bus_LV_1311-3_1_5_node_94 | 0.4 | n |  | TRUE
41 | bus_LV_1311-3_1_5_node_96 | 0.4 | n |  | TRUE
42 | bus_LV_1311-3_1_5_node_129 | 0.4 | n |  | TRUE
43 | bus_LV_1311-3_1_5_node_130 | 0.4 | n |  | TRUE
44 | bus_LV_1311-3_1_5_node_131 | 0.4 | n |  | TRUE
45 | bus_LV_1311-3_1_5_node_132 | 0.4 | n |  | TRUE
46 | bus_LV_1311-3_1_5_node_135 | 0.4 | n |  | TRUE
47 | bus_LV_1311-3_1_5_node_136 | 0.4 | n |  | TRUE
48 | bus_LV_1311-3_1_5_node_184 | 0.4 | n |  | TRUE
49 | bus_LV_1311-3_1_5_node_176 | 0.4 | n |  | TRUE
50 | bus_LV_1311-3_1_5_node_133 | 0.4 | n |  | TRUE
51 | bus_LV_1311-3_1_5_node_134 | 0.4 | n |  | TRUE
52 | bus_LV_1311-3_1_5_node_193 | 0.4 | n |  | TRUE
53 | bus_LV_1311-3_1_5_node_144 | 0.4 | n |  | TRUE
54 | bus_LV_1311-3_1_5_node_171 | 0.4 | n |  | TRUE
55 | bus_LV_1311-3_1_5_node_168 | 0.4 | n |  | TRUE
56 | bus_LV_1311-3_1_5_node_137 | 0.4 | n |  | TRUE
57 | bus_LV_1311-3_1_5_node_138 | 0.4 | n |  | TRUE
58 | bus_LV_1311-3_1_5_node_139 | 0.4 | n |  | TRUE
59 | bus_LV_1311-3_1_5_node_140 | 0.4 | n |  | TRUE
60 | bus_LV_1311-3_1_5_node_142 | 0.4 | n |  | TRUE
61 | bus_LV_1311-3_1_5_node_143 | 0.4 | n |  | TRUE
62 | bus_LV_1311-3_1_5_node_148 | 0.4 | n |  | TRUE
63 | bus_LV_1311-3_1_5_node_206 | 0.4 | n |  | TRUE
64 | bus_LV_1311-3_1_5_node_145 | 0.4 | n |  | TRUE
65 | bus_LV_1311-3_1_5_node_146 | 0.4 | n |  | TRUE
66 | bus_LV_1311-3_1_5_node_147 | 0.4 | n |  | TRUE
67 | bus_LV_1311-3_1_5_node_149 | 0.4 | n |  | TRUE
68 | bus_LV_1311-3_1_5_node_150 | 0.4 | n |  | TRUE
69 | bus_LV_1311-3_1_5_node_151 | 0.4 | n |  | TRUE
70 | bus_LV_1311-3_1_5_node_152 | 0.4 | n |  | TRUE
71 | bus_LV_1311-3_1_5_node_178 | 0.4 | n |  | TRUE
72 | bus_LV_1311-3_1_5_node_156 | 0.4 | n |  | TRUE
73 | bus_LV_1311-3_1_5_node_153 | 0.4 | n |  | TRUE
74 | bus_LV_1311-3_1_5_node_154 | 0.4 | n |  | TRUE
75 | bus_LV_1311-3_1_5_node_155 | 0.4 | n |  | TRUE
76 | bus_LV_1311-3_1_5_node_157 | 0.4 | n |  | TRUE
77 | bus_LV_1311-3_1_5_node_158 | 0.4 | n |  | TRUE
78 | bus_LV_1311-3_1_5_node_159 | 0.4 | n |  | TRUE
79 | bus_LV_1311-3_1_5_node_160 | 0.4 | n |  | TRUE
80 | bus_LV_1311-3_1_5_node_161 | 0.4 | n |  | TRUE
81 | bus_LV_1311-3_1_5_node_172 | 0.4 | n |  | TRUE
82 | bus_LV_1311-3_1_5_node_162 | 0.4 | n |  | TRUE
83 | bus_LV_1311-3_1_5_node_163 | 0.4 | n |  | TRUE
84 | bus_LV_1311-3_1_5_node_164 | 0.4 | n |  | TRUE
85 | bus_LV_1311-3_1_5_node_165 | 0.4 | n |  | TRUE
86 | bus_LV_1311-3_1_5_node_166 | 0.4 | n |  | TRUE
87 | bus_LV_1311-3_1_5_node_167 | 0.4 | n |  | TRUE
88 | bus_LV_1311-3_1_5_node_174 | 0.4 | n |  | TRUE
89 | bus_LV_1311-3_1_5_node_177 | 0.4 | n |  | TRUE
90 | bus_LV_1311-3_1_5_node_183 | 0.4 | n |  | TRUE
91 | bus_LV_1311-3_1_5_node_180 | 0.4 | n |  | TRUE
92 | bus_LV_1311-3_1_5_node_185 | 0.4 | n |  | TRUE
93 | bus_LV_1311-3_1_5_node_186 | 0.4 | n |  | TRUE
94 | bus_LV_1311-3_1_5_node_175 | 0.4 | n |  | TRUE
95 | bus_LV_1311-3_1_5_node_179 | 0.4 | n |  | TRUE
96 | bus_LV_1311-3_1_5_node_181 | 0.4 | n |  | TRUE
97 | bus_LV_1311-3_1_5_node_192 | 0.4 | n |  | TRUE
98 | bus_LV_1311-3_1_5_node_187 | 0.4 | n |  | TRUE
99 | bus_LV_1311-3_1_5_node_188 | 0.4 | n |  | TRUE
100 | bus_LV_1311-3_1_5_node_189 | 0.4 | n |  | TRUE
101 | bus_LV_1311-3_1_5_node_190 | 0.4 | n |  | TRUE
102 | bus_LV_1311-3_1_5_node_191 | 0.4 | n |  | TRUE
103 | bus_LV_1311-3_1_5_node_207 | 0.4 | n |  | TRUE
104 | bus_LV_1311-3_1_5_node_201 | 0.4 | n |  | TRUE
105 | bus_LV_1311-3_1_5_node_203 | 0.4 | n |  | TRUE
106 | bus_MV_127_0_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1311-3_1_5_load_211 | 5 | 0.00060303 | 0.00015113 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1311-3_1_5_load_210 | 6 | 0.0023509 | 0.00058918 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1311-3_1_5_load_97 | 7 | 0.003077 | 0.00077117 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1311-3_1_5_load_194 | 9 | 0.00023875 | 5.9835e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1311-3_1_5_load_209 | 10 | 0.000457 | 0.00011454 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1311-3_1_5_load_208 | 11 | 0.0026113 | 0.00065445 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1311-3_1_5_load_109 | 12 | 0.0012911 | 0.00032359 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1311-3_1_5_load_110 | 13 | 0.00074872 | 0.00018765 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1311-3_1_5_load_173 | 14 | 0.0015775 | 0.00039536 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1311-3_1_5_load_141 | 15 | 0.0024388 | 0.00061122 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1311-3_1_5_load_58 | 16 | 0.00025417 | 6.37e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1311-3_1_5_load_59 | 17 | 0.00046227 | 0.00011586 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1311-3_1_5_load_61 | 18 | 0.0004945 | 0.00012393 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1311-3_1_5_load_70 | 21 | 0.00026826 | 6.7233e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1311-3_1_5_load_67 | 22 | 0.00021551 | 5.4011e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1311-3_1_5_load_86 | 23 | 0.00019727 | 4.9439e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1311-3_1_5_load_85 | 24 | 0.00030141 | 7.5541e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1311-3_1_5_load_68 | 26 | 0.00030205 | 7.5701e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1311-3_1_5_load_63 | 27 | 0.00034978 | 8.7662e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1311-3_1_5_load_64 | 28 | 0.00024331 | 6.098e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1311-3_1_5_load_65 | 29 | 0.0001953 | 4.8948e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1311-3_1_5_load_81 | 30 | 0.00070682 | 0.00017715 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1311-3_1_5_load_82 | 31 | 0.00015447 | 3.8715e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1311-3_1_5_load_88 | 34 | 0.00028341 | 7.103e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1311-3_1_5_load_196 | 36 | 0.0001993 | 4.995e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1311-3_1_5_load_182 | 38 | 0.00054553 | 0.00013672 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1311-3_1_5_load_202 | 39 | 0.00019664 | 4.9282e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1311-3_1_5_load_94 | 40 | 0.0021877 | 0.00054829 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1311-3_1_5_load_129 | 42 | 0.00092493 | 0.00023181 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1311-3_1_5_load_135 | 46 | 0.00094679 | 0.00023729 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1311-3_1_5_load_184 | 48 | 0.0012588 | 0.00031548 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1311-3_1_5_load_176 | 49 | 0.0027694 | 0.00069408 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1311-3_1_5_load_193 | 52 | 0.0070768 | 0.0017736 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1311-3_1_5_load_144 | 53 | 0.0016919 | 0.00042403 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1311-3_1_5_load_168 | 55 | 0.0013413 | 0.00033616 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1311-3_1_5_load_137 | 56 | 0.0021217 | 0.00053176 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1311-3_1_5_load_140 | 59 | 0.00074467 | 0.00018663 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1311-3_1_5_load_142 | 60 | 0.0030136 | 0.00075527 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1311-3_1_5_load_143 | 61 | 0.0015882 | 0.00039803 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1311-3_1_5_load_148 | 62 | 0.0018101 | 0.00045366 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1311-3_1_5_load_206 | 63 | 0.0029066 | 0.00072846 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1311-3_1_5_load_146 | 65 | 0.00061837 | 0.00015498 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1311-3_1_5_load_147 | 66 | 0.00086356 | 0.00021643 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1311-3_1_5_load_150 | 68 | 0.004355 | 0.0010915 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1311-3_1_5_load_151 | 69 | 0.014381 | 0.0036042 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1311-3_1_5_load_152 | 70 | 0.00083876 | 0.00021021 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1311-3_1_5_load_178 | 71 | 0.001798 | 0.00045062 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1311-3_1_5_load_156 | 72 | 0.00095209 | 0.00023862 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1311-3_1_5_load_153 | 73 | 0.0023129 | 0.00057966 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1311-3_1_5_load_154 | 74 | 0.0021571 | 0.00054062 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1311-3_1_5_load_155 | 75 | 0.00084297 | 0.00021127 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1311-3_1_5_load_157 | 76 | 0.00079101 | 0.00019825 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1311-3_1_5_load_158 | 77 | 0.0019297 | 0.00048362 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1311-3_1_5_load_159 | 78 | 0.002784 | 0.00069773 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1311-3_1_5_load_160 | 79 | 0.0025081 | 0.00062858 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1311-3_1_5_load_161 | 80 | 0.0028839 | 0.00072277 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1311-3_1_5_load_172 | 81 | 0.0037593 | 0.00094216 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1311-3_1_5_load_162 | 82 | 0.0015206 | 0.00038109 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1311-3_1_5_load_163 | 83 | 0.001513 | 0.0003792 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1311-3_1_5_load_165 | 85 | 0.00045787 | 0.00011475 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1311-3_1_5_load_166 | 86 | 0.0031321 | 0.00078498 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1311-3_1_5_load_167 | 87 | 0.0048282 | 0.0012101 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1311-3_1_5_load_177 | 89 | 0.0058494 | 0.001466 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1311-3_1_5_load_183 | 90 | 0.0017208 | 0.00043128 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1311-3_1_5_load_180 | 91 | 0.0018476 | 0.00046306 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1311-3_1_5_load_185 | 92 | 0.00044885 | 0.00011249 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1311-3_1_5_load_186 | 93 | 0.00018583 | 4.6573e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1311-3_1_5_load_175 | 94 | 0.0027845 | 0.00069786 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1311-3_1_5_load_179 | 95 | 0.0027223 | 0.00068228 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1311-3_1_5_load_181 | 96 | 0.00043697 | 0.00010951 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1311-3_1_5_load_192 | 97 | 0.0011013 | 0.00027601 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1311-3_1_5_load_187 | 98 | 0.00063508 | 0.00015917 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1311-3_1_5_load_188 | 99 | 0.00076815 | 0.00019252 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1311-3_1_5_load_190 | 101 | 0.0042082 | 0.0010547 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1311-3_1_5_load_191 | 102 | 0.00057978 | 0.00014531 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1311-3_1_5_load_207 | 103 | 0.0015945 | 0.00039963 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1311-3_1_5_load_201 | 104 | 0.00014816 | 3.7133e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1311-3_1_5_load_203 | 105 | 0.00049463 | 0.00012397 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 67 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1311-3_1_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.19656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1311-3_1_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.15354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1311-3_1_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.02041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1311-3_1_5_line_3 | NAYY 4x150 SE | 2 | 7 | 0.018854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1311-3_1_5_line_4 | NAYY 4x150 SE | 2 | 8 | 0.028706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1311-3_1_5_line_5 | NAYY 4x150 SE | 3 | 9 | 0.13632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1311-3_1_5_line_6 | NAYY 4x150 SE | 4 | 5 | 0.022109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1311-3_1_5_line_7 | NAYY 4x150 SE | 4 | 6 | 0.11761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1311-3_1_5_line_8 | NAYY 4x150 SE | 6 | 15 | 0.010811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1311-3_1_5_line_9 | NAYY 4x150 SE | 8 | 13 | 0.017772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1311-3_1_5_line_10 | NAYY 4x150 SE | 8 | 41 | 0.094818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1311-3_1_5_line_11 | NAYY 4x150 SE | 9 | 92 | 0.049112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1311-3_1_5_line_12 | NAYY 4x150 SE | 10 | 11 | 0.0058841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1311-3_1_5_line_13 | NAYY 4x150 SE | 11 | 103 | 0.004351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1311-3_1_5_line_14 | NAYY 4x150 SE | 12 | 13 | 0.014363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1311-3_1_5_line_15 | NAYY 4x150 SE | 12 | 14 | 0.19467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1311-3_1_5_line_16 | NAYY 4x150 SE | 15 | 57 | 0.030984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1311-3_1_5_line_17 | NAYY 4x150 SE | 16 | 17 | 0.18849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1311-3_1_5_line_18 | NAYY 4x150 SE | 17 | 18 | 0.023356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1311-3_1_5_line_19 | NAYY 4x150 SE | 18 | 19 | 0.068118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1311-3_1_5_line_20 | NAYY 4x150 SE | 19 | 23 | 0.20061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1311-3_1_5_line_21 | NAYY 4x150 SE | 19 | 24 | 0.17809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1311-3_1_5_line_22 | NAYY 4x150 SE | 20 | 21 | 0.17873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1311-3_1_5_line_23 | NAYY 4x150 SE | 20 | 22 | 0.012514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1311-3_1_5_line_24 | NAYY 4x150 SE | 21 | 25 | 0.12433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1311-3_1_5_line_25 | NAYY 4x150 SE | 22 | 26 | 0.091648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1311-3_1_5_line_26 | NAYY 4x150 SE | 23 | 32 | 0.017494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1311-3_1_5_line_27 | NAYY 4x150 SE | 24 | 33 | 0.2156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1311-3_1_5_line_28 | NAYY 4x150 SE | 25 | 34 | 0.22454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1311-3_1_5_line_29 | NAYY 4x150 SE | 25 | 31 | 0.07671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1311-3_1_5_line_30 | NAYY 4x150 SE | 26 | 33 | 0.053756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1311-3_1_5_line_31 | NAYY 4x150 SE | 27 | 28 | 0.0052701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1311-3_1_5_line_32 | NAYY 4x150 SE | 28 | 29 | 0.0066813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1311-3_1_5_line_33 | NAYY 4x150 SE | 29 | 30 | 0.0083025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1311-3_1_5_line_34 | NAYY 4x150 SE | 30 | 31 | 0.11398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1311-3_1_5_line_35 | NAYY 4x150 SE | 32 | 38 | 0.26826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1311-3_1_5_line_36 | NAYY 4x150 SE | 34 | 35 | 0.028962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1311-3_1_5_line_37 | NAYY 4x150 SE | 35 | 39 | 0.03705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1311-3_1_5_line_38 | NAYY 4x150 SE | 36 | 37 | 0.15171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1311-3_1_5_line_39 | NAYY 4x150 SE | 37 | 97 | 0.17784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1311-3_1_5_line_40 | NAYY 4x150 SE | 38 | 96 | 0.078203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1311-3_1_5_line_41 | NAYY 4x150 SE | 39 | 104 | 0.096693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1311-3_1_5_line_42 | NAYY 4x150 SE | 40 | 41 | 0.017572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1311-3_1_5_line_43 | NAYY 4x150 SE | 42 | 43 | 0.096997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1311-3_1_5_line_44 | NAYY 4x150 SE | 42 | 44 | 0.037494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1311-3_1_5_line_45 | NAYY 4x150 SE | 43 | 45 | 0.00758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1311-3_1_5_line_46 | NAYY 4x150 SE | 44 | 46 | 0.031926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1311-3_1_5_line_47 | NAYY 4x150 SE | 44 | 47 | 0.069557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1311-3_1_5_line_48 | NAYY 4x150 SE | 45 | 48 | 0.022199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1311-3_1_5_line_49 | NAYY 4x150 SE | 45 | 49 | 0.041678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_1311-3_1_5_line_50 | NAYY 4x150 SE | 47 | 54 | 0.16893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1311-3_1_5_line_51 | NAYY 4x150 SE | 47 | 55 | 0.06785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1311-3_1_5_line_52 | NAYY 4x150 SE | 48 | 69 | 0.11711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1311-3_1_5_line_53 | NAYY 4x150 SE | 49 | 94 | 0.02759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1311-3_1_5_line_54 | NAYY 4x150 SE | 50 | 51 | 0.11962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1311-3_1_5_line_55 | NAYY 4x150 SE | 50 | 52 | 0.04281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1311-3_1_5_line_56 | NAYY 4x150 SE | 51 | 53 | 0.1114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1311-3_1_5_line_57 | NAYY 4x150 SE | 52 | 102 | 0.032559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1311-3_1_5_line_58 | NAYY 4x150 SE | 53 | 64 | 0.015073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1311-3_1_5_line_59 | NAYY 4x150 SE | 54 | 90 | 0.0049193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1311-3_1_5_line_60 | NAYY 4x150 SE | 54 | 91 | 0.0075684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1311-3_1_5_line_61 | NAYY 4x150 SE | 56 | 57 | 0.019488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1311-3_1_5_line_62 | NAYY 4x150 SE | 56 | 58 | 0.018202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1311-3_1_5_line_63 | NAYY 4x150 SE | 57 | 59 | 0.00236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1311-3_1_5_line_64 | NAYY 4x150 SE | 58 | 60 | 0.011695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1311-3_1_5_line_65 | NAYY 4x150 SE | 58 | 61 | 0.033012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1311-3_1_5_line_66 | NAYY 4x150 SE | 59 | 62 | 0.014899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1311-3_1_5_line_67 | NAYY 4x150 SE | 61 | 63 | 0.0063316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1311-3_1_5_line_68 | NAYY 4x150 SE | 62 | 66 | 0.0068742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1311-3_1_5_line_69 | NAYY 4x150 SE | 63 | 103 | 0.0027921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1311-3_1_5_line_70 | NAYY 4x150 SE | 64 | 65 | 0.027101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1311-3_1_5_line_71 | NAYY 4x150 SE | 66 | 67 | 0.026985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1311-3_1_5_line_72 | NAYY 4x150 SE | 67 | 68 | 0.056243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1311-3_1_5_line_73 | NAYY 4x150 SE | 67 | 69 | 0.045495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
74 | LV_1311-3_1_5_line_74 | NAYY 4x150 SE | 67 | 70 | 0.013913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1311-3_1_5_line_75 | NAYY 4x150 SE | 68 | 71 | 0.012117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1311-3_1_5_line_76 | NAYY 4x150 SE | 70 | 72 | 0.0012288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1311-3_1_5_line_77 | NAYY 4x150 SE | 71 | 95 | 0.042682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1311-3_1_5_line_78 | NAYY 4x150 SE | 72 | 74 | 0.017064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1311-3_1_5_line_79 | NAYY 4x150 SE | 73 | 74 | 0.021783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1311-3_1_5_line_80 | NAYY 4x150 SE | 73 | 75 | 0.0059682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1311-3_1_5_line_81 | NAYY 4x150 SE | 75 | 76 | 0.033196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1311-3_1_5_line_82 | NAYY 4x150 SE | 77 | 78 | 0.017247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1311-3_1_5_line_83 | NAYY 4x150 SE | 77 | 79 | 0.01396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1311-3_1_5_line_84 | NAYY 4x150 SE | 78 | 80 | 0.012391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1311-3_1_5_line_85 | NAYY 4x150 SE | 80 | 81 | 0.0058724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1311-3_1_5_line_86 | NAYY 4x150 SE | 81 | 86 | 0.011107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1311-3_1_5_line_87 | NAYY 4x150 SE | 82 | 83 | 0.0011728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1311-3_1_5_line_88 | NAYY 4x150 SE | 82 | 84 | 0.035104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_1311-3_1_5_line_89 | NAYY 4x150 SE | 83 | 85 | 0.04945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1311-3_1_5_line_90 | NAYY 4x150 SE | 84 | 86 | 0.024715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1311-3_1_5_line_91 | NAYY 4x150 SE | 84 | 87 | 0.007305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_1311-3_1_5_line_92 | NAYY 4x150 SE | 85 | 88 | 0.044431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1311-3_1_5_line_93 | NAYY 4x150 SE | 87 | 89 | 0.035895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
94 | LV_1311-3_1_5_line_94 | NAYY 4x150 SE | 88 | 92 | 0.022641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1311-3_1_5_line_95 | NAYY 4x150 SE | 88 | 93 | 0.030185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1311-3_1_5_line_96 | NAYY 4x150 SE | 89 | 94 | 0.027424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
97 | LV_1311-3_1_5_line_97 | NAYY 4x150 SE | 91 | 96 | 0.047909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1311-3_1_5_line_98 | NAYY 4x150 SE | 93 | 97 | 0.043015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1311-3_1_5_line_99 | NAYY 4x150 SE | 97 | 101 | 0.033002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1311-3_1_5_line_100 | NAYY 4x150 SE | 98 | 99 | 0.03968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1311-3_1_5_line_101 | NAYY 4x150 SE | 98 | 100 | 0.033845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1311-3_1_5_line_102 | NAYY 4x150 SE | 99 | 101 | 0.034657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1311-3_1_5_line_103 | NAYY 4x150 SE | 100 | 102 | 0.0072903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1311-3_1_5_line_104 | NAYY 4x150 SE | 104 | 105 | 0.0096706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1311-3_1_5_trafo_149 | 0.25 MVA 20/0.4 kV | 106 | 67 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25
0 | 2682956.0341 | 1206067.6092 | 2682958.5482 | 1206047.0754 | 2682955.0464 | 1206017.1853 | 2682955.3067 | 1205999.5554 | 2682963.0819 | 1205966.0753 | 2682965.5848 | 1205960.0284 | 2682974.1127 | 1205956.1221 | 2682988.9979 | 1205941.3973 | 2683008.7544 | 1205927.0071 | 2683012.9363 | 1205907.9863 | 2683017.2676 | 1205895.7276
1 | 2682872.2738 | 1206196.2844 | 2682956.0341 | 1206067.6092
2 | 2683023.7834 | 1205876.806 | 2683021.8559 | 1205888.509 | 2683017.2676 | 1205895.7276
3 | 2682872.2738 | 1206196.2844 | 2682878.7709 | 1206201.111 | 2682888.4961 | 1206205.7156
4 | 2682846.0434 | 1206185.091 | 2682858.9795 | 1206188.5282 | 2682872.2738 | 1206196.2844
5 | 2683023.7834 | 1205876.806 | 2683016.4247 | 1205872.1118 | 2683010.13 | 1205862.5626 | 2683008.8333 | 1205852.9718 | 2683010.8257 | 1205841.5255 | 2683010.8359 | 1205833.6872 | 2683008.3588 | 1205828.5718 | 2682995.5361 | 1205819.1208 | 2682980.5402 | 1205804.5809 | 2682974.7202 | 1205796.984 | 2682965.3356 | 1205781.5215 | 2682960.4929 | 1205778.5857 | 2682949.6131 | 1205775.9172
6 | 2682896.4721 | 1205872.4346 | 2682884.9073 | 1205868.8051 | 2682874.8747 | 1205868.221
7 | 2682896.4721 | 1205872.4346 | 2682922.769 | 1205875.1014 | 2682920.5038 | 1205864.0406 | 2682912.1076 | 1205854.6291 | 2682897.9327 | 1205844.4925 | 2682857.8111 | 1205814.9112
8 | 2682857.8111 | 1205814.9112 | 2682849.1097 | 1205808.4958
9 | 2682846.0434 | 1206185.091 | 2682837.7581 | 1206174.8361 | 2682835.0552 | 1206171.1279
10 | 2682846.0434 | 1206185.091 | 2682855.2396 | 1206198.2159 | 2682859.1908 | 1206206.7206 | 2682861.2163 | 1206216.4216 | 2682863.3485 | 1206232.6728 | 2682871.6915 | 1206250.2665 | 2682873.4206 | 1206257.7509 | 2682871.8757 | 1206262.1989 | 2682868.464 | 1206266.332 | 2682862.9055 | 1206268.4118
11 | 2682911.2919 | 1205748.5378 | 2682913.2018 | 1205752.3232 | 2682919.7398 | 1205760.8083 | 2682933.5558 | 1205771.5959 | 2682942.9053 | 1205774.2719 | 2682949.6131 | 1205775.9172
12 | 2682895.1671 | 1205802.8359 | 2682898.4052 | 1205803.9064 | 2682900.8681 | 1205803.6773
13 | 2682891.3815 | 1205800.7655 | 2682893.7712 | 1205802.3744 | 2682895.1671 | 1205802.8359
14 | 2682827.6908 | 1206158.8511 | 2682831.2495 | 1206165.9068 | 2682835.0552 | 1206171.1279
15 | 2682827.6908 | 1206158.8511 | 2682771.3175 | 1205972.5184
16 | 2682819.4529 | 1205804.1111 | 2682826.2889 | 1205805.3734 | 2682835.2262 | 1205804.3189 | 2682841.6392 | 1205804.2745 | 2682846.4608 | 1205806.5428 | 2682849.1097 | 1205808.4958
17 | 2682517.2229 | 1206157.2555 | 2682515.4438 | 1206154.6607 | 2682502.565 | 1206127.2541 | 2682499.2046 | 1206121.0926 | 2682496.0524 | 1206118.0249 | 2682490.7558 | 1206116.5619 | 2682479.5219 | 1206115.4282 | 2682472.365 | 1206113.1835 | 2682466.6369 | 1206106.6224 | 2682466.2496 | 1206099.9683 | 2682469.4013 | 1206092.6183 | 2682477.0863 | 1206085.82 | 2682489.5437 | 1206076.0414 | 2682513.3973 | 1206062.818 | 2682522.0704 | 1206056.6339 | 2682525.3799 | 1206046.6733 | 2682523.8215 | 1206035.6113 | 2682518.5201 | 1206026.7879
18 | 2682518.5201 | 1206026.7879 | 2682518.5201 | 1206026.7879 | 2682507.199 | 1206021.4948 | 2682496.7155 | 1206018.6671
19 | 2682470.6553 | 1205968.8451 | 2682466.356 | 1205982.728 | 2682466.2471 | 1205994.4674 | 2682469.1953 | 1206004.5923 | 2682478.8961 | 1206012.1089 | 2682490.4286 | 1206016.9713 | 2682496.7155 | 1206018.6671
20 | 2682470.6553 | 1205968.8451 | 2682473.0836 | 1205961.007 | 2682470.8558 | 1205952.1372 | 2682456.0942 | 1205916.7218 | 2682451.52 | 1205907.5528 | 2682443.3411 | 1205903.8375 | 2682427.1236 | 1205902.7685 | 2682418.7653 | 1205898.8172 | 2682413.6101 | 1205893.1647 | 2682412.2928 | 1205886.6535 | 2682414.6794 | 1205868.6082 | 2682413.7737 | 1205860.9352 | 2682401.7945 | 1205842.6693 | 2682381.2126 | 1205821.0715 | 2682374.9014 | 1205815.7425
21 | 2682470.6553 | 1205968.8451 | 2682464.4834 | 1205954.2061 | 2682456.021 | 1205946.2397 | 2682448.1534 | 1205939.8158 | 2682437.9658 | 1205935.5947 | 2682435.9767 | 1205934.7667 | 2682424.3185 | 1205931.2814 | 2682416.0959 | 1205930.1783 | 2682400.1007 | 1205934.4936 | 2682390.2138 | 1205936.036 | 2682386.6032 | 1205933.1065 | 2682384.5384 | 1205924.5392 | 2682379.8259 | 1205921.5278 | 2682368.1183 | 1205923.2675 | 2682355.2353 | 1205917.0302 | 2682341.9709 | 1205919.1376 | 2682331.6877 | 1205924.5993 | 2682329.1235 | 1205934.1892
22 | 2682347.0434 | 1206058.6858 | 2682345.7448 | 1206063.4932 | 2682345.454 | 1206096.6993 | 2682349.1746 | 1206107.6354 | 2682350.3841 | 1206118.1032 | 2682346.5744 | 1206122.4424 | 2682340.1035 | 1206125.5996 | 2682329.5853 | 1206131.5806 | 2682323.8051 | 1206144.7761 | 2682305.2322 | 1206175.5509 | 2682286.2316 | 1206203.1623 | 2682281.2917 | 1206211.294
23 | 2682347.0434 | 1206058.6858 | 2682334.5803 | 1206057.561
24 | 2682324.1103 | 1206299.6351 | 2682321.129 | 1206293.0008 | 2682314.0428 | 1206288.4002 | 2682302.5306 | 1206285.4063 | 2682283.6518 | 1206277.7301 | 2682275.0467 | 1206267.9941 | 2682270.2236 | 1206262.5353 | 2682265.7565 | 1206251.122 | 2682265.6217 | 1206242.1366 | 2682268.9305 | 1206231.6421 | 2682281.2917 | 1206211.294
25 | 2682334.5803 | 1206057.561 | 2682333.8096 | 1206057.4914 | 2682327.8217 | 1206055.9634 | 2682315.2211 | 1206057.9466 | 2682309.0908 | 1206057.9176 | 2682303.723 | 1206053.8966 | 2682300.992 | 1206047.8551 | 2682300.0031 | 1206040.1365 | 2682296.8127 | 1206031.5537 | 2682269.5828 | 1206018.2478 | 2682264.3887 | 1206017.669
26 | 2682361.5353 | 1205804.4562 | 2682374.9014 | 1205815.7425
27 | 2682212.7409 | 1206028.705 | 2682232.1375 | 1206010.4604 | 2682233.4176 | 1206000.9163 | 2682234.862 | 1205992.1417 | 2682234.7536 | 1205984.0017 | 2682237.8282 | 1205978.9185 | 2682243.5943 | 1205977.2302 | 2682249.7884 | 1205975.948 | 2682251.462 | 1205973.1693 | 2682248.4621 | 1205967.3131 | 2682242.2791 | 1205959.5119 | 2682240.1081 | 1205954.223 | 2682234.9577 | 1205948.2149 | 2682236.4109 | 1205941.564 | 2682239.662 | 1205938.5735 | 2682243.4457 | 1205933.3668 | 2682251.6061 | 1205931.8115 | 2682262.6091 | 1205935.3764 | 2682271.898 | 1205938.0394 | 2682280.0659 | 1205942.5549 | 2682285.4829 | 1205944.6753 | 2682303.2588 | 1205942.4966 | 2682314.4899 | 1205941.1061 | 2682326.019 | 1205940.7203 | 2682327.7898 | 1205939.1771 | 2682329.1235 | 1205934.1892
28 | 2682324.1103 | 1206299.6351 | 2682343.2905 | 1206294.285 | 2682355.1175 | 1206294.8596 | 2682364.8372 | 1206299.8746 | 2682372.0037 | 1206312.9819 | 2682382.914 | 1206320.4594 | 2682394.0317 | 1206327.7841 | 2682401.4485 | 1206334.324 | 2682412.0076 | 1206340.785 | 2682425.0083 | 1206345.0338 | 2682431.1636 | 1206342.6839 | 2682439.5715 | 1206331.982 | 2682447.6333 | 1206322.1092 | 2682456.573 | 1206316.9627 | 2682471.9997 | 1206311.8836 | 2682479.9173 | 1206310.8034 | 2682489.6048 | 1206313.7391 | 2682499.4433 | 1206323.9037 | 2682502.0468 | 1206332.5452 | 2682502.2286 | 1206336.1805
29 | 2682324.1103 | 1206299.6351 | 2682318.5849 | 1206302.0938 | 2682309.8219 | 1206300.5053 | 2682262.5411 | 1206303.9449 | 2682255.575 | 1206304.427 | 2682250.1831 | 1206299.4051
30 | 2682212.7409 | 1206028.705 | 2682239.2597 | 1206024.6231 | 2682256.1478 | 1206016.7506 | 2682264.3887 | 1206017.669
31 | 2682213.3824 | 1206195.341 | 2682218.6435 | 1206195.6496
32 | 2682225.3133 | 1206196.0408 | 2682218.6435 | 1206195.6496
33 | 2682225.3133 | 1206196.0408 | 2682225.3133 | 1206196.0408 | 2682232.259 | 1206200.5893
34 | 2682250.1831 | 1206299.4051 | 2682248.3705 | 1206279.156 | 2682246.8847 | 1206273.8321 | 2682242.8605 | 1206271.6642 | 2682232.282 | 1206264.3805 | 2682224.8912 | 1206256.4848 | 2682224.0034 | 1206249.1568 | 2682228.0433 | 1206238.0386 | 2682236.4344 | 1206211.9819 | 2682235.7536 | 1206202.8778 | 2682232.259 | 1206200.5893
35 | 2682361.5353 | 1205804.4562 | 2682331.1193 | 1205780.5325 | 2682320.7565 | 1205770.2387 | 2682306.1721 | 1205756.6178 | 2682302.8687 | 1205750.157 | 2682303.7724 | 1205745.2997 | 2682305.9725 | 1205741.8612 | 2682316.0043 | 1205739.7648 | 2682326.0977 | 1205746.4304 | 2682337.848 | 1205757.0547 | 2682358.7987 | 1205767.9506 | 2682371.2331 | 1205775.8494 | 2682385.3214 | 1205778.0006 | 2682409.1237 | 1205776.2724 | 2682432.5876 | 1205777.0189 | 2682455.3059 | 1205782.1803 | 2682471.39 | 1205788.5534
36 | 2682506.2958 | 1206364.6468 | 2682506.694 | 1206362.2507 | 2682504.5548 | 1206353.5934 | 2682502.6188 | 1206343.9827 | 2682502.2286 | 1206336.1805
37 | 2682506.2958 | 1206364.6468 | 2682503.1177 | 1206366.215 | 2682494.6845 | 1206363.8859 | 2682472.885 | 1206358.4479 | 2682470.6092 | 1206358.695
38 | 2683100.7696 | 1205624.4149 | 2683107.4858 | 1205617.9041 | 2683116.6728 | 1205610.4161 | 2683129.9157 | 1205597.3587 | 2683133.6018 | 1205596.4983 | 2683138.3718 | 1205598.1102 | 2683141.1403 | 1205604.1415 | 2683139.2978 | 1205627.1973 | 2683140.316 | 1205633.8269 | 2683144.0055 | 1205640.3713 | 2683151.9001 | 1205652.4779 | 2683154.3649 | 1205657.9268 | 2683154.665 | 1205665.8694 | 2683149.2197 | 1205696.1063
39 | 2682937.2062 | 1205694.2171 | 2683100.7696 | 1205624.4149
40 | 2682471.39 | 1205788.5534 | 2682475.8607 | 1205790.3249 | 2682495.248 | 1205799.8321 | 2682511.1518 | 1205812.0597 | 2682519.198 | 1205818.2303 | 2682528.8939 | 1205827.2145 | 2682536.8759 | 1205829.7709 | 2682536.8759 | 1205829.7709
41 | 2682381.3826 | 1206368.9075 | 2682387.5013 | 1206372.1781 | 2682398.886 | 1206375.5818 | 2682410.7053 | 1206376.1564 | 2682420.9029 | 1206376.2972 | 2682432.3079 | 1206377.6777 | 2682441.3168 | 1206375.7675 | 2682450.8168 | 1206366.9486 | 2682460.7124 | 1206359.7695 | 2682470.6092 | 1206358.695
42 | 2682862.9055 | 1206268.4118 | 2682877.8836 | 1206277.5996
43 | 2682669.4893 | 1205730.953 | 2682665.4147 | 1205730.7632 | 2682654.8009 | 1205728.1924 | 2682651.0424 | 1205724.9494 | 2682647.4192 | 1205718.5285 | 2682646.5514 | 1205701.55 | 2682637.3284 | 1205680.9314 | 2682630.4779 | 1205672.4534 | 2682619.4726 | 1205669.0323 | 2682611.825 | 1205668.9264
44 | 2682574.9486 | 1205665.8256 | 2682577.4672 | 1205667.417 | 2682587.7117 | 1205669.2042 | 2682610.2549 | 1205668.9047 | 2682611.825 | 1205668.9264
45 | 2682669.4893 | 1205730.953 | 2682670.7245 | 1205738.4305
46 | 2682574.9486 | 1205665.8256 | 2682573.2973 | 1205672.4625 | 2682572.6644 | 1205675.3223 | 2682580.5645 | 1205682.1692 | 2682588.2232 | 1205691.0586
47 | 2682574.9486 | 1205665.8256 | 2682571.1704 | 1205663.4496 | 2682565.5386 | 1205655.3999 | 2682560.9862 | 1205644.1075 | 2682555.8857 | 1205637.2437 | 2682549.1757 | 1205636.1947 | 2682541.1748 | 1205636.0841 | 2682522.0306 | 1205641.4229
48 | 2682670.7245 | 1205738.4305 | 2682672.1052 | 1205756.2721 | 2682673.4147 | 1205760.3719
49 | 2682670.7245 | 1205738.4305 | 2682675.6312 | 1205737.3088 | 2682681.914 | 1205729.6464 | 2682692.8665 | 1205714.9108 | 2682699.2348 | 1205709.4704
50 | 2682522.0306 | 1205641.4229 | 2682504.283 | 1205651.3841 | 2682493.5444 | 1205660.0302 | 2682488.644 | 1205667.3005 | 2682488.1746 | 1205678.1454 | 2682499.488 | 1205720.9179 | 2682505.7278 | 1205744.964 | 2682515.5782 | 1205769.1934 | 2682527.7572 | 1205785.0941
51 | 2682522.0306 | 1205641.4229 | 2682507.9515 | 1205641.8842 | 2682490.6161 | 1205643.4902 | 2682471.3901 | 1205643.1912 | 2682455.938 | 1205642.2772 | 2682454.3901 | 1205641.7151
52 | 2682727.0679 | 1205802.2439 | 2682725.8294 | 1205803.0683 | 2682722.7346 | 1205807.3726 | 2682718.7185 | 1205813.3986 | 2682716.7204 | 1205824.7449 | 2682711.1662 | 1205829.7823 | 2682703.6343 | 1205829.8781 | 2682699.988 | 1205826.2364 | 2682696.992 | 1205819.0236 | 2682680.7537 | 1205772.7691 | 2682674.5986 | 1205764.0783 | 2682673.4147 | 1205760.3719
53 | 2682722.7576 | 1205695.3555 | 2682720.1825 | 1205696.2438 | 2682704.2132 | 1205705.2173 | 2682699.2348 | 1205709.4704
54 | 2682760.2832 | 1205570.2409 | 2682748.7025 | 1205572.6486 | 2682736.3989 | 1205565.1956 | 2682725.6433 | 1205553.0722 | 2682712.8991 | 1205549.9604 | 2682699.8767 | 1205552.1036 | 2682692.9413 | 1205558.5339 | 2682685.434 | 1205569.4592 | 2682679.7907 | 1205552.359 | 2682676.5236 | 1205542.7409
55 | 2682760.2832 | 1205570.2409 | 2682767.5631 | 1205574.0776 | 2682800.8827 | 1205583.3317
56 | 2682676.5236 | 1205542.7409 | 2682674.6152 | 1205556.957 | 2682670.3897 | 1205574.7877 | 2682663.3059 | 1205592.4898 | 2682655.1516 | 1205599.6038 | 2682649.7118 | 1205601.8633 | 2682646.3234 | 1205603.7509 | 2682641.9491 | 1205602.6786 | 2682638.6419 | 1205598.1521 | 2682630.3588 | 1205584.9068 | 2682628.1934 | 1205571.7379
57 | 2682832.2544 | 1205592.0448 | 2682800.8827 | 1205583.3317
58 | 2682624.7878 | 1205557.0786 | 2682627.1594 | 1205565.4501 | 2682628.1934 | 1205571.7379
59 | 2682527.7572 | 1205785.0941 | 2682532.0411 | 1205787.5123
60 | 2682527.7572 | 1205785.0941 | 2682531.9114 | 1205791.4205
61 | 2682819.4529 | 1205804.1111 | 2682832.1692 | 1205797.1274 | 2682836.6444 | 1205794.9419
62 | 2682853.0006 | 1205786.9543 | 2682836.6444 | 1205794.9419
63 | 2682819.4529 | 1205804.1111 | 2682817.1808 | 1205803.4728
64 | 2682853.0006 | 1205786.9543 | 2682864.2874 | 1205783.7755
65 | 2682853.0006 | 1205786.9543 | 2682857.2106 | 1205788.8917 | 2682865.4835 | 1205790.7633 | 2682878.377 | 1205791.2981 | 2682881.6982 | 1205794.2461 | 2682883.8133 | 1205795.6701
66 | 2682817.1808 | 1205803.4728 | 2682807.2537 | 1205800.6841 | 2682802.6996 | 1205800.1313
67 | 2682883.8133 | 1205795.6701 | 2682889.0655 | 1205799.2062
68 | 2682795.8547 | 1205800.004 | 2682799.7054 | 1205799.7678 | 2682802.6996 | 1205800.1313
69 | 2682891.3815 | 1205800.7655 | 2682889.0655 | 1205799.2062
70 | 2682624.7878 | 1205557.0786 | 2682620.503 | 1205556.1298 | 2682611.4324 | 1205549.211 | 2682603.5264 | 1205543.8871 | 2682602.0072 | 1205542.9729
71 | 2682769.5122 | 1205797.192 | 2682780.6345 | 1205800.9375 | 2682795.8547 | 1205800.004
72 | 2682769.5122 | 1205797.192 | 2682786.6756 | 1205768.4782 | 2682796.5475 | 1205751.0483 | 2682798.3405 | 1205748.9506
73 | 2682769.5122 | 1205797.192 | 2682762.3114 | 1205794.8018 | 2682751.4207 | 1205792.4605 | 2682740.3671 | 1205794.1862 | 2682735.9406 | 1205796.3374 | 2682727.0679 | 1205802.2439
74 | 2682769.5122 | 1205797.192 | 2682767.621 | 1205810.9764
75 | 2682798.3405 | 1205748.9506 | 2682802.5864 | 1205743.9831 | 2682807.261 | 1205740.9327
76 | 2682767.621 | 1205810.9764 | 2682767.454 | 1205812.1938
77 | 2682848.2444 | 1205731.7529 | 2682820.3439 | 1205734.4232 | 2682810.8614 | 1205738.5832 | 2682807.261 | 1205740.9327
78 | 2682767.454 | 1205812.1938 | 2682766.7367 | 1205817.4221 | 2682761.4712 | 1205827.967 | 2682761.4712 | 1205827.967
79 | 2682748.1615 | 1205845.1741 | 2682752.5143 | 1205838.672 | 2682761.4712 | 1205827.967
80 | 2682748.1615 | 1205845.1741 | 2682744.8415 | 1205850.1336
81 | 2682727.3586 | 1205878.0916 | 2682728.7033 | 1205873.4088 | 2682741.0029 | 1205855.8679 | 2682744.8415 | 1205850.1336
82 | 2682727.2531 | 1205746.144 | 2682728.4766 | 1205738.8527 | 2682733.8776 | 1205730.6111 | 2682733.8776 | 1205730.6111
83 | 2682727.5055 | 1205760.0751 | 2682727.0173 | 1205747.5492 | 2682727.2531 | 1205746.144
84 | 2682733.8776 | 1205730.6111 | 2682738.4242 | 1205728.028 | 2682745.5729 | 1205727.5935
85 | 2682751.1355 | 1205729.4757 | 2682745.5729 | 1205727.5935
86 | 2682751.1355 | 1205729.4757 | 2682761.2302 | 1205732.8916 | 2682761.6773 | 1205732.8391
87 | 2682811.8449 | 1205713.1312 | 2682813.0142 | 1205713.221
88 | 2682778.6094 | 1205718.2453 | 2682783.4604 | 1205714.0098 | 2682794.2549 | 1205711.7803 | 2682811.8449 | 1205713.1312
89 | 2682813.0142 | 1205713.221 | 2682825.7059 | 1205714.1957 | 2682849.8032 | 1205715.9088 | 2682862.1223 | 1205713.4448
90 | 2682778.6094 | 1205718.2453 | 2682777.5295 | 1205722.0661 | 2682775.7125 | 1205725.8322 | 2682769.4437 | 1205731.927 | 2682761.6773 | 1205732.8391
91 | 2682778.6094 | 1205718.2453 | 2682771.69 | 1205715.9036
92 | 2682903.8415 | 1205727.4217 | 2682897.9232 | 1205724.7045 | 2682889.4746 | 1205720.6846 | 2682869.6424 | 1205713.6604 | 2682862.1223 | 1205713.4448
93 | 2682749.1422 | 1205690.1634 | 2682749.1422 | 1205690.1634 | 2682752.0584 | 1205694.3509 | 2682758.5286 | 1205707.7492 | 2682762.3014 | 1205712.1487 | 2682768.8804 | 1205714.9528 | 2682771.69 | 1205715.9036
94 | 2682903.8415 | 1205727.4217 | 2682905.4509 | 1205736.9613 | 2682911.2919 | 1205748.5378
95 | 2682903.8415 | 1205727.4217 | 2682910.6148 | 1205726.6374 | 2682916.7412 | 1205726.4224 | 2682925.9011 | 1205727.9728 | 2682933.8338 | 1205727.5048 | 2682933.8338 | 1205727.5048
96 | 2682749.1422 | 1205690.1634 | 2682744.6901 | 1205689.2233 | 2682738.1215 | 1205690.055 | 2682722.7576 | 1205695.3555
97 | 2682536.8759 | 1205829.7709 | 2682543.2422 | 1205827.0572 | 2682547.0981 | 1205819.9504 | 2682546.4189 | 1205813.5146 | 2682531.9114 | 1205791.4205
98 | 2682933.8338 | 1205727.5048 | 2682940.262 | 1205723.6361 | 2682942.8546 | 1205722.0933 | 2682946.4141 | 1205716.6504 | 2682947.3234 | 1205710.3367 | 2682944.9277 | 1205702.0982 | 2682937.2062 | 1205694.2171
99 | 2682937.2062 | 1205694.2171 | 2682928.9368 | 1205685.7767 | 2682918.5119 | 1205679.4613 | 2682913.0365 | 1205672.3218
100 | 2682864.4238 | 1205616.649 | 2682884.766 | 1205634.1416 | 2682892.3929 | 1205644.485
101 | 2682839.2788 | 1205593.9958 | 2682862.4778 | 1205614.9755 | 2682864.4238 | 1205616.649
102 | 2682892.3929 | 1205644.485 | 2682909.9795 | 1205668.3357 | 2682913.0365 | 1205672.3218
103 | 2682839.2788 | 1205593.9958 | 2682832.2544 | 1205592.0448
104 | 2682372.8539 | 1206364.3487 | 2682381.3826 | 1206368.9075

## bus_geodata
| x | y | coords
0 | 2682956.0341 | 1206067.6092
1 | 2683017.2676 | 1205895.7276
2 | 2682872.2738 | 1206196.2844
3 | 2683023.7834 | 1205876.806
4 | 2682896.4721 | 1205872.4346
5 | 2682874.8747 | 1205868.221
6 | 2682857.8111 | 1205814.9112
7 | 2682888.4961 | 1206205.7156
8 | 2682846.0434 | 1206185.091
9 | 2682949.6131 | 1205775.9172
10 | 2682900.8681 | 1205803.6773
11 | 2682895.1671 | 1205802.8359
12 | 2682827.6908 | 1206158.8511
13 | 2682835.0552 | 1206171.1279
14 | 2682771.3175 | 1205972.5184
15 | 2682849.1097 | 1205808.4958
16 | 2682517.2229 | 1206157.2555
17 | 2682518.5201 | 1206026.7879
18 | 2682496.7155 | 1206018.6671
19 | 2682470.6553 | 1205968.8451
20 | 2682347.0434 | 1206058.6858
21 | 2682281.2917 | 1206211.294
22 | 2682334.5803 | 1206057.561
23 | 2682374.9014 | 1205815.7425
24 | 2682329.1235 | 1205934.1892
25 | 2682324.1103 | 1206299.6351
26 | 2682264.3887 | 1206017.669
27 | 2682213.3824 | 1206195.341
28 | 2682218.6435 | 1206195.6496
29 | 2682225.3133 | 1206196.0408
30 | 2682232.259 | 1206200.5893
31 | 2682250.1831 | 1206299.4051
32 | 2682361.5353 | 1205804.4562
33 | 2682212.7409 | 1206028.705
34 | 2682502.2286 | 1206336.1805
35 | 2682506.2958 | 1206364.6468
36 | 2683149.2197 | 1205696.1063
37 | 2683100.7696 | 1205624.4149
38 | 2682471.39 | 1205788.5534
39 | 2682470.6092 | 1206358.695
40 | 2682877.8836 | 1206277.5996
41 | 2682862.9055 | 1206268.4118
42 | 2682611.825 | 1205668.9264
43 | 2682669.4893 | 1205730.953
44 | 2682574.9486 | 1205665.8256
45 | 2682670.7245 | 1205738.4305
46 | 2682588.2232 | 1205691.0586
47 | 2682522.0306 | 1205641.4229
48 | 2682673.4147 | 1205760.3719
49 | 2682699.2348 | 1205709.4704
50 | 2682760.2832 | 1205570.2409
51 | 2682676.5236 | 1205542.7409
52 | 2682800.8828 | 1205583.3317
53 | 2682628.1934 | 1205571.7379
54 | 2682527.7572 | 1205785.0941
55 | 2682454.3901 | 1205641.7151
56 | 2682836.6444 | 1205794.9419
57 | 2682819.4529 | 1205804.1111
58 | 2682853.0006 | 1205786.9543
59 | 2682817.1808 | 1205803.4728
60 | 2682864.2874 | 1205783.7755
61 | 2682883.8133 | 1205795.6701
62 | 2682802.6996 | 1205800.1313
63 | 2682889.0655 | 1205799.2062
64 | 2682624.7878 | 1205557.0786
65 | 2682602.0072 | 1205542.9729
66 | 2682795.8547 | 1205800.004
67 | 2682769.5122 | 1205797.192
68 | 2682798.3405 | 1205748.9506
69 | 2682727.0679 | 1205802.2439
70 | 2682767.621 | 1205810.9764
71 | 2682807.261 | 1205740.9327
72 | 2682767.454 | 1205812.1938
73 | 2682748.1615 | 1205845.1741
74 | 2682761.4712 | 1205827.967
75 | 2682744.8415 | 1205850.1336
76 | 2682727.3586 | 1205878.0916
77 | 2682727.2531 | 1205746.144
78 | 2682733.8776 | 1205730.6111
79 | 2682727.5055 | 1205760.0751
80 | 2682745.5729 | 1205727.5935
81 | 2682751.1355 | 1205729.4757
82 | 2682811.8449 | 1205713.1312
83 | 2682813.0142 | 1205713.221
84 | 2682778.6094 | 1205718.2453
85 | 2682862.1223 | 1205713.4448
86 | 2682761.6773 | 1205732.8391
87 | 2682771.69 | 1205715.9036
88 | 2682903.8415 | 1205727.4217
89 | 2682749.1422 | 1205690.1634
90 | 2682532.0411 | 1205787.5123
91 | 2682531.9114 | 1205791.4205
92 | 2682911.2919 | 1205748.5378
93 | 2682933.8338 | 1205727.5048
94 | 2682722.7576 | 1205695.3555
95 | 2682848.2444 | 1205731.7529
96 | 2682536.8759 | 1205829.7709
97 | 2682937.2062 | 1205694.2171
98 | 2682864.4238 | 1205616.649
99 | 2682892.3929 | 1205644.485
100 | 2682839.2788 | 1205593.9958
101 | 2682913.0365 | 1205672.3218
102 | 2682832.2544 | 1205592.0448
103 | 2682891.3815 | 1205800.7655
104 | 2682381.3826 | 1206368.9075
105 | 2682372.8539 | 1206364.3487
106 | 2682819.4529 | 1205804.1111

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97311 | -0.19014 | 0 | 0
1 | 0.97568 | -0.17167 | 0 | 0
2 | 0.97111 | -0.20461 | 0 | 0
3 | 0.97594 | -0.16975 | 0 | 0
4 | 0.998 | -0.014003 | 0 | 0
5 | 0.99799 | -0.014137 | 0.00060303 | 0.00015113
6 | 0.99811 | -0.013283 | 0.0023509 | 0.00058918
7 | 0.97103 | -0.20523 | 0.003077 | 0.00077117
8 | 0.97087 | -0.20639 | 0 | 0
9 | 0.97772 | -0.15698 | 0.00023875 | 5.9835e-05
10 | 0.99713 | -0.020103 | 0.000457 | 0.00011454
11 | 0.99714 | -0.020076 | 0.0026113 | 0.00065445
12 | 0.97071 | -0.20751 | 0.0012911 | 0.00032359
13 | 0.97077 | -0.20707 | 0.00074872 | 0.00018765
14 | 0.97026 | -0.21078 | 0.0015775 | 0.00039536
15 | 0.99815 | -0.012962 | 0.0024388 | 0.00061122
16 | 0.97785 | -0.15808 | 0.00025417 | 6.37e-05
17 | 0.97792 | -0.15756 | 0.00046227 | 0.00011586
18 | 0.97794 | -0.15739 | 0.0004945 | 0.00012393
19 | 0.97806 | -0.15651 | 0 | 0
20 | 0.97517 | -0.17789 | 0 | 0
21 | 0.97437 | -0.18374 | 0.00026826 | 6.7233e-05
22 | 0.97522 | -0.17748 | 0.00021551 | 5.4011e-05
23 | 0.97955 | -0.14555 | 0.00019727 | 4.9439e-05
24 | 0.97706 | -0.16393 | 0.00030141 | 7.5541e-05
25 | 0.97387 | -0.18745 | 0 | 0
26 | 0.97566 | -0.17426 | 0.00030205 | 7.5701e-05
27 | 0.97341 | -0.19073 | 0.00034978 | 8.7662e-05
28 | 0.97342 | -0.19071 | 0.00024331 | 6.098e-05
29 | 0.97342 | -0.19066 | 0.0001953 | 4.8948e-05
30 | 0.97343 | -0.1906 | 0.00070682 | 0.00017715
31 | 0.97368 | -0.18879 | 0.00015447 | 3.8715e-05
32 | 0.97968 | -0.14456 | 0 | 0
33 | 0.97594 | -0.1722 | 0 | 0
34 | 0.9735 | -0.19016 | 0.00028341 | 7.103e-05
35 | 0.97346 | -0.19042 | 0 | 0
36 | 0.97679 | -0.16374 | 0.0001993 | 4.995e-05
37 | 0.97683 | -0.16341 | 0 | 0
38 | 0.98174 | -0.12935 | 0.00054553 | 0.00013672
39 | 0.97342 | -0.19076 | 0.00019664 | 4.9282e-05
40 | 0.97051 | -0.209 | 0.0021877 | 0.00054829
41 | 0.97056 | -0.20859 | 0 | 0
42 | 0.98714 | -0.090236 | 0.00092493 | 0.00023181
43 | 0.98897 | -0.077054 | 0 | 0
44 | 0.98648 | -0.094986 | 0 | 0
45 | 0.98911 | -0.076025 | 0 | 0
46 | 0.98643 | -0.095296 | 0.00094679 | 0.00023729
47 | 0.98535 | -0.10313 | 0 | 0
48 | 0.99035 | -0.067331 | 0.0012588 | 0.00031548
49 | 0.98719 | -0.089566 | 0.0027694 | 0.00069408
50 | 0.97375 | -0.18557 | 0 | 0
51 | 0.97334 | -0.18851 | 0 | 0
52 | 0.97389 | -0.18452 | 0.0070768 | 0.0017736
53 | 0.97296 | -0.19123 | 0.0016919 | 0.00042403
54 | 0.98293 | -0.12062 | 0 | 0
55 | 0.98522 | -0.10407 | 0.0013413 | 0.00033616
56 | 0.99799 | -0.014075 | 0.0021217 | 0.00053176
57 | 0.99839 | -0.011283 | 0 | 0
58 | 0.99768 | -0.016297 | 0 | 0
59 | 0.99846 | -0.010817 | 0.00074467 | 0.00018663
60 | 0.99762 | -0.01665 | 0.0030136 | 0.00075527
61 | 0.99724 | -0.019331 | 0.0015882 | 0.00039803
62 | 0.99889 | -0.0077672 | 0.0018101 | 0.00045366
63 | 0.99717 | -0.019812 | 0.0029066 | 0.00072846
64 | 0.97295 | -0.19133 | 0 | 0
65 | 0.97293 | -0.1915 | 0.00061837 | 0.00015498
66 | 0.99911 | -0.0062363 | 0.00086356 | 0.00021643
67 | 1 | 0 | -0.13437 | -0.033621
68 | 0.99929 | -0.0049901 | 0.004355 | 0.0010915
69 | 0.99696 | -0.021075 | 0.014381 | 0.0036042
70 | 0.99984 | -0.0010976 | 0.00083876 | 0.00021021
71 | 0.99921 | -0.0055381 | 0.001798 | 0.00045062
72 | 0.99983 | -0.0011843 | 0.00095209 | 0.00023862
73 | 0.99956 | -0.0030852 | 0.0023129 | 0.00057966
74 | 0.99968 | -0.0022254 | 0.0021571 | 0.00054062
75 | 0.99955 | -0.0031828 | 0.00084297 | 0.00021127
76 | 0.99951 | -0.0034457 | 0.00079101 | 0.00019825
77 | 0.98205 | -0.12604 | 0.0019297 | 0.00048362
78 | 0.98216 | -0.12524 | 0.002784 | 0.00069773
79 | 0.982 | -0.1264 | 0.0025081 | 0.00062858
80 | 0.98229 | -0.12432 | 0.0028839 | 0.00072277
81 | 0.98238 | -0.1237 | 0.0037593 | 0.00094216
82 | 0.98244 | -0.12327 | 0.0015206 | 0.00038109
83 | 0.98239 | -0.12362 | 0.001513 | 0.0003792
84 | 0.98321 | -0.11777 | 0 | 0
85 | 0.98043 | -0.13759 | 0.00045787 | 0.00011475
86 | 0.9826 | -0.12211 | 0.0031321 | 0.00078498
87 | 0.98346 | -0.11599 | 0.0048282 | 0.0012101
88 | 0.9787 | -0.14998 | 0 | 0
89 | 0.98482 | -0.10634 | 0.0058494 | 0.001466
90 | 0.98292 | -0.12071 | 0.0017208 | 0.00043128
91 | 0.98284 | -0.12127 | 0.0018476 | 0.00046306
92 | 0.97838 | -0.15226 | 0.00044885 | 0.00011249
93 | 0.97794 | -0.15538 | 0.00018583 | 4.6573e-05
94 | 0.98598 | -0.098166 | 0.0027845 | 0.00069786
95 | 0.99904 | -0.0067007 | 0.0027223 | 0.00068228
96 | 0.98241 | -0.12448 | 0.00043697 | 0.00010951
97 | 0.97688 | -0.163 | 0.0011013 | 0.00027601
98 | 0.97494 | -0.17697 | 0.00063508 | 0.00015917
99 | 0.97555 | -0.17254 | 0.00076815 | 0.00019252
100 | 0.97444 | -0.18053 | 0 | 0
101 | 0.97613 | -0.16839 | 0.0042082 | 0.0010547
102 | 0.97434 | -0.18129 | 0.00057978 | 0.00014531
103 | 0.99716 | -0.019942 | 0.0015945 | 0.00039963
104 | 0.97333 | -0.19142 | 0.00014816 | 3.7133e-05
105 | 0.97332 | -0.19147 | 0.00049463 | 0.00012397
106 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0089036 | -0.0022276 | 0.0089263 | 0.0022339 | 2.273e-05 | 6.2937e-06 | 0.013613 | 0.013612 | 0.013613 | 0.97311 | -0.19014 | 0.97568 | -0.17167 | 5.042
1 | 0.0089036 | 0.0022276 | -0.0088858 | -0.0022227 | 1.7756e-05 | 4.9257e-06 | 0.013613 | 0.013614 | 0.013614 | 0.97311 | -0.19014 | 0.97111 | -0.20461 | 5.0422
2 | -0.0089263 | -0.0022339 | 0.0089287 | 0.0022346 | 2.3599e-06 | 6.5269e-07 | 0.013612 | 0.013612 | 0.013612 | 0.97568 | -0.17167 | 0.97594 | -0.16975 | 5.0416
3 | 0.0030773 | 0.00077104 | -0.003077 | -0.00077117 | 2.6157e-07 | -1.3264e-07 | 0.0047152 | 0.0047153 | 0.0047153 | 0.97111 | -0.20461 | 0.97103 | -0.20523 | 1.7464
4 | 0.0058085 | 0.0014517 | -0.0058071 | -0.0014515 | 1.4185e-06 | 1.9051e-07 | 0.0088988 | 0.0088989 | 0.0088989 | 0.97111 | -0.20461 | 0.97087 | -0.20639 | 3.2959
5 | -0.0089287 | -0.0022346 | 0.0089444 | 0.0022389 | 1.5762e-05 | 4.3556e-06 | 0.013612 | 0.013612 | 0.013612 | 0.97594 | -0.16975 | 0.97772 | -0.15698 | 5.0416
6 | 0.00060304 | 0.00015085 | -0.00060303 | -0.00015113 | 1.1152e-08 | -2.846e-07 | 0.00089903 | 0.00089913 | 0.00089913 | 0.998 | -0.014003 | 0.99799 | -0.014137 | 0.33301
7 | -0.00060304 | -0.00015085 | 0.0006031 | 0.00014934 | 5.9281e-08 | -1.5141e-06 | 0.00089903 | 0.00089849 | 0.00089903 | 0.998 | -0.014003 | 0.99811 | -0.013283 | 0.33297
8 | -0.002954 | -0.00073851 | 0.0029541 | 0.00073842 | 1.3079e-07 | -9.0994e-08 | 0.0044032 | 0.0044032 | 0.0044032 | 0.99811 | -0.013283 | 0.99815 | -0.012962 | 1.6308
9 | 0.0036186 | 0.00090427 | -0.0036183 | -0.00090436 | 3.4101e-07 | -8.8596e-08 | 0.0055452 | 0.0055452 | 0.0055452 | 0.97087 | -0.20639 | 0.97077 | -0.20707 | 2.0538
10 | 0.0021885 | 0.00054721 | -0.0021878 | -0.00054812 | 6.6558e-07 | -9.1616e-07 | 0.0033538 | 0.0033542 | 0.0033542 | 0.97087 | -0.20639 | 0.97056 | -0.20859 | 1.2423
11 | -0.0091832 | -0.0022988 | 0.0091891 | 0.0023005 | 5.9851e-06 | 1.6856e-06 | 0.013975 | 0.013975 | 0.013975 | 0.97772 | -0.15698 | 0.97838 | -0.15226 | 5.176
12 | -0.000457 | -0.00011454 | 0.000457 | 0.00011446 | 1.7076e-09 | -7.6096e-08 | 0.00068198 | 0.00068195 | 0.00068198 | 0.99713 | -0.020103 | 0.99714 | -0.020076 | 0.25259
13 | -0.0030683 | -0.00076891 | 0.0030683 | 0.00076887 | 5.6919e-08 | -3.4864e-08 | 0.0045787 | 0.0045787 | 0.0045787 | 0.99714 | -0.020076 | 0.99716 | -0.019942 | 1.6958
14 | -0.0028694 | -0.00071682 | 0.0028695 | 0.00071671 | 1.7333e-07 | -1.1091e-07 | 0.0043976 | 0.0043976 | 0.0043976 | 0.97071 | -0.20751 | 0.97077 | -0.20707 | 1.6288
15 | 0.0015782 | 0.00039323 | -0.0015775 | -0.00039536 | 7.1075e-07 | -2.1321e-06 | 0.0024184 | 0.0024193 | 0.0024193 | 0.97071 | -0.20751 | 0.97026 | -0.21078 | 0.89604
16 | -0.0053929 | -0.0013496 | 0.0053941 | 0.0013497 | 1.2494e-06 | 7.5461e-08 | 0.0080389 | 0.0080388 | 0.0080389 | 0.99815 | -0.012962 | 0.99839 | -0.011283 | 2.9774
17 | -0.00025417 | -6.37e-05 | 0.00025418 | 6.1342e-05 | 1.7556e-08 | -2.3579e-06 | 0.00038677 | 0.00038594 | 0.00038677 | 0.97785 | -0.15808 | 0.97792 | -0.15756 | 0.14325
18 | -0.00071645 | -0.0001772 | 0.00071647 | 0.00017691 | 1.7292e-08 | -2.8638e-07 | 0.0010893 | 0.0010892 | 0.0010893 | 0.97792 | -0.15756 | 0.97794 | -0.15739 | 0.40345
19 | -0.001211 | -0.00030085 | 0.0012111 | 0.00030005 | 1.4414e-07 | -7.9934e-07 | 0.0018416 | 0.0018413 | 0.0018416 | 0.97794 | -0.15739 | 0.97806 | -0.15651 | 0.68209
20 | -0.0050863 | -0.0012551 | 0.0050938 | 0.0012554 | 7.4814e-06 | 3.5601e-07 | 0.0077313 | 0.0077304 | 0.0077313 | 0.97806 | -0.15651 | 0.97955 | -0.14555 | 2.8634
21 | 0.0038752 | 0.00095505 | -0.0038713 | -0.0009558 | 3.8557e-06 | -7.4979e-07 | 0.0058899 | 0.0058907 | 0.0058907 | 0.97806 | -0.15651 | 0.97706 | -0.16393 | 2.1817
22 | 0.0030458 | 0.00075269 | -0.0030434 | -0.000754 | 2.4056e-06 | -1.3028e-06 | 0.0046438 | 0.0046446 | 0.0046446 | 0.97517 | -0.17789 | 0.97437 | -0.18374 | 1.7202
23 | -0.0030458 | -0.00075269 | 0.003046 | 0.0007526 | 1.6839e-07 | -9.1361e-08 | 0.0046438 | 0.0046438 | 0.0046438 | 0.97517 | -0.17789 | 0.97522 | -0.17748 | 1.7199
24 | 0.0027752 | 0.00068676 | -0.0027738 | -0.00068778 | 1.3916e-06 | -1.0126e-06 | 0.004235 | 0.0042355 | 0.0042355 | 0.97437 | -0.18374 | 0.97387 | -0.18745 | 1.5687
25 | -0.0032615 | -0.00080661 | 0.0032629 | 0.00080601 | 1.414e-06 | -6.0019e-07 | 0.0049726 | 0.0049722 | 0.0049726 | 0.97522 | -0.17748 | 0.97566 | -0.17426 | 1.8417
26 | -0.0052911 | -0.0013049 | 0.0052918 | 0.0013049 | 7.0388e-07 | 5.0479e-08 | 0.00803 | 0.00803 | 0.00803 | 0.97955 | -0.14555 | 0.97968 | -0.14456 | 2.9741
27 | 0.0035699 | 0.00088025 | -0.003566 | -0.00088142 | 3.9698e-06 | -1.1702e-06 | 0.0054317 | 0.0054326 | 0.0054326 | 0.97706 | -0.16393 | 0.97594 | -0.1722 | 2.0121
28 | 0.0011234 | 0.00027668 | -0.001123 | -0.00027932 | 4.1221e-07 | -2.6342e-06 | 0.0017147 | 0.0017157 | 0.0017157 | 0.97387 | -0.18745 | 0.9735 | -0.19016 | 0.63545
29 | 0.0016504 | 0.00041109 | -0.0016501 | -0.00041193 | 3.0421e-07 | -8.3729e-07 | 0.0025208 | 0.0025211 | 0.0025211 | 0.97387 | -0.18745 | 0.97368 | -0.18879 | 0.93375
30 | -0.003565 | -0.00088171 | 0.003566 | 0.00088142 | 9.9003e-07 | -2.9073e-07 | 0.0054329 | 0.0054326 | 0.0054329 | 0.97566 | -0.17426 | 0.97594 | -0.1722 | 2.0122
31 | -0.00034978 | -8.7662e-05 | 0.00034978 | 8.7597e-05 | 9.4013e-10 | -6.5152e-08 | 0.00053469 | 0.00053467 | 0.00053469 | 0.97341 | -0.19073 | 0.97342 | -0.19071 | 0.19803
32 | -0.00059309 | -0.00014858 | 0.00059309 | 0.0001485 | 3.4266e-09 | -8.1738e-08 | 0.00090661 | 0.00090658 | 0.00090661 | 0.97342 | -0.19071 | 0.97342 | -0.19066 | 0.33578
33 | -0.0007884 | -0.00019744 | 0.00078841 | 0.00019734 | 7.5239e-09 | -1.0032e-07 | 0.0012051 | 0.0012051 | 0.0012051 | 0.97342 | -0.19066 | 0.97343 | -0.1906 | 0.44634
34 | -0.0014952 | -0.00037449 | 0.0014956 | 0.00037321 | 3.7145e-07 | -1.2744e-06 | 0.0022856 | 0.002285 | 0.0022856 | 0.97343 | -0.1906 | 0.97368 | -0.18879 | 0.8465
35 | -0.0052918 | -0.0013049 | 0.0053026 | 0.0013057 | 1.0792e-05 | 7.6583e-07 | 0.00803 | 0.0080288 | 0.00803 | 0.97968 | -0.14456 | 0.98174 | -0.12935 | 2.9741
36 | 0.00083956 | 0.00020829 | -0.00083953 | -0.00020864 | 2.973e-08 | -3.4864e-07 | 0.0012825 | 0.0012827 | 0.0012827 | 0.9735 | -0.19016 | 0.97346 | -0.19042 | 0.47506
37 | 0.00083953 | 0.00020864 | -0.00083949 | -0.00020908 | 3.804e-08 | -4.4596e-07 | 0.0012827 | 0.0012828 | 0.0012828 | 0.97346 | -0.19042 | 0.97342 | -0.19076 | 0.47512
38 | -0.0001993 | -4.995e-05 | 0.00019931 | 4.8054e-05 | 8.7073e-09 | -1.8958e-06 | 0.00030361 | 0.00030294 | 0.00030361 | 0.97679 | -0.16374 | 0.97683 | -0.16341 | 0.11245
39 | -0.00019931 | -4.8054e-05 | 0.00019932 | 4.5832e-05 | 1.0158e-08 | -2.2224e-06 | 0.00030294 | 0.00030219 | 0.00030294 | 0.97683 | -0.16341 | 0.97688 | -0.163 | 0.1122
40 | -0.0058481 | -0.0014424 | 0.0058519 | 0.0014429 | 3.8267e-06 | 4.823e-07 | 0.0088556 | 0.0088553 | 0.0088556 | 0.98174 | -0.12935 | 0.98241 | -0.12448 | 3.2799
41 | 0.00064285 | 0.0001598 | -0.0006428 | -0.00016098 | 5.8236e-08 | -1.1795e-06 | 0.00098223 | 0.00098266 | 0.00098266 | 0.97342 | -0.19076 | 0.97333 | -0.19142 | 0.36395
42 | -0.0021877 | -0.00054829 | 0.0021878 | 0.00054812 | 1.2336e-07 | -1.6969e-07 | 0.0033543 | 0.0033542 | 0.0033543 | 0.97051 | -0.209 | 0.97056 | -0.20859 | 1.2423
43 | -0.013118 | -0.0032647 | 0.013141 | 0.0032726 | 2.3646e-05 | 7.8525e-06 | 0.019766 | 0.019765 | 0.019766 | 0.98714 | -0.090236 | 0.98897 | -0.077054 | 7.3207
44 | 0.012193 | 0.0030329 | -0.012185 | -0.0030304 | 7.8967e-06 | 2.5582e-06 | 0.018372 | 0.018372 | 0.018372 | 0.98714 | -0.090236 | 0.98648 | -0.094986 | 6.8044
45 | -0.013141 | -0.0032726 | 0.013143 | 0.0032732 | 1.8478e-06 | 6.1343e-07 | 0.019765 | 0.019765 | 0.019765 | 0.98897 | -0.077054 | 0.98911 | -0.076025 | 7.3205
46 | 0.00094683 | 0.0002369 | -0.00094679 | -0.00023729 | 4.0632e-08 | -3.9195e-07 | 0.0014281 | 0.0014282 | 0.0014282 | 0.98648 | -0.094986 | 0.98643 | -0.095296 | 0.52897
47 | 0.011238 | 0.0027935 | -0.011226 | -0.0027896 | 1.2461e-05 | 3.9057e-06 | 0.016944 | 0.016944 | 0.016944 | 0.98648 | -0.094986 | 0.98535 | -0.10313 | 6.2756
48 | -0.077117 | -0.01936 | 0.07721 | 0.019395 | 9.3238e-05 | 3.529e-05 | 0.11603 | 0.11603 | 0.11603 | 0.98911 | -0.076025 | 0.99035 | -0.067331 | 21.4862
49 | 0.063974 | 0.016086 | -0.063853 | -0.016041 | 0.00012049 | 4.5275e-05 | 0.09626 | 0.096261 | 0.096261 | 0.98911 | -0.076025 | 0.98719 | -0.089566 | 17.826
50 | 0.0098843 | 0.0024542 | -0.0098608 | -0.0024473 | 2.3462e-05 | 6.8774e-06 | 0.014918 | 0.014919 | 0.014919 | 0.98535 | -0.10313 | 0.98293 | -0.12062 | 5.5256
51 | 0.0013415 | 0.00033537 | -0.0013413 | -0.00033616 | 1.7373e-07 | -7.9732e-07 | 0.0020255 | 0.0020258 | 0.0020258 | 0.98535 | -0.10313 | 0.98522 | -0.10407 | 0.75031
52 | -0.078469 | -0.01971 | 0.078977 | 0.019903 | 0.00050803 | 0.00019236 | 0.11792 | 0.11792 | 0.11792 | 0.99035 | -0.067331 | 0.99696 | -0.021075 | 21.8364
53 | 0.061084 | 0.015347 | -0.061011 | -0.01532 | 7.2995e-05 | 2.737e-05 | 0.092086 | 0.092086 | 0.092086 | 0.98719 | -0.089566 | 0.98598 | -0.098166 | 17.0531
54 | 0.0023121 | 0.00057631 | -0.0023111 | -0.00057744 | 9.313e-07 | -1.1291e-06 | 0.003532 | 0.0035326 | 0.0035326 | 0.97375 | -0.18557 | 0.97334 | -0.18851 | 1.3084
55 | -0.0023121 | -0.00057631 | 0.0023124 | 0.00057591 | 3.3324e-07 | -4.0444e-07 | 0.003532 | 0.0035319 | 0.003532 | 0.97375 | -0.18557 | 0.97389 | -0.18452 | 1.3082
56 | 0.0023111 | 0.00057744 | -0.0023103 | -0.00057849 | 8.6761e-07 | -1.0504e-06 | 0.0035326 | 0.0035331 | 0.0035331 | 0.97334 | -0.18851 | 0.97296 | -0.19123 | 1.3085
57 | -0.0093893 | -0.0023495 | 0.0093934 | 0.0023507 | 4.1805e-06 | 1.2026e-06 | 0.014345 | 0.014344 | 0.014345 | 0.97389 | -0.18452 | 0.97434 | -0.18129 | 5.3128
58 | 0.00061839 | 0.00015446 | -0.00061838 | -0.00015465 | 8.41e-09 | -1.8396e-07 | 0.00094556 | 0.00094562 | 0.00094562 | 0.97296 | -0.19123 | 0.97295 | -0.19133 | 0.35023
59 | 0.0017208 | 0.00043122 | -0.0017208 | -0.00043128 | 2.0832e-08 | -5.4341e-08 | 0.0026051 | 0.0026051 | 0.0026051 | 0.98293 | -0.12062 | 0.98292 | -0.12071 | 0.96485
60 | 0.00814 | 0.0020161 | -0.0081392 | -0.0020159 | 7.1615e-07 | 1.7952e-07 | 0.012314 | 0.012314 | 0.012314 | 0.98293 | -0.12062 | 0.98284 | -0.12127 | 4.5608
61 | -0.014301 | -0.0035843 | 0.014307 | 0.0035862 | 5.5292e-06 | 1.8719e-06 | 0.021323 | 0.021323 | 0.021323 | 0.99799 | -0.014075 | 0.99839 | -0.011283 | 7.8975
62 | 0.01218 | 0.0030525 | -0.012176 | -0.0030513 | 3.7457e-06 | 1.2029e-06 | 0.01816 | 0.01816 | 0.01816 | 0.99799 | -0.014075 | 0.99768 | -0.016297 | 6.7259
63 | -0.019701 | -0.0049359 | 0.019702 | 0.0049363 | 1.2696e-06 | 4.5745e-07 | 0.029362 | 0.029362 | 0.029362 | 0.99839 | -0.011283 | 0.99846 | -0.010817 | 10.8748
64 | 0.0030137 | 0.00075518 | -0.0030136 | -0.00075527 | 1.4744e-07 | -9.6001e-08 | 0.0044949 | 0.0044949 | 0.0044949 | 0.99768 | -0.016297 | 0.99762 | -0.01665 | 1.6648
65 | 0.0091621 | 0.0022961 | -0.0091582 | -0.0022951 | 3.8466e-06 | 1.0486e-06 | 0.013665 | 0.013665 | 0.013665 | 0.99768 | -0.016297 | 0.99724 | -0.019331 | 5.0612
66 | -0.020447 | -0.005123 | 0.020456 | 0.0051261 | 8.6324e-06 | 3.1252e-06 | 0.030472 | 0.030472 | 0.030472 | 0.99846 | -0.010817 | 0.99889 | -0.0077672 | 11.2859
67 | 0.00757 | 0.0018971 | -0.0075695 | -0.001897 | 5.0409e-07 | 1.1128e-07 | 0.011295 | 0.011295 | 0.011295 | 0.99724 | -0.019331 | 0.99717 | -0.019812 | 4.1835
68 | -0.022266 | -0.0055798 | 0.02227 | 0.0055815 | 4.719e-06 | 1.725e-06 | 0.033168 | 0.033168 | 0.033168 | 0.99889 | -0.0077672 | 0.99911 | -0.0062363 | 12.2845
69 | 0.0046629 | 0.0011685 | -0.0046629 | -0.0011685 | 8.4353e-08 | -3.9793e-09 | 0.0069581 | 0.0069582 | 0.0069582 | 0.99717 | -0.019812 | 0.99716 | -0.019942 | 2.5771
70 | 0.00061838 | 0.00015465 | -0.00061837 | -0.00015498 | 1.5124e-08 | -3.3075e-07 | 0.00094562 | 0.00094574 | 0.00094574 | 0.97295 | -0.19133 | 0.97293 | -0.1915 | 0.35028
71 | -0.023134 | -0.0057979 | 0.023154 | 0.0058052 | 1.9989e-05 | 7.3343e-06 | 0.034454 | 0.034454 | 0.034454 | 0.99911 | -0.0062363 | 1 | 0 | 12.7609
72 | 0.0088822 | 0.0022256 | -0.0088761 | -0.0022239 | 6.1307e-06 | 1.6206e-06 | 0.013217 | 0.013217 | 0.013217 | 1 | 0 | 0.99929 | -0.0049901 | 4.8952
73 | 0.093634 | 0.023612 | -0.093358 | -0.023507 | 0.00027575 | 0.00010487 | 0.13938 | 0.13938 | 0.13938 | 1 | 0 | 0.99696 | -0.021075 | 25.8111
74 | 0.0078975 | 0.0019784 | -0.0078963 | -0.0019782 | 1.1989e-06 | 2.7862e-07 | 0.011751 | 0.011751 | 0.011751 | 1 | 0 | 0.99984 | -0.0010976 | 4.3523
75 | 0.0045211 | 0.0011325 | -0.0045208 | -0.0011325 | 3.4266e-07 | -2.693e-08 | 0.0067321 | 0.0067321 | 0.0067321 | 0.99929 | -0.0049901 | 0.99921 | -0.0055381 | 2.4934
76 | 0.0070575 | 0.0017679 | -0.0070574 | -0.0017679 | 8.4588e-08 | 1.6418e-08 | 0.010503 | 0.010503 | 0.010503 | 0.99984 | -0.0010976 | 0.99983 | -0.0011843 | 3.89
77 | 0.0027228 | 0.00068189 | -0.0027223 | -0.00068228 | 4.3787e-07 | -3.9057e-07 | 0.0040546 | 0.0040548 | 0.0040548 | 0.99921 | -0.0055381 | 0.99904 | -0.0067007 | 1.5018
78 | 0.0061053 | 0.0015293 | -0.0061045 | -0.0015292 | 8.7905e-07 | 1.1434e-07 | 0.0090861 | 0.0090862 | 0.0090862 | 0.99983 | -0.0011843 | 0.99968 | -0.0022254 | 3.3652
79 | -0.0039469 | -0.00098868 | 0.0039474 | 0.00098857 | 4.6921e-07 | -1.0509e-07 | 0.0058754 | 0.0058753 | 0.0058754 | 0.99956 | -0.0030852 | 0.99968 | -0.0022254 | 2.1761
80 | 0.001634 | 0.00040902 | -0.001634 | -0.00040909 | 2.2034e-08 | -6.9754e-08 | 0.0024324 | 0.0024324 | 0.0024324 | 0.99956 | -0.0030852 | 0.99955 | -0.0031828 | 0.90088
81 | 0.00079104 | 0.00019782 | -0.00079101 | -0.00019825 | 2.8722e-08 | -4.2405e-07 | 0.0011775 | 0.0011776 | 0.0011776 | 0.99955 | -0.0031828 | 0.99951 | -0.0034457 | 0.43615
82 | -0.0044378 | -0.0011121 | 0.0044383 | 0.001112 | 4.866e-07 | -3.1087e-08 | 0.0067242 | 0.0067241 | 0.0067242 | 0.98205 | -0.12604 | 0.98216 | -0.12524 | 2.4905
83 | 0.0025082 | 0.00062845 | -0.0025081 | -0.00062858 | 1.2582e-07 | -1.2823e-07 | 0.0038004 | 0.0038004 | 0.0038004 | 0.98205 | -0.12604 | 0.982 | -0.1264 | 1.4076
84 | -0.0072223 | -0.0018098 | 0.0072232 | 0.00181 | 9.2573e-07 | 1.9922e-07 | 0.010942 | 0.010942 | 0.010942 | 0.98216 | -0.12524 | 0.98229 | -0.12432 | 4.0526
85 | -0.010107 | -0.0025327 | 0.010108 | 0.002533 | 8.5898e-07 | 2.5603e-07 | 0.015311 | 0.015311 | 0.015311 | 0.98229 | -0.12432 | 0.98238 | -0.1237 | 5.6706
86 | -0.013867 | -0.0034752 | 0.01387 | 0.0034762 | 3.0579e-06 | 1.0354e-06 | 0.021005 | 0.021005 | 0.021005 | 0.98238 | -0.1237 | 0.9826 | -0.12211 | 7.7795
87 | 0.028844 | 0.0072367 | -0.028843 | -0.0072362 | 1.3969e-06 | 5.2243e-07 | 0.043691 | 0.043691 | 0.043691 | 0.98244 | -0.12327 | 0.98239 | -0.12362 | 16.1818
88 | -0.030365 | -0.0076178 | 0.030388 | 0.0076258 | 2.3169e-05 | 8.0215e-06 | 0.045994 | 0.045994 | 0.045994 | 0.98244 | -0.12327 | 0.98321 | -0.11777 | 8.5174
89 | 0.02733 | 0.006857 | -0.027277 | -0.0068373 | 5.2886e-05 | 1.9716e-05 | 0.041399 | 0.041399 | 0.041399 | 0.98239 | -0.12362 | 0.98043 | -0.13759 | 15.3331
90 | 0.017013 | 0.0042648 | -0.017002 | -0.0042612 | 1.0224e-05 | 3.6191e-06 | 0.025748 | 0.025748 | 0.025748 | 0.98321 | -0.11777 | 0.9826 | -0.12211 | 9.5362
91 | -0.047401 | -0.011891 | 0.047413 | 0.011895 | 1.173e-05 | 4.3263e-06 | 0.071741 | 0.071741 | 0.071741 | 0.98321 | -0.11777 | 0.98346 | -0.11599 | 13.2854
92 | 0.026819 | 0.0067225 | -0.026773 | -0.0067054 | 4.5937e-05 | 1.7109e-05 | 0.040705 | 0.040705 | 0.040705 | 0.98043 | -0.13759 | 0.9787 | -0.14998 | 15.0758
93 | -0.052241 | -0.013105 | 0.052311 | 0.013131 | 6.9977e-05 | 2.6002e-05 | 0.079047 | 0.079046 | 0.079047 | 0.98346 | -0.11599 | 0.98482 | -0.10634 | 14.6383
94 | 0.009641 | 0.0024138 | -0.009638 | -0.0024129 | 3.0353e-06 | 8.8299e-07 | 0.014657 | 0.014658 | 0.014658 | 0.9787 | -0.14998 | 0.97838 | -0.15226 | 5.4287
95 | 0.017132 | 0.0042916 | -0.01712 | -0.0042871 | 1.2779e-05 | 4.5361e-06 | 0.026047 | 0.026047 | 0.026047 | 0.9787 | -0.14998 | 0.97794 | -0.15538 | 9.6472
96 | -0.05816 | -0.014597 | 0.058226 | 0.014622 | 6.6085e-05 | 2.4719e-05 | 0.087884 | 0.087884 | 0.087884 | 0.98482 | -0.10634 | 0.98598 | -0.098166 | 16.2749
97 | 0.0062916 | 0.0015529 | -0.0062889 | -0.0015524 | 2.7077e-06 | 4.3455e-07 | 0.0095169 | 0.0095171 | 0.0095171 | 0.98284 | -0.12127 | 0.98241 | -0.12448 | 3.5249
98 | 0.016934 | 0.0042405 | -0.016916 | -0.0042342 | 1.7818e-05 | 6.3139e-06 | 0.025765 | 0.025765 | 0.025765 | 0.97794 | -0.15538 | 0.97688 | -0.163 | 9.5425
99 | 0.015615 | 0.0039123 | -0.015604 | -0.0039083 | 1.165e-05 | 4.0681e-06 | 0.023785 | 0.023785 | 0.023785 | 0.97688 | -0.163 | 0.97613 | -0.16839 | 8.8094
100 | -0.010614 | -0.002657 | 0.010621 | 0.002659 | 6.4973e-06 | 2.0038e-06 | 0.016199 | 0.016199 | 0.016199 | 0.97494 | -0.17697 | 0.97555 | -0.17254 | 5.9996
101 | 0.0099792 | 0.0024978 | -0.0099743 | -0.0024964 | 4.8986e-06 | 1.4622e-06 | 0.01523 | 0.01523 | 0.01523 | 0.97494 | -0.17697 | 0.97444 | -0.18053 | 5.6407
102 | -0.011389 | -0.0028515 | 0.011395 | 0.0028536 | 6.5253e-06 | 2.0767e-06 | 0.017371 | 0.01737 | 0.017371 | 0.97555 | -0.17254 | 0.97613 | -0.16839 | 6.4335
103 | 0.0099743 | 0.0024964 | -0.0099732 | -0.002496 | 1.0552e-06 | 3.1503e-07 | 0.01523 | 0.01523 | 0.01523 | 0.97444 | -0.18053 | 0.97434 | -0.18129 | 5.6407
104 | 0.00049463 | 0.00012385 | -0.00049463 | -0.00012397 | 3.4505e-09 | -1.1887e-07 | 0.00075615 | 0.00075619 | 0.00075619 | 0.97333 | -0.19142 | 0.97332 | -0.19147 | 0.28007

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.13437 | 0.033621

## res_load
| p_mw | q_mvar
0 | 0.00060303 | 0.00015113
1 | 0.0023509 | 0.00058918
2 | 0.003077 | 0.00077117
3 | 0.00023875 | 5.9835e-05
4 | 0.000457 | 0.00011454
5 | 0.0026113 | 0.00065445
6 | 0.0012911 | 0.00032359
7 | 0.00074872 | 0.00018765
8 | 0.0015775 | 0.00039536
9 | 0.0024388 | 0.00061122
10 | 0.00025417 | 6.37e-05
11 | 0.00046227 | 0.00011586
12 | 0.0004945 | 0.00012393
13 | 0.00026826 | 6.7233e-05
14 | 0.00021551 | 5.4011e-05
15 | 0.00019727 | 4.9439e-05
16 | 0.00030141 | 7.5541e-05
17 | 0.00030205 | 7.5701e-05
18 | 0.00034978 | 8.7662e-05
19 | 0.00024331 | 6.098e-05
20 | 0.0001953 | 4.8948e-05
21 | 0.00070682 | 0.00017715
22 | 0.00015447 | 3.8715e-05
23 | 0.00028341 | 7.103e-05
24 | 0.0001993 | 4.995e-05
25 | 0.00054553 | 0.00013672
26 | 0.00019664 | 4.9282e-05
27 | 0.0021877 | 0.00054829
28 | 0.00092493 | 0.00023181
29 | 0.00094679 | 0.00023729
30 | 0.0012588 | 0.00031548
31 | 0.0027694 | 0.00069408
32 | 0.0070768 | 0.0017736
33 | 0.0016919 | 0.00042403
34 | 0.0013413 | 0.00033616
35 | 0.0021217 | 0.00053176
36 | 0.00074467 | 0.00018663
37 | 0.0030136 | 0.00075527
38 | 0.0015882 | 0.00039803
39 | 0.0018101 | 0.00045366
40 | 0.0029066 | 0.00072846
41 | 0.00061837 | 0.00015498
42 | 0.00086356 | 0.00021643
43 | 0.004355 | 0.0010915
44 | 0.014381 | 0.0036042
45 | 0.00083876 | 0.00021021
46 | 0.001798 | 0.00045062
47 | 0.00095209 | 0.00023862
48 | 0.0023129 | 0.00057966
49 | 0.0021571 | 0.00054062
50 | 0.00084297 | 0.00021127
51 | 0.00079101 | 0.00019825
52 | 0.0019297 | 0.00048362
53 | 0.002784 | 0.00069773
54 | 0.0025081 | 0.00062858
55 | 0.0028839 | 0.00072277
56 | 0.0037593 | 0.00094216
57 | 0.0015206 | 0.00038109
58 | 0.001513 | 0.0003792
59 | 0.00045787 | 0.00011475
60 | 0.0031321 | 0.00078498
61 | 0.0048282 | 0.0012101
62 | 0.0058494 | 0.001466
63 | 0.0017208 | 0.00043128
64 | 0.0018476 | 0.00046306
65 | 0.00044885 | 0.00011249
66 | 0.00018583 | 4.6573e-05
67 | 0.0027845 | 0.00069786
68 | 0.0027223 | 0.00068228
69 | 0.00043697 | 0.00010951
70 | 0.0011013 | 0.00027601
71 | 0.00063508 | 0.00015917
72 | 0.00076815 | 0.00019252
73 | 0.0042082 | 0.0010547
74 | 0.00057978 | 0.00014531
75 | 0.0015945 | 0.00039963
76 | 0.00014816 | 3.7133e-05
77 | 0.00049463 | 0.00012397

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1