## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1311-8_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1311-8_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1311-8_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1311-8_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1311-8_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1311-8_0_3_node_32 | 0.4 | n |  | TRUE
6 | bus_LV_1311-8_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1311-8_0_3_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_1311-8_0_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_1311-8_0_3_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_1311-8_0_3_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1311-8_0_3_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1311-8_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1311-8_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1311-8_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1311-8_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1311-8_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1311-8_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1311-8_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1311-8_0_3_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1311-8_0_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1311-8_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1311-8_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1311-8_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1311-8_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1311-8_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1311-8_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1311-8_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1311-8_0_3_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1311-8_0_3_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1311-8_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1311-8_0_3_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1311-8_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_MV_127_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1311-8_0_3_load_0 | 0 | 0.02254 | 0.0056491 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1311-8_0_3_load_1 | 1 | 0.001766 | 0.00044261 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1311-8_0_3_load_2 | 2 | 0.0041965 | 0.0010518 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1311-8_0_3_load_3 | 3 | 0.0033039 | 0.00082803 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1311-8_0_3_load_5 | 4 | 0.0025754 | 0.00064546 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1311-8_0_3_load_32 | 5 | 0.0011869 | 0.00029746 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1311-8_0_3_load_34 | 7 | 0.0037302 | 0.00093488 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1311-8_0_3_load_30 | 10 | 0.0050527 | 0.0012663 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1311-8_0_3_load_33 | 11 | 0.0026063 | 0.0006532 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1311-8_0_3_load_7 | 12 | 0.0074473 | 0.0018665 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1311-8_0_3_load_8 | 13 | 0.00331 | 0.00082957 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1311-8_0_3_load_9 | 14 | 0.0041586 | 0.0010422 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1311-8_0_3_load_10 | 15 | 0.018176 | 0.0045553 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1311-8_0_3_load_11 | 16 | 0.011479 | 0.002877 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1311-8_0_3_load_12 | 17 | 0.0028778 | 0.00072125 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1311-8_0_3_load_13 | 18 | 0.0092008 | 0.0023059 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1311-8_0_3_load_26 | 19 | 0.0048699 | 0.0012205 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1311-8_0_3_load_22 | 20 | 0.0074244 | 0.0018607 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1311-8_0_3_load_17 | 21 | 0.0068944 | 0.0017279 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1311-8_0_3_load_14 | 22 | 0.0069246 | 0.0017355 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1311-8_0_3_load_18 | 25 | 0.0069612 | 0.0017446 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1311-8_0_3_load_19 | 26 | 0.007832 | 0.0019629 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1311-8_0_3_load_20 | 27 | 0.010367 | 0.0025982 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1311-8_0_3_load_24 | 29 | 0.0024773 | 0.00062088 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1311-8_0_3_load_25 | 30 | 0.010751 | 0.0026944 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1311-8_0_3_load_27 | 31 | 0.01002 | 0.0025111 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1311-8_0_3_load_29 | 32 | 0.011489 | 0.0028795 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1311-8_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0057192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1311-8_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.013181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1311-8_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0065806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1311-8_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0061637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1311-8_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.016127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1311-8_0_3_line_5 | NAYY 4x150 SE | 5 | 9 | 0.006233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1311-8_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.048328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1311-8_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.085789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1311-8_0_3_line_8 | NAYY 4x150 SE | 8 | 10 | 0.016974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1311-8_0_3_line_9 | NAYY 4x150 SE | 8 | 11 | 0.014138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1311-8_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0085592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1311-8_0_3_line_11 | NAYY 4x150 SE | 9 | 29 | 0.030153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1311-8_0_3_line_12 | NAYY 4x150 SE | 10 | 32 | 0.0018256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1311-8_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0052093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1311-8_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.019069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1311-8_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0012529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1311-8_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0018531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1311-8_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0050708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1311-8_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.010298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1311-8_0_3_line_19 | NAYY 4x150 SE | 17 | 19 | 0.0033211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1311-8_0_3_line_20 | NAYY 4x150 SE | 18 | 20 | 0.00016806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1311-8_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.0047866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1311-8_0_3_line_22 | NAYY 4x150 SE | 21 | 23 | 0.022921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1311-8_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.011113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1311-8_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.059355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1311-8_0_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.0081316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1311-8_0_3_line_26 | NAYY 4x150 SE | 23 | 26 | 0.021865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1311-8_0_3_line_27 | NAYY 4x150 SE | 24 | 27 | 0.029535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1311-8_0_3_line_28 | NAYY 4x150 SE | 25 | 28 | 0.0025538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1311-8_0_3_line_29 | NAYY 4x150 SE | 26 | 29 | 0.0082925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1311-8_0_3_line_30 | NAYY 4x150 SE | 27 | 30 | 0.017076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1311-8_0_3_line_31 | NAYY 4x150 SE | 28 | 31 | 0.017349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1311-8_0_3_trafo_17 | 0.25 MVA 20/0.4 kV | 33 | 21 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2682836.1124 | 1205155.6489 | 2682836.1124 | 1205155.6489 | 2682832.9612 | 1205150.8762
1 | 2682836.1124 | 1205155.6489 | 2682838.0073 | 1205168.6926
2 | 2682832.9612 | 1205150.8762 | 2682830.8744 | 1205147.7156 | 2682828.99 | 1205145.6537
3 | 2682824.8319 | 1205141.1038 | 2682828.99 | 1205145.6537
4 | 2682824.8319 | 1205141.1038 | 2682820.9227 | 1205136.8262 | 2682818.1092 | 1205126.8842
5 | 2682816.412 | 1205120.8868 | 2682818.1092 | 1205126.8842
6 | 2682804.1403 | 1205185.1022 | 2682756.0603 | 1205191.2064
7 | 2682756.0603 | 1205191.2064 | 2682754.7385 | 1205181.1927 | 2682752.4791 | 1205159.7922 | 2682766.3539 | 1205146.1646 | 2682785.2398 | 1205131.0611 | 2682794.1874 | 1205125.4927
8 | 2682794.1874 | 1205125.4927 | 2682794.7845 | 1205111.5143 | 2682795.5409 | 1205108.6285
9 | 2682794.1874 | 1205125.4927 | 2682808.0309 | 1205122.6237
10 | 2682816.412 | 1205120.8868 | 2682808.0309 | 1205122.6237
11 | 2682816.412 | 1205120.8868 | 2682808.2027 | 1205091.8725
12 | 2682796.0038 | 1205106.8625 | 2682795.5409 | 1205108.6285
13 | 2682861.0026 | 1205037.3773 | 2682866.05 | 1205036.0889
14 | 2682861.0026 | 1205037.3773 | 2682855.7271 | 1205038.7239 | 2682843.8612 | 1205045.42
15 | 2682867.264 | 1205035.779 | 2682866.05 | 1205036.0889
16 | 2682843.8612 | 1205045.42 | 2682842.2473 | 1205046.3307 | 2682842.2473 | 1205046.3307
17 | 2682867.264 | 1205035.779 | 2682872.1772 | 1205034.5248
18 | 2682832.6804 | 1205050.1411 | 2682842.2473 | 1205046.3307
19 | 2682872.1772 | 1205034.5248 | 2682875.3951 | 1205033.7034
20 | 2682832.6804 | 1205050.1411 | 2682832.5243 | 1205050.2033
21 | 2682832.5243 | 1205050.2033 | 2682828.0774 | 1205051.9745
22 | 2682807.4843 | 1205061.9586 | 2682820.2309 | 1205055.0976 | 2682823.1761 | 1205053.9266 | 2682828.0774 | 1205051.9745
23 | 2682807.4843 | 1205061.9586 | 2682804.0304 | 1205051.3959
24 | 2682793.3164 | 1204994.1299 | 2682793.1826 | 1205000.4877 | 2682793.5554 | 1205013.1009 | 2682795.7637 | 1205019.5357 | 2682801.336 | 1205029.1524 | 2682803.2588 | 1205049.0362 | 2682804.0304 | 1205051.3959
25 | 2682807.4843 | 1205061.9586 | 2682800.3836 | 1205065.9214
26 | 2682807.4843 | 1205061.9586 | 2682806.9085 | 1205077.1381 | 2682806.6576 | 1205083.808
27 | 2682793.3164 | 1204994.1299 | 2682822.7679 | 1204996.345
28 | 2682798.1536 | 1205067.1659 | 2682800.3836 | 1205065.9214
29 | 2682808.2027 | 1205091.8725 | 2682806.5711 | 1205086.1059 | 2682806.6576 | 1205083.808
30 | 2682822.7679 | 1204996.345 | 2682829.9321 | 1204996.8838 | 2682839.7653 | 1204995.812
31 | 2682798.1536 | 1205067.1659 | 2682783.0046 | 1205075.6207

## bus_geodata
| x | y | coords
0 | 2682836.1124 | 1205155.6489
1 | 2682832.9612 | 1205150.8762
2 | 2682838.0073 | 1205168.6926
3 | 2682828.99 | 1205145.6537
4 | 2682824.8319 | 1205141.1038
5 | 2682818.1092 | 1205126.8842
6 | 2682756.0603 | 1205191.2064
7 | 2682804.1403 | 1205185.1022
8 | 2682794.1874 | 1205125.4927
9 | 2682816.412 | 1205120.8868
10 | 2682795.5409 | 1205108.6285
11 | 2682808.0309 | 1205122.6237
12 | 2682861.0026 | 1205037.3773
13 | 2682866.05 | 1205036.0889
14 | 2682843.8612 | 1205045.42
15 | 2682867.264 | 1205035.779
16 | 2682842.2473 | 1205046.3307
17 | 2682872.1772 | 1205034.5248
18 | 2682832.6804 | 1205050.1411
19 | 2682875.3951 | 1205033.7034
20 | 2682832.5243 | 1205050.2033
21 | 2682828.0774 | 1205051.9745
22 | 2682804.0304 | 1205051.3959
23 | 2682807.4843 | 1205061.9586
24 | 2682793.3164 | 1204994.1299
25 | 2682800.3836 | 1205065.9214
26 | 2682806.6576 | 1205083.808
27 | 2682822.7679 | 1204996.345
28 | 2682798.1536 | 1205067.1659
29 | 2682808.2027 | 1205091.8725
30 | 2682839.7653 | 1204995.812
31 | 2682783.0046 | 1205075.6207
32 | 2682796.0038 | 1205106.8625
33 | 2682807.4843 | 1205061.9586

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99082 | -0.064362 | 0.02254 | 0.0056491
1 | 0.99104 | -0.062808 | 0.001766 | 0.00044261
2 | 0.99074 | -0.064925 | 0.0041965 | 0.0010518
3 | 0.99131 | -0.060903 | 0.0033039 | 0.00082803
4 | 0.99159 | -0.058912 | 0.0025754 | 0.00064546
5 | 0.99239 | -0.053288 | 0.0011869 | 0.00029746
6 | 0.99156 | -0.059189 | 0 | 0
7 | 0.9913 | -0.06102 | 0.0037302 | 0.00093488
8 | 0.99202 | -0.055934 | 0 | 0
9 | 0.99271 | -0.051041 | 0 | 0
10 | 0.99161 | -0.058783 | 0.0050527 | 0.0012663
11 | 0.99243 | -0.053027 | 0.0026063 | 0.0006532
12 | 0.99764 | -0.016551 | 0.0074473 | 0.0018665
13 | 0.99742 | -0.018078 | 0.00331 | 0.00082957
14 | 0.99864 | -0.0095429 | 0.0041586 | 0.0010422
15 | 0.99737 | -0.018404 | 0.018176 | 0.0045553
16 | 0.99874 | -0.0087855 | 0.011479 | 0.002877
17 | 0.99732 | -0.018798 | 0.0028778 | 0.00072125
18 | 0.99951 | -0.0033987 | 0.0092008 | 0.0023059
19 | 0.99729 | -0.01896 | 0.0048699 | 0.0012205
20 | 0.99953 | -0.0032954 | 0.0074244 | 0.0018607
21 | 1 | 0 | -0.18434 | -0.046104
22 | 0.99768 | -0.016168 | 0.0069246 | 0.0017355
23 | 0.99813 | -0.013044 | 0 | 0
24 | 0.99589 | -0.028763 | 0 | 0
25 | 0.99793 | -0.014427 | 0.0069612 | 0.0017446
26 | 0.99597 | -0.028142 | 0.007832 | 0.0019629
27 | 0.99499 | -0.035046 | 0.010367 | 0.0025982
28 | 0.9979 | -0.014684 | 0 | 0
29 | 0.99524 | -0.033231 | 0.0024773 | 0.00062088
30 | 0.99473 | -0.036897 | 0.010751 | 0.0026944
31 | 0.99765 | -0.016426 | 0.01002 | 0.0025111
32 | 0.99158 | -0.058996 | 0.011489 | 0.0028795
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.026737 | -0.0067008 | 0.026743 | 0.0067029 | 5.7539e-06 | 2.1394e-06 | 0.040154 | 0.040153 | 0.040154 | 0.99082 | -0.064362 | 0.99104 | -0.062808 | 14.8717
1 | 0.0041969 | 0.0010517 | -0.0041965 | -0.0010518 | 3.2674e-07 | -4.4079e-08 | 0.0063028 | 0.0063029 | 0.0063029 | 0.99082 | -0.064362 | 0.99074 | -0.064925 | 2.3344
2 | -0.028509 | -0.0071455 | 0.028516 | 0.0071483 | 7.5239e-06 | 2.809e-06 | 0.042805 | 0.042805 | 0.042805 | 0.99104 | -0.062808 | 0.99131 | -0.060903 | 15.8537
3 | -0.03182 | -0.0079764 | 0.031829 | 0.0079797 | 8.7747e-06 | 3.2954e-06 | 0.047764 | 0.047764 | 0.047764 | 0.99131 | -0.060903 | 0.99159 | -0.058912 | 17.6905
4 | -0.034404 | -0.0086251 | 0.034431 | 0.0086352 | 2.6825e-05 | 1.0109e-05 | 0.051629 | 0.051629 | 0.051629 | 0.99159 | -0.058912 | 0.99239 | -0.053288 | 19.1219
5 | -0.035618 | -0.0089327 | 0.035629 | 0.0089369 | 1.1094e-05 | 4.1865e-06 | 0.053409 | 0.053409 | 0.053409 | 0.99239 | -0.053288 | 0.99271 | -0.051041 | 19.781
6 | 0.0037311 | 0.00093462 | -0.0037302 | -0.00093488 | 9.4545e-07 | -2.5957e-07 | 0.0055991 | 0.0055993 | 0.0055993 | 0.99156 | -0.059189 | 0.9913 | -0.06102 | 2.0738
7 | -0.0037311 | -0.00093462 | 0.0037328 | 0.00093415 | 1.6781e-06 | -4.6164e-07 | 0.0055991 | 0.0055987 | 0.0055991 | 0.99156 | -0.059189 | 0.99202 | -0.055934 | 2.0737
8 | 0.016549 | 0.0041482 | -0.016542 | -0.0041459 | 6.5268e-06 | 2.2912e-06 | 0.024823 | 0.024823 | 0.024823 | 0.99202 | -0.055934 | 0.99161 | -0.058783 | 9.1938
9 | -0.020282 | -0.0050823 | 0.02029 | 0.0050853 | 8.1646e-06 | 2.9576e-06 | 0.030422 | 0.030422 | 0.030422 | 0.99202 | -0.055934 | 0.99243 | -0.053027 | 11.2674
10 | 0.022902 | 0.0057408 | -0.022896 | -0.0057385 | 6.2944e-06 | 2.3103e-06 | 0.03433 | 0.03433 | 0.03433 | 0.99271 | -0.051041 | 0.99243 | -0.053027 | 12.7147
11 | -0.058531 | -0.014678 | 0.058676 | 0.014733 | 0.00014484 | 5.5318e-05 | 0.087738 | 0.087738 | 0.087738 | 0.99271 | -0.051041 | 0.99524 | -0.033231 | 32.4957
12 | 0.01149 | 0.0028796 | -0.011489 | -0.0028795 | 3.3863e-07 | 1.0669e-07 | 0.017241 | 0.017241 | 0.017241 | 0.99161 | -0.058783 | 0.99158 | -0.058996 | 6.3856
13 | 0.029241 | 0.0073295 | -0.029235 | -0.0073271 | 6.1835e-06 | 2.3103e-06 | 0.043615 | 0.043615 | 0.043615 | 0.99764 | -0.016551 | 0.99742 | -0.018078 | 16.1538
14 | -0.036689 | -0.0091959 | 0.036724 | 0.0092094 | 3.5634e-05 | 1.3456e-05 | 0.054723 | 0.054723 | 0.054723 | 0.99764 | -0.016551 | 0.99864 | -0.0095429 | 20.2678
15 | 0.025925 | 0.0064976 | -0.025924 | -0.0064971 | 1.1695e-06 | 4.3345e-07 | 0.038677 | 0.038677 | 0.038677 | 0.99742 | -0.018078 | 0.99737 | -0.018404 | 14.3248
16 | -0.040883 | -0.010252 | 0.040887 | 0.010253 | 4.2914e-06 | 1.6263e-06 | 0.06092 | 0.06092 | 0.06092 | 0.99864 | -0.0095429 | 0.99874 | -0.0087855 | 22.5628
17 | 0.0077483 | 0.0019419 | -0.0077479 | -0.0019418 | 4.2284e-07 | 9.6457e-08 | 0.01156 | 0.01156 | 0.01156 | 0.99737 | -0.018404 | 0.99732 | -0.018798 | 4.2815
18 | -0.052367 | -0.01313 | 0.052406 | 0.013145 | 3.9117e-05 | 1.491e-05 | 0.078022 | 0.078022 | 0.078022 | 0.99874 | -0.0087855 | 0.99951 | -0.0033987 | 28.8972
19 | 0.0048701 | 0.0012205 | -0.0048699 | -0.0012205 | 1.0942e-07 | -1.2527e-09 | 0.0072662 | 0.0072662 | 0.0072662 | 0.99732 | -0.018798 | 0.99729 | -0.01896 | 2.6912
20 | -0.061607 | -0.015451 | 0.061607 | 0.015451 | 8.822e-07 | 3.371e-07 | 0.09172 | 0.09172 | 0.09172 | 0.99951 | -0.0033987 | 0.99953 | -0.0032954 | 33.9704
21 | -0.069032 | -0.017312 | 0.069063 | 0.017324 | 3.1548e-05 | 1.2071e-05 | 0.10277 | 0.10277 | 0.10277 | 0.99953 | -0.0032954 | 1 | 0 | 38.064
22 | 0.11448 | 0.028779 | -0.11427 | -0.0287 | 0.0002076 | 7.9246e-05 | 0.17038 | 0.17038 | 0.17038 | 1 | 0 | 0.99813 | -0.013044 | 31.552
23 | -0.028101 | -0.0070491 | 0.028113 | 0.0070536 | 1.2182e-05 | 4.5403e-06 | 0.041913 | 0.041913 | 0.041913 | 0.99768 | -0.016168 | 0.99813 | -0.013044 | 15.5235
24 | 0.021176 | 0.0053136 | -0.021139 | -0.0053002 | 3.6951e-05 | 1.3438e-05 | 0.031586 | 0.031586 | 0.031586 | 0.99768 | -0.016168 | 0.99589 | -0.028763 | 11.6985
25 | 0.016987 | 0.0042577 | -0.016984 | -0.0042566 | 3.2541e-06 | 1.1453e-06 | 0.025324 | 0.025324 | 0.025324 | 0.99813 | -0.013044 | 0.99793 | -0.014427 | 9.3793
26 | 0.069174 | 0.017389 | -0.069029 | -0.017333 | 0.00014515 | 5.5542e-05 | 0.10314 | 0.10314 | 0.10314 | 0.99813 | -0.013044 | 0.99597 | -0.028142 | 38.2012
27 | 0.021139 | 0.0053002 | -0.021121 | -0.0052935 | 1.8387e-05 | 6.6878e-06 | 0.031586 | 0.031586 | 0.031586 | 0.99589 | -0.028763 | 0.99499 | -0.035046 | 11.6985
28 | 0.010022 | 0.0025119 | -0.010022 | -0.0025118 | 3.5589e-07 | 1.0352e-07 | 0.014944 | 0.014944 | 0.014944 | 0.99793 | -0.014427 | 0.9979 | -0.014684 | 5.5349
29 | 0.061197 | 0.01537 | -0.061154 | -0.015354 | 4.3267e-05 | 1.6533e-05 | 0.091442 | 0.091442 | 0.091442 | 0.99597 | -0.028142 | 0.99524 | -0.033231 | 33.8674
30 | 0.010754 | 0.0026952 | -0.010751 | -0.0026944 | 2.7558e-06 | 8.382e-07 | 0.016082 | 0.016082 | 0.016082 | 0.99499 | -0.035046 | 0.99473 | -0.036897 | 5.9563
31 | 0.010022 | 0.0025118 | -0.01002 | -0.0025111 | 2.4177e-06 | 7.0329e-07 | 0.014944 | 0.014944 | 0.014944 | 0.9979 | -0.014684 | 0.99765 | -0.016426 | 5.5349

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19124 | 0.047832

## res_load
| p_mw | q_mvar
0 | 0.02254 | 0.0056491
1 | 0.001766 | 0.00044261
2 | 0.0041965 | 0.0010518
3 | 0.0033039 | 0.00082803
4 | 0.0025754 | 0.00064546
5 | 0.0011869 | 0.00029746
6 | 0.0037302 | 0.00093488
7 | 0.0050527 | 0.0012663
8 | 0.0026063 | 0.0006532
9 | 0.0074473 | 0.0018665
10 | 0.00331 | 0.00082957
11 | 0.0041586 | 0.0010422
12 | 0.018176 | 0.0045553
13 | 0.011479 | 0.002877
14 | 0.0028778 | 0.00072125
15 | 0.0092008 | 0.0023059
16 | 0.0048699 | 0.0012205
17 | 0.0074244 | 0.0018607
18 | 0.0068944 | 0.0017279
19 | 0.0069246 | 0.0017355
20 | 0.0069612 | 0.0017446
21 | 0.007832 | 0.0019629
22 | 0.010367 | 0.0025982
23 | 0.0024773 | 0.00062088
24 | 0.010751 | 0.0026944
25 | 0.01002 | 0.0025111
26 | 0.011489 | 0.0028795

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1