## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1361-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1361-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1361-1_0_6_node_51 | 0.4 | n |  | TRUE
3 | bus_LV_1361-1_0_6_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1361-1_0_6_node_50 | 0.4 | n |  | TRUE
5 | bus_LV_1361-1_0_6_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_1361-1_0_6_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_1361-1_0_6_node_61 | 0.4 | n |  | TRUE
8 | bus_LV_1361-1_0_6_node_2 | 0.4 | n |  | TRUE
9 | bus_LV_1361-1_0_6_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_1361-1_0_6_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_1361-1_0_6_node_69 | 0.4 | n |  | TRUE
12 | bus_LV_1361-1_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1361-1_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1361-1_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1361-1_0_6_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1361-1_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1361-1_0_6_node_64 | 0.4 | n |  | TRUE
18 | bus_LV_1361-1_0_6_node_65 | 0.4 | n |  | TRUE
19 | bus_LV_1361-1_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1361-1_0_6_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1361-1_0_6_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1361-1_0_6_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1361-1_0_6_node_88 | 0.4 | n |  | TRUE
24 | bus_LV_1361-1_0_6_node_100 | 0.4 | n |  | TRUE
25 | bus_LV_1361-1_0_6_node_87 | 0.4 | n |  | TRUE
26 | bus_LV_1361-1_0_6_node_116 | 0.4 | n |  | TRUE
27 | bus_LV_1361-1_0_6_node_98 | 0.4 | n |  | TRUE
28 | bus_LV_1361-1_0_6_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1361-1_0_6_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1361-1_0_6_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1361-1_0_6_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1361-1_0_6_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1361-1_0_6_node_63 | 0.4 | n |  | TRUE
34 | bus_LV_1361-1_0_6_node_80 | 0.4 | n |  | TRUE
35 | bus_LV_1361-1_0_6_node_68 | 0.4 | n |  | TRUE
36 | bus_LV_1361-1_0_6_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_1361-1_0_6_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_1361-1_0_6_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_1361-1_0_6_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_1361-1_0_6_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_1361-1_0_6_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_1361-1_0_6_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_1361-1_0_6_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_1361-1_0_6_node_62 | 0.4 | n |  | TRUE
45 | bus_LV_1361-1_0_6_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_1361-1_0_6_node_56 | 0.4 | n |  | TRUE
47 | bus_LV_1361-1_0_6_node_96 | 0.4 | n |  | TRUE
48 | bus_LV_1361-1_0_6_node_123 | 0.4 | n |  | TRUE
49 | bus_LV_1361-1_0_6_node_120 | 0.4 | n |  | TRUE
50 | bus_LV_1361-1_0_6_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_1361-1_0_6_node_57 | 0.4 | n |  | TRUE
52 | bus_LV_1361-1_0_6_node_58 | 0.4 | n |  | TRUE
53 | bus_LV_1361-1_0_6_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_1361-1_0_6_node_97 | 0.4 | n |  | TRUE
55 | bus_LV_1361-1_0_6_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_1361-1_0_6_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_1361-1_0_6_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_1361-1_0_6_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_1361-1_0_6_node_31 | 0.4 | n |  | TRUE
60 | bus_LV_1361-1_0_6_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_1361-1_0_6_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_1361-1_0_6_node_84 | 0.4 | n |  | TRUE
63 | bus_LV_1361-1_0_6_node_83 | 0.4 | n |  | TRUE
64 | bus_LV_1361-1_0_6_node_33 | 0.4 | n |  | TRUE
65 | bus_LV_1361-1_0_6_node_34 | 0.4 | n |  | TRUE
66 | bus_LV_1361-1_0_6_node_35 | 0.4 | n |  | TRUE
67 | bus_LV_1361-1_0_6_node_36 | 0.4 | n |  | TRUE
68 | bus_LV_1361-1_0_6_node_37 | 0.4 | n |  | TRUE
69 | bus_LV_1361-1_0_6_node_70 | 0.4 | n |  | TRUE
70 | bus_LV_1361-1_0_6_node_94 | 0.4 | n |  | TRUE
71 | bus_LV_1361-1_0_6_node_92 | 0.4 | n |  | TRUE
72 | bus_LV_1361-1_0_6_node_38 | 0.4 | n |  | TRUE
73 | bus_LV_1361-1_0_6_node_39 | 0.4 | n |  | TRUE
74 | bus_LV_1361-1_0_6_node_43 | 0.4 | n |  | TRUE
75 | bus_LV_1361-1_0_6_node_101 | 0.4 | n |  | TRUE
76 | bus_LV_1361-1_0_6_node_40 | 0.4 | n |  | TRUE
77 | bus_LV_1361-1_0_6_node_131 | 0.4 | n |  | TRUE
78 | bus_LV_1361-1_0_6_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_1361-1_0_6_node_99 | 0.4 | n |  | TRUE
80 | bus_LV_1361-1_0_6_node_45 | 0.4 | n |  | TRUE
81 | bus_LV_1361-1_0_6_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_1361-1_0_6_node_48 | 0.4 | n |  | TRUE
83 | bus_LV_1361-1_0_6_node_49 | 0.4 | n |  | TRUE
84 | bus_LV_1361-1_0_6_node_52 | 0.4 | n |  | TRUE
85 | bus_LV_1361-1_0_6_node_53 | 0.4 | n |  | TRUE
86 | bus_LV_1361-1_0_6_node_89 | 0.4 | n |  | TRUE
87 | bus_LV_1361-1_0_6_node_86 | 0.4 | n |  | TRUE
88 | bus_LV_1361-1_0_6_node_110 | 0.4 | n |  | TRUE
89 | bus_LV_1361-1_0_6_node_111 | 0.4 | n |  | TRUE
90 | bus_LV_1361-1_0_6_node_109 | 0.4 | n |  | TRUE
91 | bus_LV_1361-1_0_6_node_66 | 0.4 | n |  | TRUE
92 | bus_LV_1361-1_0_6_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_1361-1_0_6_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_1361-1_0_6_node_67 | 0.4 | n |  | TRUE
95 | bus_LV_1361-1_0_6_node_82 | 0.4 | n |  | TRUE
96 | bus_LV_1361-1_0_6_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_1361-1_0_6_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_1361-1_0_6_node_71 | 0.4 | n |  | TRUE
99 | bus_LV_1361-1_0_6_node_72 | 0.4 | n |  | TRUE
100 | bus_LV_1361-1_0_6_node_73 | 0.4 | n |  | TRUE
101 | bus_LV_1361-1_0_6_node_74 | 0.4 | n |  | TRUE
102 | bus_LV_1361-1_0_6_node_75 | 0.4 | n |  | TRUE
103 | bus_LV_1361-1_0_6_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_1361-1_0_6_node_104 | 0.4 | n |  | TRUE
105 | bus_LV_1361-1_0_6_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_1361-1_0_6_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_1361-1_0_6_node_121 | 0.4 | n |  | TRUE
108 | bus_LV_1361-1_0_6_node_122 | 0.4 | n |  | TRUE
109 | bus_LV_1361-1_0_6_node_130 | 0.4 | n |  | TRUE
110 | bus_LV_1361-1_0_6_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_1361-1_0_6_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_1361-1_0_6_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_1361-1_0_6_node_117 | 0.4 | n |  | TRUE
114 | bus_LV_1361-1_0_6_node_118 | 0.4 | n |  | TRUE
115 | bus_LV_1361-1_0_6_node_129 | 0.4 | n |  | TRUE
116 | bus_LV_1361-1_0_6_node_145 | 0.4 | n |  | TRUE
117 | bus_LV_1361-1_0_6_node_119 | 0.4 | n |  | TRUE
118 | bus_LV_1361-1_0_6_node_105 | 0.4 | n |  | TRUE
119 | bus_LV_1361-1_0_6_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_1361-1_0_6_node_107 | 0.4 | n |  | TRUE
121 | bus_LV_1361-1_0_6_node_108 | 0.4 | n |  | TRUE
122 | bus_LV_1361-1_0_6_node_132 | 0.4 | n |  | TRUE
123 | bus_LV_1361-1_0_6_node_112 | 0.4 | n |  | TRUE
124 | bus_LV_1361-1_0_6_node_124 | 0.4 | n |  | TRUE
125 | bus_LV_1361-1_0_6_node_113 | 0.4 | n |  | TRUE
126 | bus_LV_1361-1_0_6_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_1361-1_0_6_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_1361-1_0_6_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_1361-1_0_6_node_127 | 0.4 | n |  | TRUE
130 | bus_LV_1361-1_0_6_node_128 | 0.4 | n |  | TRUE
131 | bus_LV_1361-1_0_6_node_134 | 0.4 | n |  | TRUE
132 | bus_LV_1361-1_0_6_node_126 | 0.4 | n |  | TRUE
133 | bus_LV_1361-1_0_6_node_144 | 0.4 | n |  | TRUE
134 | bus_LV_1361-1_0_6_node_143 | 0.4 | n |  | TRUE
135 | bus_LV_1361-1_0_6_node_133 | 0.4 | n |  | TRUE
136 | bus_LV_1361-1_0_6_node_135 | 0.4 | n |  | TRUE
137 | bus_LV_1361-1_0_6_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_1361-1_0_6_node_139 | 0.4 | n |  | TRUE
139 | bus_LV_1361-1_0_6_node_138 | 0.4 | n |  | TRUE
140 | bus_LV_1361-1_0_6_node_137 | 0.4 | n |  | TRUE
141 | bus_LV_1361-1_0_6_node_141 | 0.4 | n |  | TRUE
142 | bus_LV_1361-1_0_6_node_140 | 0.4 | n |  | TRUE
143 | bus_LV_1361-1_0_6_node_142 | 0.4 | n |  | TRUE
144 | bus_MV_22_1_node_11 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1361-1_0_6_load_0 | 0 | 0.0052357 | 0.0013122 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1361-1_0_6_load_51 | 2 | 0.0019202 | 0.00048126 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1361-1_0_6_load_50 | 4 | 0.0089653 | 0.0022469 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1361-1_0_6_load_47 | 5 | 0.0014522 | 0.00036396 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1361-1_0_6_load_60 | 6 | 0.0009634 | 0.00024145 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1361-1_0_6_load_61 | 7 | 0.0035537 | 0.00089065 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1361-1_0_6_load_2 | 8 | 0.0015556 | 0.00038987 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1361-1_0_6_load_3 | 9 | 0.0016085 | 0.00040312 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1361-1_0_6_load_55 | 10 | 0.0013559 | 0.00033981 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1361-1_0_6_load_69 | 11 | 0.0018544 | 0.00046475 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1361-1_0_6_load_6 | 12 | 0.0017374 | 0.00043544 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1361-1_0_6_load_7 | 13 | 0.0022093 | 0.00055369 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1361-1_0_6_load_8 | 14 | 0.00085902 | 0.00021529 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1361-1_0_6_load_9 | 15 | 0.0028388 | 0.00071147 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1361-1_0_6_load_10 | 16 | 0.00076102 | 0.00019073 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1361-1_0_6_load_64 | 17 | 0.0016999 | 0.00042604 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1361-1_0_6_load_65 | 18 | 0.0015623 | 0.00039155 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1361-1_0_6_load_11 | 19 | 0.0032324 | 0.00081011 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1361-1_0_6_load_12 | 20 | 0.0028824 | 0.0007224 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1361-1_0_6_load_88 | 23 | 0.0015121 | 0.00037898 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1361-1_0_6_load_87 | 25 | 0.00097745 | 0.00024497 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1361-1_0_6_load_116 | 26 | 0.0031234 | 0.00078279 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1361-1_0_6_load_98 | 27 | 0.0017263 | 0.00043264 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1361-1_0_6_load_15 | 28 | 0.00042479 | 0.00010646 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1361-1_0_6_load_16 | 29 | 0.00049559 | 0.00012421 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1361-1_0_6_load_17 | 30 | 0.00053254 | 0.00013347 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1361-1_0_6_load_18 | 31 | 0.00049836 | 0.0001249 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1361-1_0_6_load_19 | 32 | 0.00054334 | 0.00013617 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1361-1_0_6_load_80 | 34 | 0.00067427 | 0.00016899 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1361-1_0_6_load_68 | 35 | 0.00092065 | 0.00023074 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1361-1_0_6_load_42 | 36 | 0.0015994 | 0.00040085 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1361-1_0_6_load_20 | 37 | 0.001888 | 0.00047319 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1361-1_0_6_load_21 | 38 | 0.0017239 | 0.00043204 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1361-1_0_6_load_24 | 41 | 0.0012693 | 0.00031811 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1361-1_0_6_load_25 | 42 | 0.0013621 | 0.00034137 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1361-1_0_6_load_26 | 43 | 0.0017559 | 0.00044008 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1361-1_0_6_load_62 | 44 | 0.0019422 | 0.00048676 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1361-1_0_6_load_46 | 45 | 0.0018741 | 0.0004697 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1361-1_0_6_load_96 | 47 | 0.0011939 | 0.00029923 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1361-1_0_6_load_123 | 48 | 0.0020002 | 0.0005013 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1361-1_0_6_load_120 | 49 | 0.0013906 | 0.00034853 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1361-1_0_6_load_44 | 50 | 0.0013733 | 0.00034418 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1361-1_0_6_load_57 | 51 | 0.0029431 | 0.00073762 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1361-1_0_6_load_58 | 52 | 0.0019017 | 0.0004766 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1361-1_0_6_load_59 | 53 | 0.0018745 | 0.0004698 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1361-1_0_6_load_97 | 54 | 0.003492 | 0.00087518 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1361-1_0_6_load_27 | 55 | 0.0013374 | 0.00033519 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1361-1_0_6_load_28 | 56 | 0.00079715 | 0.00019979 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1361-1_0_6_load_30 | 58 | 0.00073754 | 0.00018485 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1361-1_0_6_load_31 | 59 | 0.00055482 | 0.00013905 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1361-1_0_6_load_32 | 60 | 0.0016379 | 0.00041049 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1361-1_0_6_load_54 | 61 | 0.0023798 | 0.00059644 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1361-1_0_6_load_84 | 62 | 0.0011307 | 0.00028338 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1361-1_0_6_load_83 | 63 | 0.0013377 | 0.00033527 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1361-1_0_6_load_33 | 64 | 0.0019228 | 0.00048191 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1361-1_0_6_load_34 | 65 | 0.0025634 | 0.00064245 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1361-1_0_6_load_35 | 66 | 0.0015513 | 0.0003888 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1361-1_0_6_load_36 | 67 | 0.0022639 | 0.00056738 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1361-1_0_6_load_37 | 68 | 0.0043655 | 0.0010941 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1361-1_0_6_load_70 | 69 | 0.0026041 | 0.00065265 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1361-1_0_6_load_94 | 70 | 0.0017678 | 0.00044306 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1361-1_0_6_load_92 | 71 | 0.0033949 | 0.00085085 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1361-1_0_6_load_38 | 72 | 0.0015409 | 0.00038619 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1361-1_0_6_load_43 | 74 | 0.0020972 | 0.00052561 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1361-1_0_6_load_101 | 75 | 0.0014215 | 0.00035625 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1361-1_0_6_load_40 | 76 | 0.0016875 | 0.00042292 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1361-1_0_6_load_131 | 77 | 0.0053619 | 0.0013438 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1361-1_0_6_load_76 | 78 | 0.00085142 | 0.00021339 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1361-1_0_6_load_99 | 79 | 0.0011897 | 0.00029816 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1361-1_0_6_load_45 | 80 | 0.0012814 | 0.00032114 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1361-1_0_6_load_77 | 81 | 0.0014422 | 0.00036145 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1361-1_0_6_load_48 | 82 | 0.0015691 | 0.00039326 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1361-1_0_6_load_53 | 85 | 0.0018024 | 0.00045173 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1361-1_0_6_load_89 | 86 | 0.0016213 | 0.00040635 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1361-1_0_6_load_86 | 87 | 0.0017989 | 0.00045084 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1361-1_0_6_load_111 | 89 | 0.0029357 | 0.00073575 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1361-1_0_6_load_109 | 90 | 0.0035802 | 0.00089729 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1361-1_0_6_load_66 | 91 | 0.0032849 | 0.00082327 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1361-1_0_6_load_81 | 92 | 0.0025618 | 0.00064204 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1361-1_0_6_load_95 | 93 | 0.0024938 | 0.00062502 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1361-1_0_6_load_67 | 94 | 0.0027124 | 0.00067978 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1361-1_0_6_load_82 | 95 | 0.0010838 | 0.00027164 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1361-1_0_6_load_78 | 96 | 0.0020256 | 0.00050767 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1361-1_0_6_load_79 | 97 | 0.0015637 | 0.00039191 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1361-1_0_6_load_71 | 98 | 0.00081641 | 0.00020461 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1361-1_0_6_load_72 | 99 | 0.00055138 | 0.00013819 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1361-1_0_6_load_104 | 104 | 0.0013059 | 0.00032729 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1361-1_0_6_load_103 | 105 | 0.0014852 | 0.00037222 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1361-1_0_6_load_102 | 106 | 0.0022438 | 0.00056234 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1361-1_0_6_load_121 | 107 | 0.0022528 | 0.0005646 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1361-1_0_6_load_122 | 108 | 0.0022101 | 0.0005539 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1361-1_0_6_load_130 | 109 | 0.0033828 | 0.0008478 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1361-1_0_6_load_90 | 110 | 0.0039178 | 0.0009819 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1361-1_0_6_load_91 | 111 | 0.0029692 | 0.00074414 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1361-1_0_6_load_93 | 112 | 0.0013069 | 0.00032753 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1361-1_0_6_load_145 | 116 | 0.0017063 | 0.00042763 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1361-1_0_6_load_119 | 117 | 0.0009388 | 0.00023528 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1361-1_0_6_load_105 | 118 | 0.0019995 | 0.00050113 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1361-1_0_6_load_106 | 119 | 0.0010507 | 0.00026332 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1361-1_0_6_load_107 | 120 | 0.0030893 | 0.00077424 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1361-1_0_6_load_108 | 121 | 0.00073247 | 0.00018357 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1361-1_0_6_load_132 | 122 | 0.00045706 | 0.00011455 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1361-1_0_6_load_112 | 123 | 0.0022487 | 0.00056358 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1361-1_0_6_load_124 | 124 | 0.0013629 | 0.00034158 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1361-1_0_6_load_113 | 125 | 0.002991 | 0.00074963 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1361-1_0_6_load_114 | 126 | 0.0019808 | 0.00049644 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1361-1_0_6_load_125 | 127 | 0.0022811 | 0.00057169 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1361-1_0_6_load_115 | 128 | 0.002408 | 0.0006035 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1361-1_0_6_load_127 | 129 | 0.0020426 | 0.00051193 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1361-1_0_6_load_128 | 130 | 0.0015893 | 0.00039832 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1361-1_0_6_load_134 | 131 | 0.00051877 | 0.00013002 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1361-1_0_6_load_126 | 132 | 0.0026945 | 0.0006753 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1361-1_0_6_load_144 | 133 | 0.0033086 | 0.00082921 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1361-1_0_6_load_143 | 134 | 0.0014594 | 0.00036577 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1361-1_0_6_load_133 | 135 | 0.0010068 | 0.00025232 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1361-1_0_6_load_136 | 137 | 0.0010045 | 0.00025176 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1361-1_0_6_load_139 | 138 | 0.001469 | 0.00036815 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1361-1_0_6_load_137 | 140 | 0.00061824 | 0.00015495 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_1361-1_0_6_load_141 | 141 | 0.00062943 | 0.00015775 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_1361-1_0_6_load_140 | 142 | 0.00092734 | 0.00023241 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_1361-1_0_6_load_142 | 143 | 0.0012083 | 0.00030283 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 87 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1361-1_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.075896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1361-1_0_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.10408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1361-1_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.048499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1361-1_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.021539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1361-1_0_6_line_4 | NAYY 4x150 SE | 3 | 7 | 0.061285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1361-1_0_6_line_5 | NAYY 4x150 SE | 4 | 5 | 0.11962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1361-1_0_6_line_6 | NAYY 4x150 SE | 5 | 81 | 0.0096228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1361-1_0_6_line_7 | NAYY 4x150 SE | 5 | 80 | 0.027529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1361-1_0_6_line_8 | NAYY 4x150 SE | 6 | 7 | 0.091223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1361-1_0_6_line_9 | NAYY 4x150 SE | 6 | 8 | 0.067116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1361-1_0_6_line_10 | NAYY 4x150 SE | 8 | 9 | 0.04395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1361-1_0_6_line_11 | NAYY 4x150 SE | 9 | 10 | 0.006126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1361-1_0_6_line_12 | NAYY 4x150 SE | 10 | 11 | 0.028967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1361-1_0_6_line_13 | NAYY 4x150 SE | 11 | 69 | 0.020693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1361-1_0_6_line_14 | NAYY 4x150 SE | 12 | 13 | 0.001448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1361-1_0_6_line_15 | NAYY 4x150 SE | 12 | 14 | 0.021864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1361-1_0_6_line_16 | NAYY 4x150 SE | 13 | 15 | 0.0070932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1361-1_0_6_line_17 | NAYY 4x150 SE | 14 | 16 | 0.0016415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1361-1_0_6_line_18 | NAYY 4x150 SE | 15 | 17 | 0.016322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1361-1_0_6_line_19 | NAYY 4x150 SE | 17 | 18 | 0.0027904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1361-1_0_6_line_20 | NAYY 4x150 SE | 18 | 33 | 0.017127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1361-1_0_6_line_21 | NAYY 4x150 SE | 19 | 20 | 0.02209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1361-1_0_6_line_22 | NAYY 4x150 SE | 19 | 21 | 0.038774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1361-1_0_6_line_23 | NAYY 4x150 SE | 21 | 22 | 0.011545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1361-1_0_6_line_24 | NAYY 4x150 SE | 22 | 23 | 0.018811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1361-1_0_6_line_25 | NAYY 4x150 SE | 22 | 24 | 0.019366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1361-1_0_6_line_26 | NAYY 4x150 SE | 23 | 25 | 0.011942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1361-1_0_6_line_27 | NAYY 4x150 SE | 24 | 26 | 0.087436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1361-1_0_6_line_28 | NAYY 4x150 SE | 24 | 27 | 0.04706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1361-1_0_6_line_29 | NAYY 4x150 SE | 25 | 87 | 0.017013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1361-1_0_6_line_30 | NAYY 4x150 SE | 26 | 113 | 0.041008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1361-1_0_6_line_31 | NAYY 4x150 SE | 27 | 79 | 0.047063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1361-1_0_6_line_32 | NAYY 4x150 SE | 28 | 29 | 0.016227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1361-1_0_6_line_33 | NAYY 4x150 SE | 28 | 30 | 0.022721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1361-1_0_6_line_34 | NAYY 4x150 SE | 29 | 31 | 0.0031597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1361-1_0_6_line_35 | NAYY 4x150 SE | 30 | 32 | 0.0051302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1361-1_0_6_line_36 | NAYY 4x150 SE | 31 | 33 | 0.0025277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1361-1_0_6_line_37 | NAYY 4x150 SE | 32 | 34 | 0.0024154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1361-1_0_6_line_38 | NAYY 4x150 SE | 33 | 35 | 0.029231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1361-1_0_6_line_39 | NAYY 4x150 SE | 34 | 36 | 0.020174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1361-1_0_6_line_40 | NAYY 4x150 SE | 35 | 59 | 0.035673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1361-1_0_6_line_41 | NAYY 4x150 SE | 36 | 73 | 0.017345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1361-1_0_6_line_42 | NAYY 4x150 SE | 37 | 38 | 0.012774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1361-1_0_6_line_43 | NAYY 4x150 SE | 37 | 39 | 0.029354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1361-1_0_6_line_44 | NAYY 4x150 SE | 38 | 40 | 0.013629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1361-1_0_6_line_45 | NAYY 4x150 SE | 39 | 41 | 0.015827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1361-1_0_6_line_46 | NAYY 4x150 SE | 39 | 42 | 0.021082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1361-1_0_6_line_47 | NAYY 4x150 SE | 39 | 43 | 0.017547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1361-1_0_6_line_48 | NAYY 4x150 SE | 40 | 44 | 0.0067256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1361-1_0_6_line_49 | NAYY 4x150 SE | 40 | 45 | 0.016329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1361-1_0_6_line_50 | NAYY 4x150 SE | 41 | 46 | 0.031116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1361-1_0_6_line_51 | NAYY 4x150 SE | 42 | 47 | 0.019221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1361-1_0_6_line_52 | NAYY 4x150 SE | 43 | 48 | 0.023615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1361-1_0_6_line_53 | NAYY 4x150 SE | 44 | 49 | 0.022304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_1361-1_0_6_line_54 | NAYY 4x150 SE | 45 | 50 | 0.016088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1361-1_0_6_line_55 | NAYY 4x150 SE | 46 | 51 | 0.01613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1361-1_0_6_line_56 | NAYY 4x150 SE | 46 | 52 | 0.013567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1361-1_0_6_line_57 | NAYY 4x150 SE | 46 | 53 | 0.010877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1361-1_0_6_line_58 | NAYY 4x150 SE | 47 | 54 | 0.005917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1361-1_0_6_line_59 | NAYY 4x150 SE | 49 | 86 | 0.001088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1361-1_0_6_line_60 | NAYY 4x150 SE | 50 | 80 | 0.015314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1361-1_0_6_line_61 | NAYY 4x150 SE | 51 | 91 | 0.00060794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1361-1_0_6_line_62 | NAYY 4x150 SE | 52 | 92 | 0.027225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1361-1_0_6_line_63 | NAYY 4x150 SE | 53 | 93 | 0.013772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1361-1_0_6_line_64 | NAYY 4x150 SE | 55 | 56 | 0.031462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1361-1_0_6_line_65 | NAYY 4x150 SE | 55 | 57 | 0.02479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1361-1_0_6_line_66 | NAYY 4x150 SE | 56 | 58 | 0.015193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1361-1_0_6_line_67 | NAYY 4x150 SE | 57 | 59 | 0.0095725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1361-1_0_6_line_68 | NAYY 4x150 SE | 57 | 60 | 0.016799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1361-1_0_6_line_69 | NAYY 4x150 SE | 58 | 61 | 0.021516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1361-1_0_6_line_70 | NAYY 4x150 SE | 60 | 62 | 0.048556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1361-1_0_6_line_71 | NAYY 4x150 SE | 62 | 63 | 0.022344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1361-1_0_6_line_72 | NAYY 4x150 SE | 63 | 101 | 0.03577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1361-1_0_6_line_73 | NAYY 4x150 SE | 64 | 65 | 0.0091061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1361-1_0_6_line_74 | NAYY 4x150 SE | 64 | 66 | 0.0051771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1361-1_0_6_line_75 | NAYY 4x150 SE | 65 | 67 | 0.012313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1361-1_0_6_line_76 | NAYY 4x150 SE | 66 | 68 | 0.020914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1361-1_0_6_line_77 | NAYY 4x150 SE | 67 | 69 | 0.01097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1361-1_0_6_line_78 | NAYY 4x150 SE | 68 | 70 | 0.013225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1361-1_0_6_line_79 | NAYY 4x150 SE | 70 | 71 | 0.0011224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1361-1_0_6_line_80 | NAYY 4x150 SE | 71 | 110 | 0.033051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1361-1_0_6_line_81 | NAYY 4x150 SE | 72 | 73 | 0.011029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1361-1_0_6_line_82 | NAYY 4x150 SE | 73 | 74 | 0.01482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1361-1_0_6_line_83 | NAYY 4x150 SE | 74 | 75 | 0.015905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1361-1_0_6_line_84 | NAYY 4x150 SE | 75 | 79 | 0.022273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1361-1_0_6_line_85 | NAYY 4x150 SE | 76 | 77 | 0.068921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1361-1_0_6_line_86 | NAYY 4x150 SE | 77 | 78 | 0.077019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1361-1_0_6_line_87 | NAYY 4x150 SE | 78 | 100 | 0.050119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1361-1_0_6_line_88 | NAYY 4x150 SE | 82 | 83 | 0.02634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1361-1_0_6_line_89 | NAYY 4x150 SE | 83 | 84 | 0.007623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1361-1_0_6_line_90 | NAYY 4x150 SE | 83 | 85 | 0.026499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1361-1_0_6_line_91 | NAYY 4x150 SE | 84 | 86 | 0.017168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_1361-1_0_6_line_92 | NAYY 4x150 SE | 84 | 87 | 0.030978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_1361-1_0_6_line_93 | NAYY 4x150 SE | 85 | 88 | 0.012688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1361-1_0_6_line_94 | NAYY 4x150 SE | 88 | 89 | 0.050449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1361-1_0_6_line_95 | NAYY 4x150 SE | 88 | 90 | 0.0073928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1361-1_0_6_line_96 | NAYY 4x150 SE | 89 | 125 | 0.00055345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1361-1_0_6_line_97 | NAYY 4x150 SE | 90 | 120 | 0.014001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1361-1_0_6_line_98 | NAYY 4x150 SE | 91 | 94 | 0.024005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1361-1_0_6_line_99 | NAYY 4x150 SE | 92 | 95 | 0.0068721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1361-1_0_6_line_100 | NAYY 4x150 SE | 94 | 96 | 0.0022085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1361-1_0_6_line_101 | NAYY 4x150 SE | 95 | 107 | 0.01227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1361-1_0_6_line_102 | NAYY 4x150 SE | 96 | 97 | 0.0064237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1361-1_0_6_line_103 | NAYY 4x150 SE | 98 | 99 | 0.031514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1361-1_0_6_line_104 | NAYY 4x150 SE | 98 | 100 | 0.03571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1361-1_0_6_line_105 | NAYY 4x150 SE | 99 | 101 | 0.03692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1361-1_0_6_line_106 | NAYY 4x150 SE | 100 | 102 | 0.0596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1361-1_0_6_line_107 | NAYY 4x150 SE | 101 | 103 | 0.045498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1361-1_0_6_line_108 | NAYY 4x150 SE | 102 | 104 | 0.079586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1361-1_0_6_line_109 | NAYY 4x150 SE | 103 | 105 | 0.076838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1361-1_0_6_line_110 | NAYY 4x150 SE | 103 | 106 | 0.0097362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1361-1_0_6_line_111 | NAYY 4x150 SE | 105 | 109 | 0.025832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1361-1_0_6_line_112 | NAYY 4x150 SE | 107 | 108 | 0.01333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1361-1_0_6_line_113 | NAYY 4x150 SE | 110 | 111 | 0.0079627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1361-1_0_6_line_114 | NAYY 4x150 SE | 111 | 112 | 0.00065549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1361-1_0_6_line_115 | NAYY 4x150 SE | 113 | 114 | 0.015564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1361-1_0_6_line_116 | NAYY 4x150 SE | 114 | 115 | 0.01371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1361-1_0_6_line_117 | NAYY 4x150 SE | 114 | 116 | 0.12482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1361-1_0_6_line_118 | NAYY 4x150 SE | 115 | 117 | 0.010103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1361-1_0_6_line_119 | NAYY 4x150 SE | 116 | 131 | 0.19937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1361-1_0_6_line_120 | NAYY 4x150 SE | 118 | 119 | 0.019857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1361-1_0_6_line_121 | NAYY 4x150 SE | 118 | 120 | 0.0086495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1361-1_0_6_line_122 | NAYY 4x150 SE | 119 | 121 | 0.021829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1361-1_0_6_line_123 | NAYY 4x150 SE | 119 | 122 | 0.093958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1361-1_0_6_line_124 | NAYY 4x150 SE | 121 | 123 | 0.011835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1361-1_0_6_line_125 | NAYY 4x150 SE | 123 | 124 | 0.0016089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1361-1_0_6_line_126 | NAYY 4x150 SE | 124 | 127 | 0.0058231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1361-1_0_6_line_127 | NAYY 4x150 SE | 125 | 126 | 0.021032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1361-1_0_6_line_128 | NAYY 4x150 SE | 126 | 128 | 0.0060261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1361-1_0_6_line_129 | NAYY 4x150 SE | 127 | 132 | 0.015329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1361-1_0_6_line_130 | NAYY 4x150 SE | 128 | 129 | 0.018878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_1361-1_0_6_line_131 | NAYY 4x150 SE | 129 | 130 | 0.00073684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_1361-1_0_6_line_132 | NAYY 4x150 SE | 130 | 134 | 0.010778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_1361-1_0_6_line_133 | NAYY 4x150 SE | 131 | 135 | 0.036364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_1361-1_0_6_line_134 | NAYY 4x150 SE | 132 | 133 | 0.022827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_1361-1_0_6_line_135 | NAYY 4x150 SE | 135 | 136 | 0.0076547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_1361-1_0_6_line_136 | NAYY 4x150 SE | 136 | 137 | 0.011137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_1361-1_0_6_line_137 | NAYY 4x150 SE | 137 | 138 | 0.027205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_1361-1_0_6_line_138 | NAYY 4x150 SE | 138 | 139 | 0.018456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_1361-1_0_6_line_139 | NAYY 4x150 SE | 139 | 142 | 0.037552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_1361-1_0_6_line_140 | NAYY 4x150 SE | 139 | 140 | 0.034469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_1361-1_0_6_line_141 | NAYY 4x150 SE | 140 | 141 | 0.071546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_1361-1_0_6_line_142 | NAYY 4x150 SE | 142 | 143 | 0.023815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1361-1_0_6_trafo_86 | 0.25 MVA 20/0.4 kV | 144 | 87 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2696362.1299 | 1211283.8801 | 2696368.5979 | 1211270.2307 | 2696370.7301 | 1211257.7455 | 2696368.7241 | 1211209.6618
1 | 2696368.7241 | 1211209.6618 | 2696265.1698 | 1211220.1541
2 | 2696362.1299 | 1211283.8801 | 2696371.5246 | 1211274.8923 | 2696380.5666 | 1211267.9781 | 2696393.7477 | 1211259.374 | 2696400.5677 | 1211254.5142
3 | 2696252.6085 | 1211202.6574 | 2696255.016 | 1211206.0087 | 2696265.1698 | 1211220.1541
4 | 2696400.5677 | 1211254.5142 | 2696401.9481 | 1211241.5276 | 2696404.9304 | 1211229.1229 | 2696414.2278 | 1211214.4075 | 2696419.2371 | 1211197.0556
5 | 2696251.1953 | 1211083.042 | 2696252.6085 | 1211202.6574
6 | 2696260.7777 | 1211082.1614 | 2696251.1953 | 1211083.042
7 | 2696229.4976 | 1211074.5268 | 2696235.2556 | 1211084.5068 | 2696251.1953 | 1211083.042
8 | 2696417.1256 | 1211105.8573 | 2696419.2371 | 1211197.0556
9 | 2696357.4539 | 1211075.1354 | 2696417.1256 | 1211105.8573
10 | 2696357.4539 | 1211075.1354 | 2696356.0367 | 1211031.2086 | 2696356.0367 | 1211031.2086
11 | 2696357.0389 | 1211025.1651 | 2696356.0367 | 1211031.2086
12 | 2696357.0389 | 1211025.1651 | 2696361.2832 | 1210999.5717 | 2696362.5757 | 1210996.8374
13 | 2696362.5757 | 1210996.8374 | 2696364.4546 | 1210992.8628 | 2696374.8276 | 1210980.2935
14 | 2696014.7439 | 1211093.4937 | 2696013.8175 | 1211092.3808
15 | 2696014.7439 | 1211093.4937 | 2696028.7327 | 1211110.2974
16 | 2696009.2792 | 1211086.9294 | 2696013.8175 | 1211092.3808
17 | 2696029.7829 | 1211111.559 | 2696028.7327 | 1211110.2974
18 | 2696009.2792 | 1211086.9294 | 2696007.9512 | 1211085.3342 | 2696000.0803 | 1211073.4601
19 | 2695998.5386 | 1211071.1342 | 2696000.0803 | 1211073.4601
20 | 2695986.9928 | 1211058.6787 | 2695994.8472 | 1211065.5653 | 2695998.5386 | 1211071.1342
21 | 2696192.1996 | 1210953.7306 | 2696174.567 | 1210959.5872 | 2696171.5271 | 1210961.3431
22 | 2696135.4009 | 1210974.2104 | 2696158.0874 | 1210969.1059 | 2696171.5271 | 1210961.3431
23 | 2696135.4009 | 1210974.2104 | 2696130.6858 | 1210984.7528
24 | 2696130.6858 | 1210984.7528 | 2696138.6981 | 1211001.7724
25 | 2696130.6858 | 1210984.7528 | 2696126.9604 | 1210976.8096 | 2696124.3821 | 1210968.429 | 2696123.8632 | 1210966.6749
26 | 2696143.7848 | 1211012.5773 | 2696138.6981 | 1211001.7724
27 | 2696123.8632 | 1210966.6749 | 2696109.5529 | 1210880.4182
28 | 2696123.8632 | 1210966.6749 | 2696110.5631 | 1210972.7426 | 2696097.981 | 1210977.6544 | 2696087.1441 | 1210978.5027 | 2696079.2483 | 1210976.8633
29 | 2696143.7848 | 1211012.5773 | 2696151.0312 | 1211027.9702
30 | 2696103.6302 | 1210839.8401 | 2696109.5529 | 1210880.4182
31 | 2696079.2483 | 1210976.8633 | 2696070.0165 | 1210974.9467 | 2696056.3772 | 1210974.2488 | 2696046.3412 | 1210975.388 | 2696032.888 | 1210978.7912
32 | 2695984.9166 | 1211053.3839 | 2695978.9927 | 1211038.2765
33 | 2695967.1565 | 1211019.1091 | 2695967.384 | 1211019.4587 | 2695976.1293 | 1211030.9739 | 2695978.9927 | 1211038.2765
34 | 2695986.07 | 1211056.3255 | 2695984.9166 | 1211053.3839
35 | 2695967.1565 | 1211019.1091 | 2695964.3583 | 1211014.8093
36 | 2695986.9928 | 1211058.6787 | 2695986.07 | 1211056.3255
37 | 2695963.0703 | 1211012.7676 | 2695963.2379 | 1211013.0876 | 2695964.3583 | 1211014.8093
38 | 2695986.9928 | 1211058.6787 | 2695990.3007 | 1211069.4282 | 2695990.1473 | 1211077.5424 | 2695987.813 | 1211087.131
39 | 2695964.7867 | 1210995.2223 | 2695963.6619 | 1210995.7159 | 2695959.8789 | 1211000.7808 | 2695960.6423 | 1211008.1314 | 2695963.0703 | 1211012.7676
40 | 2695986.1434 | 1211122.2974 | 2695985.8699 | 1211114.7323 | 2695984.6068 | 1211106.3284 | 2695984.4421 | 1211100.9777 | 2695987.813 | 1211087.131
41 | 2695981.2079 | 1210989.8052 | 2695971.2629 | 1210992.3804 | 2695964.7867 | 1210995.2223
42 | 2696217.2913 | 1211026.1065 | 2696228.2082 | 1211019.4738
43 | 2696253.2953 | 1211004.2318 | 2696228.2082 | 1211019.4738
44 | 2696205.644 | 1211033.183 | 2696217.2913 | 1211026.1065
45 | 2696253.2953 | 1211004.2318 | 2696266.8548 | 1210996.0686
46 | 2696253.2953 | 1211004.2318 | 2696263.4928 | 1211022.6839
47 | 2696253.2953 | 1211004.2318 | 2696245.1119 | 1210988.7094
48 | 2696205.644 | 1211033.183 | 2696199.753 | 1211036.428
49 | 2696205.644 | 1211033.183 | 2696213.8044 | 1211047.3269
50 | 2696293.5132 | 1210980.0197 | 2696266.8548 | 1210996.0686
51 | 2696272.79 | 1211039.5069 | 2696263.4928 | 1211022.6839
52 | 2696234.0988 | 1210967.8194 | 2696245.1119 | 1210988.7094
53 | 2696180.2166 | 1211047.1893 | 2696199.753 | 1211036.428
54 | 2696213.8044 | 1211047.3269 | 2696221.8443 | 1211061.262
55 | 2696293.5132 | 1210980.0197 | 2696301.9342 | 1210993.7769
56 | 2696293.5132 | 1210980.0197 | 2696305.1205 | 1210972.9961
57 | 2696293.5132 | 1210980.0197 | 2696288.575 | 1210970.3282
58 | 2696271.2268 | 1211045.0713 | 2696273.0053 | 1211039.8964 | 2696272.79 | 1211039.5069
59 | 2696179.2636 | 1211047.7142 | 2696180.2166 | 1211047.1893
60 | 2696229.4976 | 1211074.5268 | 2696221.8443 | 1211061.262
61 | 2696302.2516 | 1210994.2954 | 2696301.9342 | 1210993.7769
62 | 2696305.1205 | 1210972.9961 | 2696322.5961 | 1210962.4216 | 2696325.3793 | 1210956.2178 | 2696325.3793 | 1210956.2178
63 | 2696282.3226 | 1210958.0574 | 2696288.575 | 1210970.3282
64 | 2695946.735 | 1211091.8803 | 2695955.9616 | 1211109.114 | 2695960.8516 | 1211115.5415 | 2695963.7908 | 1211118.0088
65 | 2695984.3958 | 1211131.7091 | 2695968.1707 | 1211121.6857 | 2695963.7908 | 1211118.0088
66 | 2695946.735 | 1211091.8803 | 2695939.5641 | 1211078.4863
67 | 2695984.3958 | 1211131.7091 | 2695986.1434 | 1211122.2974
68 | 2695984.3958 | 1211131.7091 | 2695981.2283 | 1211144.8115 | 2695979.784 | 1211147.8001
69 | 2695928.7227 | 1211059.9313 | 2695933.1026 | 1211066.4172 | 2695939.5641 | 1211078.4863
70 | 2695945.9312 | 1211170.0833 | 2695949.2894 | 1211172.3388 | 2695954.6837 | 1211174.3492 | 2695959.9174 | 1211173.5884 | 2695965.8225 | 1211170.3033 | 2695971.2899 | 1211164.4651 | 2695975.8112 | 1211156.0209 | 2695979.784 | 1211147.8001
71 | 2695929.9953 | 1211154.5134 | 2695935.9215 | 1211160.9383 | 2695943.3193 | 1211168.329 | 2695945.9312 | 1211170.0833
72 | 2695903.4289 | 1211131.7181 | 2695906.5963 | 1211132.3139 | 2695909.5414 | 1211133.4954 | 2695913.8102 | 1211136.9664 | 2695929.9953 | 1211154.5134
73 | 2696387.2955 | 1210960.8209 | 2696387.9136 | 1210951.7358
74 | 2696386.4797 | 1210946.7612 | 2696387.9136 | 1210951.7358 | 2696387.9136 | 1210951.7358
75 | 2696387.2955 | 1210960.8209 | 2696387.2955 | 1210960.8209 | 2696382.0759 | 1210971.5106 | 2696381.8101 | 1210971.8326
76 | 2696386.4797 | 1210946.7612 | 2696385.2507 | 1210942.4976 | 2696375.5556 | 1210932.89 | 2696372.8024 | 1210932.2466
77 | 2696374.8276 | 1210980.2935 | 2696381.8101 | 1210971.8326
78 | 2696359.7943 | 1210930.1424 | 2696365.0759 | 1210930.4412 | 2696372.8024 | 1210932.2466
79 | 2696359.7943 | 1210930.1424 | 2696358.6737 | 1210930.079
80 | 2696330.6491 | 1210914.4601 | 2696340.1998 | 1210923.3346 | 2696347.3188 | 1210927.7415 | 2696355.4471 | 1210929.8965 | 2696358.6737 | 1210930.079
81 | 2695981.2079 | 1210989.8052 | 2695975.2429 | 1210980.5289
82 | 2695981.2079 | 1210989.8052 | 2695995.4223 | 1210985.6128
83 | 2696011.0189 | 1210982.5757 | 2696010.7457 | 1210982.5978 | 2695998.0089 | 1210984.8499 | 2695995.4223 | 1210985.6128
84 | 2696011.0189 | 1210982.5757 | 2696021.2938 | 1210981.7447 | 2696031.5892 | 1210979.1198 | 2696032.888 | 1210978.7912
85 | 2695784.6773 | 1210959.9383 | 2695838.5706 | 1210916.9781
86 | 2695816.6669 | 1211024.67 | 2695815.5948 | 1211023.2105 | 2695808.2932 | 1211016.4331 | 2695802.7775 | 1211009.1951 | 2695800.7669 | 1211001.8801 | 2695800.7415 | 1210990.2162 | 2695801.4237 | 1210981.3433 | 2695797.9501 | 1210971.8922 | 2695791.643 | 1210965.1863 | 2695784.6773 | 1210959.9383
87 | 2695833.0581 | 1211071.1349 | 2695829.1326 | 1211058.1185 | 2695828.6866 | 1211050.406 | 2695826.3556 | 1211040.3284 | 2695821.1657 | 1211030.7941 | 2695816.6669 | 1211024.67
88 | 2696167.3053 | 1211062.9742 | 2696178.1821 | 1211086.9634
89 | 2696164.2257 | 1211055.9976 | 2696167.3053 | 1211062.9742
90 | 2696167.3053 | 1211062.9742 | 2696162.9912 | 1211065.1506 | 2696153.2518 | 1211070.0636 | 2696143.646 | 1211074.9085
91 | 2696164.2257 | 1211055.9976 | 2696179.2636 | 1211047.7142
92 | 2696164.2257 | 1211055.9976 | 2696151.0312 | 1211027.9702
93 | 2696132.3171 | 1211080.6224 | 2696143.646 | 1211074.9085
94 | 2696132.3171 | 1211080.6224 | 2696100.7605 | 1211041.2609
95 | 2696132.3171 | 1211080.6224 | 2696132.0572 | 1211088.0106
96 | 2696100.4143 | 1211040.8291 | 2696100.7605 | 1211041.2609
97 | 2696130.0097 | 1211101.4264 | 2696131.6576 | 1211099.369 | 2696132.0572 | 1211088.0106
98 | 2696314.7838 | 1211014.7689 | 2696302.2516 | 1210994.2954
99 | 2696324.2476 | 1210949.4396 | 2696325.3793 | 1210956.2178
100 | 2696314.7838 | 1211014.7689 | 2696315.9368 | 1211016.6526
101 | 2696324.2476 | 1210949.4396 | 2696323.5775 | 1210945.4258 | 2696319.6203 | 1210938.2428
102 | 2696319.2905 | 1211022.1313 | 2696315.9368 | 1211016.6526
103 | 2695893.1253 | 1211097.338 | 2695884.819 | 1211090.3908 | 2695876.3336 | 1211087.7637 | 2695867.209 | 1211087.0722 | 2695864.8818 | 1211085.8004
104 | 2695833.0581 | 1211071.1349 | 2695840.85 | 1211077.6645 | 2695848.3683 | 1211079.4643 | 2695857.9645 | 1211082.0202 | 2695864.8818 | 1211085.8004
105 | 2695903.4289 | 1211131.7181 | 2695902.0899 | 1211115.2631 | 2695899.662 | 1211106.4959 | 2695894.3884 | 1211098.3945 | 2695893.1253 | 1211097.338
106 | 2695833.0581 | 1211071.1349 | 2695832.7677 | 1211080.2142 | 2695831.1224 | 1211087.0591 | 2695828.2908 | 1211092.5285 | 2695823.5984 | 1211096.4891 | 2695818.4826 | 1211099.3756 | 2695803.1765 | 1211104.5111 | 2695794.2097 | 1211106.7687
107 | 2695903.4289 | 1211131.7181 | 2695900.7893 | 1211132.3317 | 2695896.3888 | 1211134.6848 | 2695882.7346 | 1211149.5866 | 2695879.2357 | 1211154.4782 | 2695873.1181 | 1211164.3644
108 | 2695794.2097 | 1211106.7687 | 2695791.0962 | 1211107.5525 | 2695783.8472 | 1211107.9142 | 2695780.026 | 1211104.9619 | 2695777.0078 | 1211098.8649 | 2695771.4714 | 1211092.9164 | 2695764.1249 | 1211087.05 | 2695754.811 | 1211082.0527 | 2695745.7737 | 1211081.1292 | 2695734.4859 | 1211082.1488 | 2695726.2884 | 1211085.7888
109 | 2695873.1181 | 1211164.3644 | 2695861.0838 | 1211186.2971 | 2695859.0505 | 1211192.691 | 2695857.6893 | 1211199.8296 | 2695854.9603 | 1211221.6006 | 2695853.3799 | 1211229.6141 | 2695850.3433 | 1211236.7284
110 | 2695873.1181 | 1211164.3644 | 2695873.2218 | 1211154.6288
111 | 2695829.8188 | 1211251.0504 | 2695837.057 | 1211248.3758 | 2695843.88 | 1211244.7162 | 2695849.5337 | 1211238.6251 | 2695850.3433 | 1211236.7284
112 | 2696313.1881 | 1210926.5674 | 2696319.6203 | 1210938.2428
113 | 2696330.6491 | 1210914.4601 | 2696324.816 | 1210909.0399
114 | 2696324.816 | 1210909.0399 | 2696324.3358 | 1210908.5937
115 | 2696103.6302 | 1210839.8401 | 2696100.7299 | 1210824.5496
116 | 2696100.7299 | 1210824.5496 | 2696088.1967 | 1210830.1849
117 | 2696100.7299 | 1210824.5496 | 2696201.3549 | 1210750.6874
118 | 2696088.1967 | 1210830.1849 | 2696085.1851 | 1210834.0613 | 2696085.2534 | 1210839.2548
119 | 2696032.3405 | 1210644.9359 | 2696201.3549 | 1210750.6874
120 | 2696122.3876 | 1211103.4236 | 2696102.5357 | 1211102.9579
121 | 2696130.0097 | 1211101.4264 | 2696128.299 | 1211103.5622 | 2696122.3876 | 1211103.4236
122 | 2696086.7017 | 1211088.1149 | 2696095.1731 | 1211097.6357 | 2696102.5357 | 1211102.9579 | 2696102.5357 | 1211102.9579
123 | 2696102.5357 | 1211102.9579 | 2696107.727 | 1211196.7724
124 | 2696086.7017 | 1211088.1149 | 2696078.8343 | 1211079.2731
125 | 2696078.8343 | 1211079.2731 | 2696077.7649 | 1211078.0712
126 | 2696073.894 | 1211073.7208 | 2696077.7649 | 1211078.0712
127 | 2696087.2587 | 1211024.4198 | 2696100.4143 | 1211040.8291
128 | 2696087.2587 | 1211024.4198 | 2696083.4894 | 1211019.7181
129 | 2696073.894 | 1211073.7208 | 2696063.7041 | 1211062.2688
130 | 2696071.681 | 1211004.9891 | 2696083.4894 | 1211019.7181
131 | 2696071.2201 | 1211004.4142 | 2696071.681 | 1211004.9891
132 | 2696064.4784 | 1210996.0052 | 2696071.2201 | 1211004.4142
133 | 2696007.3539 | 1210619.2097 | 2696020.7917 | 1210637.2347 | 2696032.3405 | 1210644.9359
134 | 2696048.5302 | 1211045.2154 | 2696063.7041 | 1211062.2688
135 | 2696002.7787 | 1210613.0727 | 2696007.3539 | 1210619.2097
136 | 2696002.7787 | 1210613.0727 | 2695999.5357 | 1210608.662 | 2695996.6187 | 1210603.8085
137 | 2695984.4184 | 1210579.5367 | 2695990.3588 | 1210589.9238 | 2695996.0268 | 1210602.8238 | 2695996.6187 | 1210603.8085
138 | 2695979.9912 | 1210562.0491 | 2695980.918 | 1210573.4162 | 2695984.4184 | 1210579.5367
139 | 2695979.9912 | 1210562.0491 | 2695979.937 | 1210547.0046 | 2695979.6831 | 1210538.6949 | 2695973.3848 | 1210525.9754
140 | 2695979.9912 | 1210562.0491 | 2695993.1134 | 1210556.6899 | 2696011.2484 | 1210551.1001 | 2696011.5602 | 1210549.8199
141 | 2696011.5602 | 1210549.8199 | 2696037.5026 | 1210483.1428
142 | 2695962.8171 | 1210504.6337 | 2695973.3848 | 1210525.9754

## bus_geodata
| x | y | coords
0 | 2696368.7241 | 1211209.6618
1 | 2696362.1299 | 1211283.8801
2 | 2696265.1698 | 1211220.1541
3 | 2696400.5677 | 1211254.5142
4 | 2696252.6085 | 1211202.6574
5 | 2696251.1953 | 1211083.042
6 | 2696417.1256 | 1211105.8573
7 | 2696419.2371 | 1211197.0556
8 | 2696357.4539 | 1211075.1354
9 | 2696356.0367 | 1211031.2086
10 | 2696357.0389 | 1211025.1651
11 | 2696362.5757 | 1210996.8374
12 | 2696014.7439 | 1211093.4937
13 | 2696013.8175 | 1211092.3808
14 | 2696028.7327 | 1211110.2974
15 | 2696009.2792 | 1211086.9294
16 | 2696029.7829 | 1211111.559
17 | 2696000.0803 | 1211073.4601
18 | 2695998.5386 | 1211071.1342
19 | 2696171.5271 | 1210961.343
20 | 2696192.1996 | 1210953.7306
21 | 2696135.4009 | 1210974.2104
22 | 2696130.6858 | 1210984.7528
23 | 2696138.6981 | 1211001.7724
24 | 2696123.8632 | 1210966.6749
25 | 2696143.7848 | 1211012.5773
26 | 2696109.5529 | 1210880.4182
27 | 2696079.2483 | 1210976.8633
28 | 2695978.9927 | 1211038.2765
29 | 2695984.9166 | 1211053.3839
30 | 2695967.1565 | 1211019.1091
31 | 2695986.07 | 1211056.3255
32 | 2695964.3583 | 1211014.8093
33 | 2695986.9928 | 1211058.6787
34 | 2695963.0703 | 1211012.7676
35 | 2695987.813 | 1211087.131
36 | 2695964.7867 | 1210995.2223
37 | 2696228.2082 | 1211019.4738
38 | 2696217.2913 | 1211026.1065
39 | 2696253.2953 | 1211004.2318
40 | 2696205.644 | 1211033.183
41 | 2696266.8548 | 1210996.0686
42 | 2696263.4928 | 1211022.6839
43 | 2696245.1119 | 1210988.7094
44 | 2696199.753 | 1211036.428
45 | 2696213.8044 | 1211047.3269
46 | 2696293.5132 | 1210980.0197
47 | 2696272.79 | 1211039.5069
48 | 2696234.0988 | 1210967.8194
49 | 2696180.2166 | 1211047.1893
50 | 2696221.8443 | 1211061.262
51 | 2696301.9342 | 1210993.7769
52 | 2696305.1205 | 1210972.9961
53 | 2696288.575 | 1210970.3282
54 | 2696271.2268 | 1211045.0713
55 | 2695963.7908 | 1211118.0088
56 | 2695946.735 | 1211091.8803
57 | 2695984.3958 | 1211131.7091
58 | 2695939.5641 | 1211078.4863
59 | 2695986.1434 | 1211122.2974
60 | 2695979.784 | 1211147.8001
61 | 2695928.7227 | 1211059.9313
62 | 2695945.9312 | 1211170.0833
63 | 2695929.9953 | 1211154.5134
64 | 2696387.9136 | 1210951.7358
65 | 2696387.2955 | 1210960.8209
66 | 2696386.4797 | 1210946.7612
67 | 2696381.8101 | 1210971.8326
68 | 2696372.8024 | 1210932.2466
69 | 2696374.8276 | 1210980.2935
70 | 2696359.7943 | 1210930.1424
71 | 2696358.6737 | 1210930.079
72 | 2695975.2429 | 1210980.5289
73 | 2695981.2079 | 1210989.8052
74 | 2695995.4223 | 1210985.6128
75 | 2696011.0189 | 1210982.5757
76 | 2695838.5706 | 1210916.9781
77 | 2695784.6773 | 1210959.9383
78 | 2695816.6669 | 1211024.67
79 | 2696032.888 | 1210978.7912
80 | 2696229.4976 | 1211074.5268
81 | 2696260.7777 | 1211082.1614
82 | 2696178.1821 | 1211086.9634
83 | 2696167.3053 | 1211062.9742
84 | 2696164.2257 | 1211055.9976
85 | 2696143.646 | 1211074.9085
86 | 2696179.2636 | 1211047.7142
87 | 2696151.0312 | 1211027.9702
88 | 2696132.3171 | 1211080.6224
89 | 2696100.7605 | 1211041.2609
90 | 2696132.0572 | 1211088.0106
91 | 2696302.2516 | 1210994.2954
92 | 2696325.3793 | 1210956.2178
93 | 2696282.3226 | 1210958.0574
94 | 2696314.7838 | 1211014.7689
95 | 2696324.2476 | 1210949.4396
96 | 2696315.9368 | 1211016.6526
97 | 2696319.2905 | 1211022.1313
98 | 2695864.8818 | 1211085.8004
99 | 2695893.1253 | 1211097.338
100 | 2695833.0581 | 1211071.1349
101 | 2695903.4289 | 1211131.7181
102 | 2695794.2097 | 1211106.7687
103 | 2695873.1181 | 1211164.3644
104 | 2695726.2884 | 1211085.7888
105 | 2695850.3433 | 1211236.7284
106 | 2695873.2218 | 1211154.6288
107 | 2696319.6203 | 1210938.2428
108 | 2696313.1881 | 1210926.5674
109 | 2695829.8188 | 1211251.0504
110 | 2696330.6491 | 1210914.4601
111 | 2696324.816 | 1210909.0399
112 | 2696324.3358 | 1210908.5937
113 | 2696103.6302 | 1210839.8401
114 | 2696100.7299 | 1210824.5496
115 | 2696088.1967 | 1210830.1849
116 | 2696201.3549 | 1210750.6874
117 | 2696085.2534 | 1210839.2548
118 | 2696122.3876 | 1211103.4236
119 | 2696102.5358 | 1211102.9579
120 | 2696130.0097 | 1211101.4264
121 | 2696086.7017 | 1211088.1149
122 | 2696107.727 | 1211196.7724
123 | 2696078.8343 | 1211079.2731
124 | 2696077.7649 | 1211078.0712
125 | 2696100.4143 | 1211040.8291
126 | 2696087.2587 | 1211024.4198
127 | 2696073.894 | 1211073.7208
128 | 2696083.4894 | 1211019.7181
129 | 2696071.681 | 1211004.9891
130 | 2696071.2201 | 1211004.4143
131 | 2696032.3405 | 1210644.9359
132 | 2696063.7041 | 1211062.2688
133 | 2696048.5302 | 1211045.2154
134 | 2696064.4784 | 1210996.0052
135 | 2696007.3539 | 1210619.2097
136 | 2696002.7787 | 1210613.0727
137 | 2695996.6186 | 1210603.8085
138 | 2695984.4184 | 1210579.5367
139 | 2695979.9912 | 1210562.0491
140 | 2696011.5602 | 1210549.8199
141 | 2696037.5026 | 1210483.1428
142 | 2695973.3848 | 1210525.9754
143 | 2695962.8171 | 1210504.6337
144 | 2696164.2257 | 1211055.9976

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9871 | -0.089953 | 0.0052357 | 0.0013122
1 | 0.98563 | -0.10023 | 0 | 0
2 | 0.98937 | -0.074045 | 0.0019202 | 0.00048126
3 | 0.9847 | -0.10681 | 0 | 0
4 | 0.98985 | -0.07062 | 0.0089653 | 0.0022469
5 | 0.99309 | -0.048034 | 0.0014522 | 0.00036396
6 | 0.98111 | -0.13213 | 0.0009634 | 0.00024145
7 | 0.98351 | -0.11514 | 0.0035537 | 0.00089065
8 | 0.97766 | -0.15658 | 0.0015556 | 0.00038987
9 | 0.97551 | -0.17198 | 0.0016085 | 0.00040312
10 | 0.97522 | -0.17402 | 0.0013559 | 0.00033981
11 | 0.97393 | -0.18331 | 0.0018544 | 0.00046475
12 | 0.97936 | -0.14454 | 0.0017374 | 0.00043544
13 | 0.97937 | -0.14449 | 0.0022093 | 0.00055369
14 | 0.97931 | -0.14491 | 0.00085902 | 0.00021529
15 | 0.97943 | -0.14408 | 0.0028388 | 0.00071147
16 | 0.97931 | -0.14492 | 0.00076102 | 0.00019073
17 | 0.97963 | -0.14265 | 0.0016999 | 0.00042604
18 | 0.97967 | -0.14236 | 0.0015623 | 0.00039155
19 | 0.99786 | -0.014811 | 0.0032324 | 0.00081011
20 | 0.99777 | -0.015449 | 0.0028824 | 0.0007224
21 | 0.9982 | -0.012434 | 0 | 0
22 | 0.9983 | -0.011726 | 0 | 0
23 | 0.99896 | -0.0071828 | 0.0015121 | 0.00037898
24 | 0.99644 | -0.024602 | 0 | 0
25 | 0.99939 | -0.0042415 | 0.00097745 | 0.00024497
26 | 0.99479 | -0.03624 | 0.0031234 | 0.00078279
27 | 0.99281 | -0.049784 | 0.0017263 | 0.00043264
28 | 0.98127 | -0.13094 | 0.00042479 | 0.00010646
29 | 0.98029 | -0.13788 | 0.00049559 | 0.00012421
30 | 0.98265 | -0.12113 | 0.00053254 | 0.00013347
31 | 0.98011 | -0.13922 | 0.00049836 | 0.0001249
32 | 0.98297 | -0.11889 | 0.00054334 | 0.00013617
33 | 0.97996 | -0.14028 | 0 | 0
34 | 0.98312 | -0.11782 | 0.00067427 | 0.00016899
35 | 0.97874 | -0.14898 | 0.00092065 | 0.00023074
36 | 0.9844 | -0.10878 | 0.0015994 | 0.00040085
37 | 0.99374 | -0.04357 | 0.001888 | 0.00047319
38 | 0.99448 | -0.038423 | 0.0017239 | 0.00043204
39 | 0.99214 | -0.054865 | 0 | 0
40 | 0.99529 | -0.032703 | 0 | 0
41 | 0.9915 | -0.059392 | 0.0012693 | 0.00031811
42 | 0.99196 | -0.056159 | 0.0013621 | 0.00034137
43 | 0.99205 | -0.055534 | 0.0017559 | 0.00044008
44 | 0.99563 | -0.030335 | 0.0019422 | 0.00048676
45 | 0.99479 | -0.036173 | 0.0018741 | 0.0004697
46 | 0.99029 | -0.067908 | 0 | 0
47 | 0.99183 | -0.057073 | 0.0011939 | 0.00029923
48 | 0.99198 | -0.056013 | 0.0020002 | 0.0005013
49 | 0.99678 | -0.022348 | 0.0013906 | 0.00034853
50 | 0.99432 | -0.039494 | 0.0013733 | 0.00034418
51 | 0.99 | -0.069966 | 0.0029431 | 0.00073762
52 | 0.9901 | -0.069291 | 0.0019017 | 0.0004766
53 | 0.99022 | -0.068392 | 0.0018745 | 0.0004698
54 | 0.9918 | -0.057282 | 0.003492 | 0.00087518
55 | 0.97673 | -0.16336 | 0.0013374 | 0.00033519
56 | 0.97655 | -0.16465 | 0.00079715 | 0.00019979
57 | 0.97692 | -0.162 | 0 | 0
58 | 0.97648 | -0.16515 | 0.00073754 | 0.00018485
59 | 0.9773 | -0.15928 | 0.00055482 | 0.00013905
60 | 0.97638 | -0.16584 | 0.0016379 | 0.00041049
61 | 0.9764 | -0.16568 | 0.0023798 | 0.00059644
62 | 0.97494 | -0.17613 | 0.0011307 | 0.00028338
63 | 0.97432 | -0.18061 | 0.0013377 | 0.00033527
64 | 0.97193 | -0.19769 | 0.0019228 | 0.00048191
65 | 0.97221 | -0.19565 | 0.0025634 | 0.00064245
66 | 0.97178 | -0.19874 | 0.0015513 | 0.0003888
67 | 0.97264 | -0.19256 | 0.0022639 | 0.00056738
68 | 0.97124 | -0.20266 | 0.0043655 | 0.0010941
69 | 0.97306 | -0.18955 | 0.0026041 | 0.00065265
70 | 0.97098 | -0.20453 | 0.0017678 | 0.00044306
71 | 0.97096 | -0.20467 | 0.0033949 | 0.00085085
72 | 0.98551 | -0.10092 | 0.0015409 | 0.00038619
73 | 0.98554 | -0.10075 | 0 | 0
74 | 0.98654 | -0.093657 | 0.0020972 | 0.00052561
75 | 0.98767 | -0.085724 | 0.0014215 | 0.00035625
76 | 0.97032 | -0.20943 | 0.0016875 | 0.00042292
77 | 0.97049 | -0.2082 | 0.0053619 | 0.0013438
78 | 0.97129 | -0.20244 | 0.00085142 | 0.00021339
79 | 0.98929 | -0.074322 | 0.0011897 | 0.00029816
80 | 0.99387 | -0.042587 | 0.0012814 | 0.00032114
81 | 0.99307 | -0.048175 | 0.0014422 | 0.00036145
82 | 0.99723 | -0.019243 | 0.0015691 | 0.00039326
83 | 0.99729 | -0.018828 | 0 | 0
84 | 0.99775 | -0.015646 | 0 | 0
85 | 0.99577 | -0.029494 | 0.0018024 | 0.00045173
86 | 0.99684 | -0.021954 | 0.0016213 | 0.00040635
87 | 1 | 0 | -0.22988 | -0.057775
88 | 0.99507 | -0.034381 | 0 | 0
89 | 0.99396 | -0.042229 | 0.0029357 | 0.00073575
90 | 0.99483 | -0.036083 | 0.0035802 | 0.00089729
91 | 0.98999 | -0.070026 | 0.0032849 | 0.00082327
92 | 0.98978 | -0.071541 | 0.0025618 | 0.00064204
93 | 0.99017 | -0.068742 | 0.0024938 | 0.00062502
94 | 0.98978 | -0.071567 | 0.0027124 | 0.00067978
95 | 0.98972 | -0.071929 | 0.0010838 | 0.00027164
96 | 0.98976 | -0.071648 | 0.0020256 | 0.00050767
97 | 0.98975 | -0.07175 | 0.0015637 | 0.00039191
98 | 0.97236 | -0.19476 | 0.00081641 | 0.00020461
99 | 0.97282 | -0.19142 | 0.00055138 | 0.00013819
100 | 0.97187 | -0.19825 | 0 | 0
101 | 0.97339 | -0.18729 | 0 | 0
102 | 0.97176 | -0.19908 | 0 | 0
103 | 0.97292 | -0.1907 | 0 | 0
104 | 0.97161 | -0.20018 | 0.0013059 | 0.00032729
105 | 0.97237 | -0.19466 | 0.0014852 | 0.00037222
106 | 0.97289 | -0.19094 | 0.0022438 | 0.00056234
107 | 0.98965 | -0.072488 | 0.0022528 | 0.0005646
108 | 0.9896 | -0.072788 | 0.0022101 | 0.0005539
109 | 0.97224 | -0.19558 | 0.0033828 | 0.0008478
110 | 0.97056 | -0.20754 | 0.0039178 | 0.0009819
111 | 0.97051 | -0.2079 | 0.0029692 | 0.00074414
112 | 0.97051 | -0.20791 | 0.0013069 | 0.00032753
113 | 0.9942 | -0.040415 | 0 | 0
114 | 0.99397 | -0.042001 | 0 | 0
115 | 0.99395 | -0.042131 | 0 | 0
116 | 0.99234 | -0.053544 | 0.0017063 | 0.00042763
117 | 0.99394 | -0.042227 | 0.0009388 | 0.00023528
118 | 0.99425 | -0.040211 | 0.0019995 | 0.00050113
119 | 0.99384 | -0.04305 | 0.0010507 | 0.00026332
120 | 0.99445 | -0.038801 | 0.0030893 | 0.00077424
121 | 0.99345 | -0.045838 | 0.00073247 | 0.00018357
122 | 0.99378 | -0.043488 | 0.00045706 | 0.00011455
123 | 0.99325 | -0.047263 | 0.0022487 | 0.00056358
124 | 0.99322 | -0.04742 | 0.0013629 | 0.00034158
125 | 0.99395 | -0.042298 | 0.002991 | 0.00074963
126 | 0.99366 | -0.044314 | 0.0019808 | 0.00049644
127 | 0.99315 | -0.047908 | 0.0022811 | 0.00057169
128 | 0.9936 | -0.044771 | 0.002408 | 0.0006035
129 | 0.99346 | -0.045743 | 0.0020426 | 0.00051193
130 | 0.99346 | -0.045766 | 0.0015893 | 0.00039832
131 | 0.99022 | -0.068564 | 0.00051877 | 0.00013002
132 | 0.99302 | -0.04884 | 0.0026945 | 0.0006753
133 | 0.99291 | -0.049604 | 0.0033086 | 0.00082921
134 | 0.99344 | -0.045925 | 0.0014594 | 0.00036577
135 | 0.98986 | -0.071115 | 0.0010068 | 0.00025232
136 | 0.9898 | -0.071573 | 0 | 0
137 | 0.9897 | -0.07224 | 0.0010045 | 0.00025176
138 | 0.98951 | -0.07359 | 0.001469 | 0.00036815
139 | 0.98942 | -0.07423 | 0 | 0
140 | 0.98936 | -0.074672 | 0.00061824 | 0.00015495
141 | 0.9893 | -0.075133 | 0.00062943 | 0.00015775
142 | 0.98931 | -0.075049 | 0.00092734 | 0.00023241
143 | 0.98927 | -0.075343 | 0.0012083 | 0.00030283
144 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.040058 | 0.010099 | -0.040001 | -0.01008 | 5.7607e-05 | 1.925e-05 | 0.060408 | 0.060409 | 0.060409 | 0.9871 | -0.089953 | 0.98563 | -0.10023 | 7.4579
1 | -0.045294 | -0.011411 | 0.045395 | 0.011446 | 0.00010099 | 3.4843e-05 | 0.068301 | 0.068299 | 0.068301 | 0.9871 | -0.089953 | 0.98937 | -0.074045 | 8.4322
2 | 0.040001 | 0.01008 | -0.039964 | -0.010067 | 3.6813e-05 | 1.2306e-05 | 0.060409 | 0.06041 | 0.06041 | 0.98563 | -0.10023 | 0.9847 | -0.10681 | 7.458
3 | -0.047315 | -0.011927 | 0.047338 | 0.011935 | 2.2703e-05 | 7.9018e-06 | 0.071187 | 0.071187 | 0.071187 | 0.98937 | -0.074045 | 0.98985 | -0.07062 | 8.7886
4 | 0.039964 | 0.010067 | -0.039917 | -0.010052 | 4.652e-05 | 1.5556e-05 | 0.06041 | 0.06041 | 0.06041 | 0.9847 | -0.10681 | 0.98351 | -0.11514 | 7.4581
5 | -0.056303 | -0.014182 | 0.056482 | 0.014246 | 0.00017835 | 6.3968e-05 | 0.084664 | 0.084663 | 0.084664 | 0.98985 | -0.07062 | 0.99309 | -0.048034 | 10.4524
6 | 0.0014422 | 0.00036133 | -0.0014422 | -0.00036145 | 2.804e-08 | -1.1372e-07 | 0.0021609 | 0.002161 | 0.002161 | 0.99309 | -0.048034 | 0.99307 | -0.048175 | 0.80037
7 | -0.059376 | -0.014971 | 0.059422 | 0.014988 | 4.5355e-05 | 1.6375e-05 | 0.089 | 0.088999 | 0.089 | 0.99309 | -0.048034 | 0.99387 | -0.042587 | 10.9876
8 | -0.036277 | -0.0091303 | 0.036364 | 0.0091611 | 8.6203e-05 | 3.0845e-05 | 0.055035 | 0.055034 | 0.055035 | 0.98111 | -0.13213 | 0.98351 | -0.11514 | 10.1916
9 | 0.035314 | 0.0088888 | -0.035194 | -0.0088435 | 0.0001202 | 4.5387e-05 | 0.053573 | 0.053574 | 0.053574 | 0.98111 | -0.13213 | 0.97766 | -0.15658 | 19.8421
10 | 0.033638 | 0.0084536 | -0.033566 | -0.0084265 | 7.1909e-05 | 2.7108e-05 | 0.051206 | 0.051206 | 0.051206 | 0.97766 | -0.15658 | 0.97551 | -0.17198 | 18.9653
11 | 0.031958 | 0.0080234 | -0.031949 | -0.0080199 | 9.0858e-06 | 3.4181e-06 | 0.048753 | 0.048753 | 0.048753 | 0.97551 | -0.17198 | 0.97522 | -0.17402 | 18.0566
12 | 0.030593 | 0.0076801 | -0.030554 | -0.0076653 | 3.9394e-05 | 1.4791e-05 | 0.046684 | 0.046684 | 0.046684 | 0.97522 | -0.17402 | 0.97393 | -0.18331 | 17.2904
13 | 0.028699 | 0.0072006 | -0.028674 | -0.0071913 | 2.483e-05 | 9.2926e-06 | 0.043851 | 0.043851 | 0.043851 | 0.97393 | -0.18331 | 0.97306 | -0.18955 | 16.2411
14 | -0.0033575 | -0.0008412 | 0.0033576 | 0.00084119 | 2.3512e-08 | -9.1771e-09 | 0.0051013 | 0.0051013 | 0.0051013 | 0.97936 | -0.14454 | 0.97937 | -0.14449 | 1.8894
15 | 0.0016201 | 0.00040576 | -0.00162 | -0.000406 | 8.2667e-08 | -2.4332e-07 | 0.0024615 | 0.0024616 | 0.0024616 | 0.97936 | -0.14454 | 0.97931 | -0.14491 | 0.91169
16 | -0.0055668 | -0.0013949 | 0.0055671 | 0.0013949 | 3.1663e-07 | 3.2518e-08 | 0.0084579 | 0.0084579 | 0.0084579 | 0.97937 | -0.14449 | 0.97943 | -0.14408 | 3.1326
17 | 0.00076103 | 0.00019071 | -0.00076102 | -0.00019073 | 1.3696e-09 | -2.0127e-08 | 0.0011563 | 0.0011563 | 0.0011563 | 0.97931 | -0.14491 | 0.97931 | -0.14492 | 0.42828
18 | -0.0084059 | -0.0021064 | 0.0084076 | 0.0021068 | 1.661e-06 | 4.3341e-07 | 0.012771 | 0.012771 | 0.012771 | 0.97943 | -0.14408 | 0.97963 | -0.14265 | 4.7299
19 | -0.010108 | -0.0025328 | 0.010108 | 0.002533 | 4.1042e-07 | 1.2272e-07 | 0.015353 | 0.015353 | 0.015353 | 0.97963 | -0.14265 | 0.97967 | -0.14236 | 5.6862
20 | -0.01167 | -0.0029245 | 0.011674 | 0.0029256 | 3.358e-06 | 1.0758e-06 | 0.017726 | 0.017726 | 0.017726 | 0.97967 | -0.14236 | 0.97996 | -0.14028 | 6.5651
21 | 0.0028827 | 0.00072221 | -0.0028824 | -0.0007224 | 2.5471e-07 | -1.9058e-07 | 0.0042985 | 0.0042986 | 0.0042986 | 0.99786 | -0.014811 | 0.99777 | -0.015449 | 1.5921
22 | -0.0061151 | -0.0015323 | 0.0061171 | 0.0015326 | 2.0118e-06 | 2.6708e-07 | 0.0091187 | 0.0091185 | 0.0091187 | 0.99786 | -0.014811 | 0.9982 | -0.012434 | 3.3773
23 | -0.0061171 | -0.0015326 | 0.0061177 | 0.0015327 | 5.99e-07 | 7.945e-08 | 0.0091185 | 0.0091185 | 0.0091185 | 0.9982 | -0.012434 | 0.9983 | -0.011726 | 3.3772
24 | -0.073366 | -0.018518 | 0.073413 | 0.018535 | 4.683e-05 | 1.7273e-05 | 0.1094 | 0.1094 | 0.1094 | 0.9983 | -0.011726 | 0.99896 | -0.0071828 | 13.5063
25 | 0.067248 | 0.016985 | -0.067127 | -0.016939 | 0.00012153 | 4.6489e-05 | 0.10028 | 0.10028 | 0.10028 | 0.9983 | -0.011726 | 0.99644 | -0.024602 | 37.1418
26 | -0.074925 | -0.018914 | 0.074956 | 0.018925 | 3.0967e-05 | 1.1441e-05 | 0.11165 | 0.11165 | 0.11165 | 0.99896 | -0.0071828 | 0.99939 | -0.0042415 | 13.7844
27 | 0.013215 | 0.0033107 | -0.013194 | -0.0033037 | 2.1247e-05 | 7.0349e-06 | 0.019734 | 0.019734 | 0.019734 | 0.99644 | -0.024602 | 0.99479 | -0.03624 | 7.3089
28 | 0.053912 | 0.013628 | -0.053721 | -0.013555 | 0.00019053 | 7.2669e-05 | 0.080549 | 0.080549 | 0.080549 | 0.99644 | -0.024602 | 0.99281 | -0.049784 | 29.8331
29 | -0.075933 | -0.01917 | 0.075978 | 0.019187 | 4.5273e-05 | 1.6744e-05 | 0.11311 | 0.11311 | 0.11311 | 0.99939 | -0.0042415 | 1 | 0 | 13.964
30 | 0.01007 | 0.0025209 | -0.010064 | -0.0025192 | 5.8054e-06 | 1.7008e-06 | 0.015062 | 0.015062 | 0.015062 | 0.99479 | -0.03624 | 0.9942 | -0.040415 | 5.5786
31 | 0.051995 | 0.013123 | -0.051816 | -0.013054 | 0.0001785 | 6.8047e-05 | 0.077962 | 0.077962 | 0.077962 | 0.99281 | -0.049784 | 0.98929 | -0.074322 | 28.8749
32 | 0.041429 | 0.010404 | -0.041389 | -0.010389 | 3.9974e-05 | 1.517e-05 | 0.062831 | 0.062831 | 0.062831 | 0.98127 | -0.13094 | 0.98029 | -0.13788 | 23.2706
33 | -0.041853 | -0.01051 | 0.041911 | 0.010532 | 5.7122e-05 | 2.1683e-05 | 0.063475 | 0.063475 | 0.063475 | 0.98127 | -0.13094 | 0.98265 | -0.12113 | 23.5092
34 | 0.040893 | 0.010265 | -0.040886 | -0.010262 | 7.5981e-06 | 2.8825e-06 | 0.062078 | 0.062078 | 0.062078 | 0.98029 | -0.13788 | 0.98011 | -0.13922 | 22.992
35 | -0.042443 | -0.010666 | 0.042456 | 0.010671 | 1.3228e-05 | 5.0226e-06 | 0.064281 | 0.064281 | 0.064281 | 0.98265 | -0.12113 | 0.98297 | -0.11889 | 23.8078
36 | 0.040387 | 0.010137 | -0.040381 | -0.010135 | 5.9311e-06 | 2.2493e-06 | 0.061322 | 0.061322 | 0.061322 | 0.98011 | -0.13922 | 0.97996 | -0.14028 | 22.7118
37 | -0.043 | -0.010807 | 0.043006 | 0.010809 | 6.3883e-06 | 2.4264e-06 | 0.065104 | 0.065104 | 0.065104 | 0.98297 | -0.11889 | 0.98312 | -0.11782 | 24.1125
38 | 0.028708 | 0.0072089 | -0.028673 | -0.007196 | 3.4668e-05 | 1.2966e-05 | 0.043596 | 0.043596 | 0.043596 | 0.97996 | -0.14028 | 0.97874 | -0.14898 | 16.1468
39 | -0.04368 | -0.010978 | 0.043735 | 0.010999 | 5.5041e-05 | 2.0914e-05 | 0.066124 | 0.066124 | 0.066124 | 0.98312 | -0.11782 | 0.9844 | -0.10878 | 24.4904
40 | 0.027752 | 0.0069652 | -0.027713 | -0.0069504 | 3.9635e-05 | 1.4796e-05 | 0.042197 | 0.042197 | 0.042197 | 0.97874 | -0.14898 | 0.9773 | -0.15928 | 15.6284
41 | -0.045335 | -0.0114 | 0.045386 | 0.011419 | 5.0848e-05 | 1.9336e-05 | 0.068542 | 0.068542 | 0.068542 | 0.9844 | -0.10878 | 0.98554 | -0.10075 | 25.3858
42 | -0.039992 | -0.010035 | 0.04002 | 0.010046 | 2.8588e-05 | 1.083e-05 | 0.059887 | 0.059887 | 0.059887 | 0.99374 | -0.04357 | 0.99448 | -0.038423 | 22.1805
43 | 0.038104 | 0.009562 | -0.038044 | -0.0095395 | 5.9639e-05 | 2.2558e-05 | 0.05706 | 0.05706 | 0.05706 | 0.99374 | -0.04357 | 0.99214 | -0.054865 | 21.1335
44 | -0.041744 | -0.010478 | 0.041777 | 0.010491 | 3.3184e-05 | 1.2586e-05 | 0.062467 | 0.062467 | 0.062467 | 0.99448 | -0.038423 | 0.99529 | -0.032703 | 23.1358
45 | 0.028238 | 0.0070826 | -0.02822 | -0.007076 | 1.7716e-05 | 6.6094e-06 | 0.042353 | 0.042353 | 0.042353 | 0.99214 | -0.054865 | 0.9915 | -0.059392 | 15.6863
46 | 0.0060498 | 0.0015159 | -0.0060487 | -0.0015157 | 1.0831e-06 | 1.4436e-07 | 0.0090734 | 0.0090735 | 0.0090735 | 0.99214 | -0.054865 | 0.99196 | -0.056159 | 3.3606
47 | 0.0037566 | 0.00094103 | -0.0037563 | -0.00094113 | 3.4757e-07 | -9.2902e-08 | 0.0056341 | 0.0056341 | 0.0056341 | 0.99214 | -0.054865 | 0.99205 | -0.055534 | 2.0867
48 | -0.10581 | -0.026645 | 0.10585 | 0.026658 | 3.503e-05 | 1.3211e-05 | 0.15824 | 0.15824 | 0.15824 | 0.99529 | -0.032703 | 0.99563 | -0.030335 | 19.5361
49 | 0.064037 | 0.016154 | -0.064006 | -0.016143 | 3.1156e-05 | 1.1347e-05 | 0.095775 | 0.095776 | 0.095776 | 0.99529 | -0.032703 | 0.99479 | -0.036173 | 11.8242
50 | 0.026951 | 0.0067579 | -0.026919 | -0.006746 | 3.1767e-05 | 1.1817e-05 | 0.040448 | 0.040448 | 0.040448 | 0.9915 | -0.059392 | 0.99029 | -0.067908 | 14.9808
51 | 0.0046867 | 0.0011744 | -0.0046861 | -0.0011744 | 5.928e-07 | -2.0092e-08 | 0.0070303 | 0.0070304 | 0.0070304 | 0.99196 | -0.056159 | 0.99183 | -0.057073 | 2.6038
52 | 0.0020004 | 0.00050105 | -0.0020002 | -0.0005013 | 1.3266e-07 | -2.5386e-07 | 0.0030003 | 0.0030004 | 0.0030004 | 0.99205 | -0.055534 | 0.99198 | -0.056013 | 1.1113
53 | -0.10779 | -0.027145 | 0.10791 | 0.02719 | 0.00012047 | 4.5464e-05 | 0.16114 | 0.16114 | 0.16114 | 0.99563 | -0.030335 | 0.99678 | -0.022348 | 19.8944
54 | 0.062131 | 0.015673 | -0.062103 | -0.015663 | 2.8925e-05 | 1.0499e-05 | 0.092972 | 0.092973 | 0.092973 | 0.99479 | -0.036173 | 0.99432 | -0.039494 | 11.4781
55 | 0.012535 | 0.0031416 | -0.012531 | -0.0031404 | 3.5706e-06 | 1.1658e-06 | 0.018835 | 0.018835 | 0.018835 | 0.99029 | -0.067908 | 0.99 | -0.069966 | 6.9759
56 | 0.010015 | 0.0025098 | -0.010013 | -0.0025093 | 1.9173e-06 | 5.6289e-07 | 0.015049 | 0.015049 | 0.015049 | 0.99029 | -0.067908 | 0.9901 | -0.069291 | 5.5737
57 | 0.0043688 | 0.0010947 | -0.0043685 | -0.0010947 | 2.9248e-07 | -2.7441e-08 | 0.0065644 | 0.0065645 | 0.0065645 | 0.99029 | -0.067908 | 0.99022 | -0.068392 | 2.4313
58 | 0.0034921 | 0.00087514 | -0.003492 | -0.00087518 | 1.0135e-07 | -3.7382e-08 | 0.0052391 | 0.0052391 | 0.0052391 | 0.99183 | -0.057073 | 0.9918 | -0.057282 | 1.9404
59 | -0.1093 | -0.027539 | 0.10931 | 0.027541 | 6.0287e-06 | 2.2762e-06 | 0.16322 | 0.16322 | 0.16322 | 0.99678 | -0.022348 | 0.99684 | -0.021954 | 20.1507
60 | 0.060729 | 0.015318 | -0.060703 | -0.015309 | 2.633e-05 | 9.5314e-06 | 0.090917 | 0.090918 | 0.090918 | 0.99432 | -0.039494 | 0.99387 | -0.042587 | 11.2244
61 | 0.0095881 | 0.0024028 | -0.009588 | -0.0024028 | 7.8787e-08 | 2.2485e-08 | 0.014411 | 0.014411 | 0.014411 | 0.99 | -0.069966 | 0.98999 | -0.070026 | 5.3375
62 | 0.0081118 | 0.0020327 | -0.0081092 | -0.002032 | 2.5249e-06 | 6.2109e-07 | 0.012191 | 0.012191 | 0.012191 | 0.9901 | -0.069291 | 0.98978 | -0.071541 | 4.5152
63 | 0.002494 | 0.00062489 | -0.0024938 | -0.00062502 | 1.207e-07 | -1.3073e-07 | 0.0037476 | 0.0037477 | 0.0037477 | 0.99022 | -0.068392 | 0.99017 | -0.068742 | 1.388
64 | 0.0039156 | 0.00098064 | -0.0039149 | -0.00098076 | 6.9857e-07 | -1.2501e-07 | 0.0059651 | 0.0059652 | 0.0059652 | 0.97673 | -0.16336 | 0.97655 | -0.16465 | 2.2093
65 | -0.005253 | -0.0013158 | 0.005254 | 0.0013159 | 9.9065e-07 | 7.0693e-08 | 0.0080026 | 0.0080025 | 0.0080026 | 0.97673 | -0.16336 | 0.97692 | -0.162 | 2.9639
66 | 0.0031178 | 0.00078098 | -0.0031175 | -0.00078108 | 2.1395e-07 | -1.0778e-07 | 0.0047505 | 0.0047506 | 0.0047506 | 0.97655 | -0.16465 | 0.97648 | -0.16515 | 1.7595
67 | -0.027148 | -0.0068076 | 0.027158 | 0.0068114 | 1.0214e-05 | 3.8086e-06 | 0.041352 | 0.041352 | 0.041352 | 0.97692 | -0.162 | 0.9773 | -0.15928 | 15.3156
68 | 0.021894 | 0.0054917 | -0.021882 | -0.0054874 | 1.1659e-05 | 4.2739e-06 | 0.03335 | 0.03335 | 0.03335 | 0.97692 | -0.162 | 0.97638 | -0.16584 | 12.3517
69 | 0.00238 | 0.00059624 | -0.0023798 | -0.00059644 | 1.766e-07 | -2.0121e-07 | 0.0036267 | 0.0036268 | 0.0036268 | 0.97648 | -0.16515 | 0.9764 | -0.16568 | 1.3433
70 | 0.020244 | 0.0050769 | -0.020215 | -0.0050664 | 2.8843e-05 | 1.0487e-05 | 0.030853 | 0.030854 | 0.030854 | 0.97638 | -0.16584 | 0.97494 | -0.17613 | 11.4273
71 | 0.019085 | 0.004783 | -0.019073 | -0.0047788 | 1.183e-05 | 4.2714e-06 | 0.029128 | 0.029128 | 0.029128 | 0.97494 | -0.17613 | 0.97432 | -0.18061 | 10.7882
72 | 0.017735 | 0.0044435 | -0.017719 | -0.0044377 | 1.6374e-05 | 5.8527e-06 | 0.027085 | 0.027085 | 0.027085 | 0.97432 | -0.18061 | 0.97339 | -0.18729 | 10.0315
73 | -0.021216 | -0.0053188 | 0.021222 | 0.005321 | 5.9952e-06 | 2.193e-06 | 0.032482 | 0.032482 | 0.032482 | 0.97193 | -0.19769 | 0.97221 | -0.19565 | 12.0304
74 | 0.019293 | 0.0048369 | -0.01929 | -0.0048359 | 2.8187e-06 | 1.02e-06 | 0.029538 | 0.029538 | 0.029538 | 0.97193 | -0.19769 | 0.97178 | -0.19874 | 10.9401
75 | -0.023785 | -0.0059635 | 0.023795 | 0.0059672 | 1.0183e-05 | 3.764e-06 | 0.036405 | 0.036405 | 0.036405 | 0.97221 | -0.19565 | 0.97264 | -0.19256 | 13.4835
76 | 0.017739 | 0.0044471 | -0.017729 | -0.0044436 | 9.6287e-06 | 3.4444e-06 | 0.027163 | 0.027163 | 0.027163 | 0.97178 | -0.19874 | 0.97124 | -0.20266 | 10.0603
77 | -0.026059 | -0.0065346 | 0.02607 | 0.0065386 | 1.0881e-05 | 4.0487e-06 | 0.039869 | 0.039869 | 0.039869 | 0.97264 | -0.19256 | 0.97306 | -0.18955 | 14.7662
78 | 0.013364 | 0.0033495 | -0.01336 | -0.0033484 | 3.4594e-06 | 1.1669e-06 | 0.020475 | 0.020475 | 0.020475 | 0.97124 | -0.20266 | 0.97098 | -0.20453 | 7.5832
79 | 0.011592 | 0.0029053 | -0.011592 | -0.0029052 | 2.2105e-07 | 7.1136e-08 | 0.017765 | 0.017765 | 0.017765 | 0.97098 | -0.20453 | 0.97096 | -0.20467 | 6.5798
80 | 0.0081973 | 0.0020544 | -0.0081941 | -0.0020535 | 3.2548e-06 | 8.4325e-07 | 0.012563 | 0.012563 | 0.012563 | 0.97096 | -0.20467 | 0.97056 | -0.20754 | 4.6529
81 | -0.0015409 | -0.00038619 | 0.0015409 | 0.00038606 | 3.7252e-08 | -1.262e-07 | 0.0023266 | 0.0023266 | 0.0023266 | 0.98551 | -0.10092 | 0.98554 | -0.10075 | 0.86171
82 | -0.046927 | -0.011805 | 0.046973 | 0.011823 | 4.6444e-05 | 1.7674e-05 | 0.070868 | 0.070868 | 0.070868 | 0.98554 | -0.10075 | 0.98654 | -0.093657 | 26.2475
83 | -0.04907 | -0.012349 | 0.049125 | 0.012369 | 5.4394e-05 | 2.0718e-05 | 0.074031 | 0.074031 | 0.074031 | 0.98654 | -0.093657 | 0.98767 | -0.085724 | 27.419
84 | -0.050546 | -0.012726 | 0.050627 | 0.012756 | 8.0643e-05 | 3.0731e-05 | 0.076173 | 0.076173 | 0.076173 | 0.98767 | -0.085724 | 0.98929 | -0.074322 | 28.2122
85 | -0.0016875 | -0.00042292 | 0.0016877 | 0.00042217 | 2.8796e-07 | -7.4072e-07 | 0.0025878 | 0.0025874 | 0.0025878 | 0.97032 | -0.20943 | 0.97049 | -0.2082 | 0.95843
86 | -0.0070496 | -0.001766 | 0.0070552 | 0.0017672 | 5.6144e-06 | 1.2069e-06 | 0.010809 | 0.010808 | 0.010809 | 0.97049 | -0.2082 | 0.97129 | -0.20244 | 4.0032
87 | -0.0079066 | -0.0019806 | 0.0079112 | 0.0019817 | 4.5883e-06 | 1.144e-06 | 0.012113 | 0.012112 | 0.012113 | 0.97129 | -0.20244 | 0.97187 | -0.19825 | 4.4861
88 | -0.0015691 | -0.00039326 | 0.0015692 | 0.00039295 | 9.0096e-08 | -3.0902e-07 | 0.0023414 | 0.0023412 | 0.0023414 | 0.99723 | -0.019243 | 0.99729 | -0.018828 | 0.86717
89 | -0.04172 | -0.010469 | 0.041738 | 0.010476 | 1.8435e-05 | 6.9907e-06 | 0.062253 | 0.062253 | 0.062253 | 0.99729 | -0.018828 | 0.99775 | -0.015646 | 23.0568
90 | 0.040151 | 0.010076 | -0.040091 | -0.010054 | 5.9353e-05 | 2.2483e-05 | 0.059912 | 0.059912 | 0.059912 | 0.99729 | -0.018828 | 0.99577 | -0.029494 | 22.1897
91 | 0.11103 | 0.027984 | -0.11093 | -0.027947 | 9.7977e-05 | 3.7012e-05 | 0.16564 | 0.16564 | 0.16564 | 0.99775 | -0.015646 | 0.99684 | -0.021954 | 20.4494
92 | -0.15277 | -0.038461 | 0.1531 | 0.038588 | 0.00033464 | 0.00012749 | 0.22789 | 0.22789 | 0.22789 | 0.99775 | -0.015646 | 1 | 0 | 28.135
93 | 0.038289 | 0.009602 | -0.038263 | -0.0095922 | 2.5922e-05 | 9.805e-06 | 0.057219 | 0.057219 | 0.057219 | 0.99577 | -0.029494 | 0.99507 | -0.034381 | 21.1922
94 | 0.015428 | 0.0038679 | -0.015411 | -0.0038621 | 1.6756e-05 | 5.7899e-06 | 0.023071 | 0.023071 | 0.023071 | 0.99507 | -0.034381 | 0.99396 | -0.042229 | 8.5448
95 | 0.022836 | 0.0057243 | -0.02283 | -0.0057223 | 5.3793e-06 | 1.973e-06 | 0.034148 | 0.034148 | 0.034148 | 0.99507 | -0.034381 | 0.99483 | -0.036083 | 12.6475
96 | 0.012475 | 0.0031264 | -0.012475 | -0.0031263 | 1.2046e-07 | 3.9157e-08 | 0.018676 | 0.018676 | 0.018676 | 0.99396 | -0.042229 | 0.99395 | -0.042298 | 6.917
97 | 0.01925 | 0.004825 | -0.019243 | -0.0048224 | 7.2433e-06 | 2.6042e-06 | 0.028793 | 0.028793 | 0.028793 | 0.99483 | -0.036083 | 0.99445 | -0.038801 | 10.6641
98 | 0.0063031 | 0.0015795 | -0.0063018 | -0.0015793 | 1.3444e-06 | 2.0851e-07 | 0.0094739 | 0.009474 | 0.009474 | 0.98999 | -0.070026 | 0.98978 | -0.071567 | 3.5089
99 | 0.0055475 | 0.00139 | -0.0055472 | -0.00139 | 2.9826e-07 | 2.6395e-08 | 0.0083398 | 0.0083399 | 0.0083399 | 0.98978 | -0.071541 | 0.98972 | -0.071929 | 3.0888
100 | 0.0035894 | 0.00089949 | -0.0035894 | -0.00089951 | 4.013e-08 | -1.2949e-08 | 0.0053963 | 0.0053963 | 0.0053963 | 0.98978 | -0.071567 | 0.98976 | -0.071648 | 1.9986
101 | 0.0044633 | 0.0011183 | -0.004463 | -0.0011184 | 3.4477e-07 | -2.5069e-08 | 0.0067103 | 0.0067104 | 0.0067104 | 0.98972 | -0.071929 | 0.98965 | -0.072488 | 2.4853
102 | 0.0015637 | 0.00039183 | -0.0015637 | -0.00039191 | 2.2154e-08 | -7.4036e-08 | 0.0023509 | 0.002351 | 0.002351 | 0.98976 | -0.071648 | 0.98975 | -0.07175 | 0.87072
103 | -0.010038 | -0.0025133 | 0.010043 | 0.0025147 | 4.64e-06 | 1.3935e-06 | 0.015361 | 0.015361 | 0.015361 | 0.97236 | -0.19476 | 0.97282 | -0.19142 | 5.6892
104 | 0.0092219 | 0.0023087 | -0.0092175 | -0.0023074 | 4.4375e-06 | 1.264e-06 | 0.014112 | 0.014112 | 0.014112 | 0.97236 | -0.19476 | 0.97187 | -0.19825 | 5.2266
105 | -0.010594 | -0.0026529 | 0.0106 | 0.0026547 | 6.0491e-06 | 1.8679e-06 | 0.016204 | 0.016204 | 0.016204 | 0.97282 | -0.19142 | 0.97339 | -0.18729 | 6.0015
106 | 0.0013062 | 0.00032569 | -0.0013061 | -0.00032638 | 1.4868e-07 | -6.8127e-07 | 0.0019993 | 0.0019996 | 0.0019996 | 0.97187 | -0.19825 | 0.97176 | -0.19908 | 0.74059
107 | 0.0071182 | 0.0017829 | -0.0071149 | -0.0017822 | 3.3615e-06 | 7.2761e-07 | 0.010881 | 0.010881 | 0.010881 | 0.97339 | -0.18729 | 0.97292 | -0.1907 | 4.0301
108 | 0.0013061 | 0.00032638 | -0.0013059 | -0.00032729 | 1.986e-07 | -9.0943e-07 | 0.0019996 | 0.002 | 0.002 | 0.97176 | -0.19908 | 0.97161 | -0.20018 | 0.74073
109 | 0.004871 | 0.0012199 | -0.0048684 | -0.0012199 | 2.661e-06 | 6.9801e-08 | 0.0074496 | 0.0074499 | 0.0074499 | 0.97292 | -0.1907 | 0.97237 | -0.19466 | 2.7592
110 | 0.0022439 | 0.00056225 | -0.0022438 | -0.00056234 | 7.1551e-08 | -9.3383e-08 | 0.0034318 | 0.0034318 | 0.0034318 | 0.97292 | -0.1907 | 0.97289 | -0.19094 | 1.271
111 | 0.0033832 | 0.00084765 | -0.0033828 | -0.0008478 | 4.3206e-07 | -1.5421e-07 | 0.0051772 | 0.0051773 | 0.0051773 | 0.97237 | -0.19466 | 0.97224 | -0.19558 | 1.9175
112 | 0.0022102 | 0.00055377 | -0.0022101 | -0.0005539 | 9.1859e-08 | -1.3594e-07 | 0.0033232 | 0.0033232 | 0.0033232 | 0.98965 | -0.072488 | 0.9896 | -0.072788 | 1.2308
113 | 0.0042762 | 0.0010716 | -0.004276 | -0.0010717 | 2.1357e-07 | -1.6258e-08 | 0.0065561 | 0.0065561 | 0.0065561 | 0.97056 | -0.20754 | 0.97051 | -0.2079 | 2.4282
114 | 0.0013069 | 0.00032752 | -0.0013069 | -0.00032753 | 1.6421e-09 | -7.4683e-09 | 0.0020037 | 0.0020037 | 0.0020037 | 0.97051 | -0.2079 | 0.97051 | -0.20791 | 0.74212
115 | 0.010064 | 0.0025192 | -0.010062 | -0.0025186 | 2.2034e-06 | 6.4568e-07 | 0.015062 | 0.015062 | 0.015062 | 0.9942 | -0.040415 | 0.99397 | -0.042001 | 5.5787
116 | 0.00093882 | 0.00023499 | -0.00093881 | -0.00023516 | 1.6897e-08 | -1.712e-07 | 0.0014053 | 0.0014054 | 0.0014054 | 0.99397 | -0.042001 | 0.99395 | -0.042131 | 0.52052
117 | 0.0091234 | 0.0022836 | -0.0091089 | -0.0022796 | 1.4528e-05 | 3.9725e-06 | 0.013657 | 0.013658 | 0.013658 | 0.99397 | -0.042001 | 0.99234 | -0.053544 | 5.0584
118 | 0.00093881 | 0.00023516 | -0.0009388 | -0.00023528 | 1.2452e-08 | -1.2615e-07 | 0.0014054 | 0.0014055 | 0.0014055 | 0.99395 | -0.042131 | 0.99394 | -0.042227 | 0.52054
119 | 0.0074026 | 0.001852 | -0.0073873 | -0.0018486 | 1.5327e-05 | 3.3248e-06 | 0.011099 | 0.0111 | 0.0111 | 0.99234 | -0.053544 | 0.99022 | -0.068564 | 4.1111
120 | 0.014151 | 0.003546 | -0.014145 | -0.0035441 | 5.5575e-06 | 1.8801e-06 | 0.021178 | 0.021178 | 0.021178 | 0.99425 | -0.040211 | 0.99384 | -0.04305 | 7.8438
121 | -0.01615 | -0.0040471 | 0.016153 | 0.0040482 | 3.1532e-06 | 1.1006e-06 | 0.024171 | 0.024171 | 0.024171 | 0.99425 | -0.040211 | 0.99445 | -0.038801 | 8.9521
122 | 0.012637 | 0.0031674 | -0.012632 | -0.0031658 | 4.8766e-06 | 1.5928e-06 | 0.018921 | 0.018921 | 0.018921 | 0.99384 | -0.04305 | 0.99345 | -0.045838 | 7.0079
123 | 0.00045709 | 0.00011334 | -0.00045706 | -0.00011455 | 2.7442e-08 | -1.2069e-06 | 0.00068394 | 0.00068437 | 0.00068437 | 0.99384 | -0.04305 | 0.99378 | -0.043488 | 0.25347
124 | 0.0119 | 0.0029823 | -0.011898 | -0.0029815 | 2.3463e-06 | 7.4921e-07 | 0.017824 | 0.017824 | 0.017824 | 0.99345 | -0.045838 | 0.99325 | -0.047263 | 6.6016
125 | 0.009649 | 0.0024179 | -0.0096487 | -0.0024179 | 2.0978e-07 | 5.9861e-08 | 0.014455 | 0.014455 | 0.014455 | 0.99325 | -0.047263 | 0.99322 | -0.04742 | 5.3538
126 | 0.0082858 | 0.0020763 | -0.0082852 | -0.0020761 | 5.5992e-07 | 1.3999e-07 | 0.012413 | 0.012413 | 0.012413 | 0.99322 | -0.04742 | 0.99315 | -0.047908 | 4.5976
127 | 0.009484 | 0.0023767 | -0.0094814 | -0.0023759 | 2.6456e-06 | 7.4504e-07 | 0.014198 | 0.014198 | 0.014198 | 0.99395 | -0.042298 | 0.99366 | -0.044314 | 5.2586
128 | 0.0075006 | 0.0018795 | -0.0075001 | -0.0018794 | 4.7439e-07 | 1.044e-07 | 0.011232 | 0.011232 | 0.011232 | 0.99366 | -0.044314 | 0.9936 | -0.044771 | 4.16
129 | 0.0060042 | 0.0015044 | -0.0060034 | -0.0015043 | 7.7408e-07 | 9.9383e-08 | 0.0089958 | 0.0089958 | 0.0089958 | 0.99315 | -0.047908 | 0.99302 | -0.04884 | 3.3318
130 | 0.0050921 | 0.0012759 | -0.0050914 | -0.0012759 | 6.8505e-07 | 1.9008e-08 | 0.0076258 | 0.0076259 | 0.0076259 | 0.9936 | -0.044771 | 0.99346 | -0.045743 | 2.8244
131 | 0.0030488 | 0.00076395 | -0.0030488 | -0.00076396 | 9.5878e-09 | -5.8532e-09 | 0.0045664 | 0.0045664 | 0.0045664 | 0.99346 | -0.045743 | 0.99346 | -0.045766 | 1.6913
132 | 0.0014595 | 0.00036564 | -0.0014594 | -0.00036577 | 3.2137e-08 | -1.2719e-07 | 0.0021859 | 0.002186 | 0.002186 | 0.99346 | -0.045766 | 0.99344 | -0.045925 | 0.80963
133 | 0.0068685 | 0.0017186 | -0.0068661 | -0.0017182 | 2.4169e-06 | 4.6196e-07 | 0.01032 | 0.010321 | 0.010321 | 0.99022 | -0.068564 | 0.98986 | -0.071115 | 3.8224
134 | 0.0033089 | 0.00082905 | -0.0033086 | -0.00082921 | 3.5018e-07 | -1.6059e-07 | 0.0049582 | 0.0049584 | 0.0049584 | 0.99302 | -0.04884 | 0.99291 | -0.049604 | 1.8364
135 | 0.0058593 | 0.0014658 | -0.005859 | -0.0014658 | 3.705e-07 | 4.4108e-08 | 0.0088072 | 0.0088072 | 0.0088072 | 0.98986 | -0.071115 | 0.9898 | -0.071573 | 3.2619
136 | 0.005859 | 0.0014658 | -0.0058584 | -0.0014657 | 5.3906e-07 | 6.4199e-08 | 0.0088072 | 0.0088072 | 0.0088072 | 0.9898 | -0.071573 | 0.9897 | -0.07224 | 3.2619
137 | 0.0048539 | 0.001214 | -0.004853 | -0.001214 | 9.039e-07 | -1.8762e-09 | 0.0072969 | 0.0072971 | 0.0072971 | 0.9897 | -0.07224 | 0.98951 | -0.07359 | 2.7026
138 | 0.003384 | 0.00084583 | -0.0033837 | -0.00084595 | 2.9814e-07 | -1.2238e-07 | 0.0050881 | 0.0050881 | 0.0050881 | 0.98951 | -0.07359 | 0.98942 | -0.07423 | 1.8845
139 | 0.0021359 | 0.00053457 | -0.0021357 | -0.00053496 | 2.4177e-07 | -3.8924e-07 | 0.003212 | 0.0032122 | 0.0032122 | 0.98942 | -0.07423 | 0.98931 | -0.075049 | 1.1897
140 | 0.0012478 | 0.00031138 | -0.0012477 | -0.00031179 | 7.5712e-08 | -4.1354e-07 | 0.0018761 | 0.0018763 | 0.0018763 | 0.98942 | -0.07423 | 0.98936 | -0.074672 | 0.69491
141 | 0.00062947 | 0.00015685 | -0.00062943 | -0.00015775 | 4.0002e-08 | -9.0332e-07 | 0.00094641 | 0.00094674 | 0.00094674 | 0.98936 | -0.074672 | 0.9893 | -0.075133 | 0.35064
142 | 0.0012084 | 0.00030255 | -0.0012083 | -0.00030283 | 4.9086e-08 | -2.8689e-07 | 0.0018174 | 0.0018175 | 0.0018175 | 0.98931 | -0.075049 | 0.98927 | -0.075343 | 0.67315

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23168 | 0.058226

## res_load
| p_mw | q_mvar
0 | 0.0052357 | 0.0013122
1 | 0.0019202 | 0.00048126
2 | 0.0089653 | 0.0022469
3 | 0.0014522 | 0.00036396
4 | 0.0009634 | 0.00024145
5 | 0.0035537 | 0.00089065
6 | 0.0015556 | 0.00038987
7 | 0.0016085 | 0.00040312
8 | 0.0013559 | 0.00033981
9 | 0.0018544 | 0.00046475
10 | 0.0017374 | 0.00043544
11 | 0.0022093 | 0.00055369
12 | 0.00085902 | 0.00021529
13 | 0.0028388 | 0.00071147
14 | 0.00076102 | 0.00019073
15 | 0.0016999 | 0.00042604
16 | 0.0015623 | 0.00039155
17 | 0.0032324 | 0.00081011
18 | 0.0028824 | 0.0007224
19 | 0.0015121 | 0.00037898
20 | 0.00097745 | 0.00024497
21 | 0.0031234 | 0.00078279
22 | 0.0017263 | 0.00043264
23 | 0.00042479 | 0.00010646
24 | 0.00049559 | 0.00012421
25 | 0.00053254 | 0.00013347
26 | 0.00049836 | 0.0001249
27 | 0.00054334 | 0.00013617
28 | 0.00067427 | 0.00016899
29 | 0.00092065 | 0.00023074
30 | 0.0015994 | 0.00040085
31 | 0.001888 | 0.00047319
32 | 0.0017239 | 0.00043204
33 | 0.0012693 | 0.00031811
34 | 0.0013621 | 0.00034137
35 | 0.0017559 | 0.00044008
36 | 0.0019422 | 0.00048676
37 | 0.0018741 | 0.0004697
38 | 0.0011939 | 0.00029923
39 | 0.0020002 | 0.0005013
40 | 0.0013906 | 0.00034853
41 | 0.0013733 | 0.00034418
42 | 0.0029431 | 0.00073762
43 | 0.0019017 | 0.0004766
44 | 0.0018745 | 0.0004698
45 | 0.003492 | 0.00087518
46 | 0.0013374 | 0.00033519
47 | 0.00079715 | 0.00019979
48 | 0.00073754 | 0.00018485
49 | 0.00055482 | 0.00013905
50 | 0.0016379 | 0.00041049
51 | 0.0023798 | 0.00059644
52 | 0.0011307 | 0.00028338
53 | 0.0013377 | 0.00033527
54 | 0.0019228 | 0.00048191
55 | 0.0025634 | 0.00064245
56 | 0.0015513 | 0.0003888
57 | 0.0022639 | 0.00056738
58 | 0.0043655 | 0.0010941
59 | 0.0026041 | 0.00065265
60 | 0.0017678 | 0.00044306
61 | 0.0033949 | 0.00085085
62 | 0.0015409 | 0.00038619
63 | 0.0020972 | 0.00052561
64 | 0.0014215 | 0.00035625
65 | 0.0016875 | 0.00042292
66 | 0.0053619 | 0.0013438
67 | 0.00085142 | 0.00021339
68 | 0.0011897 | 0.00029816
69 | 0.0012814 | 0.00032114
70 | 0.0014422 | 0.00036145
71 | 0.0015691 | 0.00039326
72 | 0.0018024 | 0.00045173
73 | 0.0016213 | 0.00040635
74 | 0.0017989 | 0.00045084
75 | 0.0029357 | 0.00073575
76 | 0.0035802 | 0.00089729
77 | 0.0032849 | 0.00082327
78 | 0.0025618 | 0.00064204
79 | 0.0024938 | 0.00062502
80 | 0.0027124 | 0.00067978
81 | 0.0010838 | 0.00027164
82 | 0.0020256 | 0.00050767
83 | 0.0015637 | 0.00039191
84 | 0.00081641 | 0.00020461
85 | 0.00055138 | 0.00013819
86 | 0.0013059 | 0.00032729
87 | 0.0014852 | 0.00037222
88 | 0.0022438 | 0.00056234
89 | 0.0022528 | 0.0005646
90 | 0.0022101 | 0.0005539
91 | 0.0033828 | 0.0008478
92 | 0.0039178 | 0.0009819
93 | 0.0029692 | 0.00074414
94 | 0.0013069 | 0.00032753
95 | 0.0017063 | 0.00042763
96 | 0.0009388 | 0.00023528
97 | 0.0019995 | 0.00050113
98 | 0.0010507 | 0.00026332
99 | 0.0030893 | 0.00077424
100 | 0.00073247 | 0.00018357
101 | 0.00045706 | 0.00011455
102 | 0.0022487 | 0.00056358
103 | 0.0013629 | 0.00034158
104 | 0.002991 | 0.00074963
105 | 0.0019808 | 0.00049644
106 | 0.0022811 | 0.00057169
107 | 0.002408 | 0.0006035
108 | 0.0020426 | 0.00051193
109 | 0.0015893 | 0.00039832
110 | 0.00051877 | 0.00013002
111 | 0.0026945 | 0.0006753
112 | 0.0033086 | 0.00082921
113 | 0.0014594 | 0.00036577
114 | 0.0010068 | 0.00025232
115 | 0.0010045 | 0.00025176
116 | 0.001469 | 0.00036815
117 | 0.00061824 | 0.00015495
118 | 0.00062943 | 0.00015775
119 | 0.00092734 | 0.00023241
120 | 0.0012083 | 0.00030283

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1