## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1361-3_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1361-3_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1361-3_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1361-3_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1361-3_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1361-3_0_6_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1361-3_0_6_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1361-3_0_6_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1361-3_0_6_node_109 | 0.4 | n |  | TRUE
9 | bus_LV_1361-3_0_6_node_113 | 0.4 | n |  | TRUE
10 | bus_LV_1361-3_0_6_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1361-3_0_6_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1361-3_0_6_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1361-3_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1361-3_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1361-3_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1361-3_0_6_node_112 | 0.4 | n |  | TRUE
17 | bus_LV_1361-3_0_6_node_111 | 0.4 | n |  | TRUE
18 | bus_LV_1361-3_0_6_node_114 | 0.4 | n |  | TRUE
19 | bus_LV_1361-3_0_6_node_110 | 0.4 | n |  | TRUE
20 | bus_LV_1361-3_0_6_node_107 | 0.4 | n |  | TRUE
21 | bus_LV_1361-3_0_6_node_70 | 0.4 | n |  | TRUE
22 | bus_LV_1361-3_0_6_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1361-3_0_6_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_1361-3_0_6_node_54 | 0.4 | n |  | TRUE
25 | bus_LV_1361-3_0_6_node_50 | 0.4 | n |  | TRUE
26 | bus_LV_1361-3_0_6_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_1361-3_0_6_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1361-3_0_6_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_1361-3_0_6_node_56 | 0.4 | n |  | TRUE
30 | bus_LV_1361-3_0_6_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1361-3_0_6_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1361-3_0_6_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1361-3_0_6_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1361-3_0_6_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1361-3_0_6_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1361-3_0_6_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1361-3_0_6_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1361-3_0_6_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_1361-3_0_6_node_88 | 0.4 | n |  | TRUE
40 | bus_LV_1361-3_0_6_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_1361-3_0_6_node_95 | 0.4 | n |  | TRUE
42 | bus_LV_1361-3_0_6_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_1361-3_0_6_node_86 | 0.4 | n |  | TRUE
44 | bus_LV_1361-3_0_6_node_68 | 0.4 | n |  | TRUE
45 | bus_LV_1361-3_0_6_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_1361-3_0_6_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_1361-3_0_6_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_1361-3_0_6_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_1361-3_0_6_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_1361-3_0_6_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_1361-3_0_6_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_1361-3_0_6_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_1361-3_0_6_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1361-3_0_6_node_64 | 0.4 | n |  | TRUE
55 | bus_LV_1361-3_0_6_node_75 | 0.4 | n |  | TRUE
56 | bus_LV_1361-3_0_6_node_117 | 0.4 | n |  | TRUE
57 | bus_LV_1361-3_0_6_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_1361-3_0_6_node_66 | 0.4 | n |  | TRUE
59 | bus_LV_1361-3_0_6_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_1361-3_0_6_node_33 | 0.4 | n |  | TRUE
61 | bus_LV_1361-3_0_6_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_1361-3_0_6_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_1361-3_0_6_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_1361-3_0_6_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_1361-3_0_6_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_1361-3_0_6_node_82 | 0.4 | n |  | TRUE
67 | bus_LV_1361-3_0_6_node_96 | 0.4 | n |  | TRUE
68 | bus_LV_1361-3_0_6_node_80 | 0.4 | n |  | TRUE
69 | bus_LV_1361-3_0_6_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_1361-3_0_6_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_1361-3_0_6_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_1361-3_0_6_node_47 | 0.4 | n |  | TRUE
73 | bus_LV_1361-3_0_6_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_1361-3_0_6_node_53 | 0.4 | n |  | TRUE
75 | bus_LV_1361-3_0_6_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_1361-3_0_6_node_61 | 0.4 | n |  | TRUE
77 | bus_LV_1361-3_0_6_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_1361-3_0_6_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_1361-3_0_6_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_1361-3_0_6_node_62 | 0.4 | n |  | TRUE
81 | bus_LV_1361-3_0_6_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_1361-3_0_6_node_91 | 0.4 | n |  | TRUE
83 | bus_LV_1361-3_0_6_node_90 | 0.4 | n |  | TRUE
84 | bus_LV_1361-3_0_6_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_1361-3_0_6_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_1361-3_0_6_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_1361-3_0_6_node_97 | 0.4 | n |  | TRUE
88 | bus_LV_1361-3_0_6_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_1361-3_0_6_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_1361-3_0_6_node_98 | 0.4 | n |  | TRUE
91 | bus_LV_1361-3_0_6_node_103 | 0.4 | n |  | TRUE
92 | bus_LV_1361-3_0_6_node_78 | 0.4 | n |  | TRUE
93 | bus_LV_1361-3_0_6_node_79 | 0.4 | n |  | TRUE
94 | bus_LV_1361-3_0_6_node_81 | 0.4 | n |  | TRUE
95 | bus_LV_1361-3_0_6_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1361-3_0_6_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_1361-3_0_6_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_1361-3_0_6_node_92 | 0.4 | n |  | TRUE
99 | bus_LV_1361-3_0_6_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_1361-3_0_6_node_100 | 0.4 | n |  | TRUE
101 | bus_LV_1361-3_0_6_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_1361-3_0_6_node_85 | 0.4 | n |  | TRUE
103 | bus_LV_1361-3_0_6_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_1361-3_0_6_node_101 | 0.4 | n |  | TRUE
105 | bus_LV_1361-3_0_6_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_1361-3_0_6_node_104 | 0.4 | n |  | TRUE
107 | bus_LV_1361-3_0_6_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_1361-3_0_6_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_1361-3_0_6_node_108 | 0.4 | n |  | TRUE
110 | bus_LV_1361-3_0_6_node_115 | 0.4 | n |  | TRUE
111 | bus_LV_1361-3_0_6_node_116 | 0.4 | n |  | TRUE
112 | bus_MV_22_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1361-3_0_6_load_0 | 0 | 0.0013358 | 0.00033478 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1361-3_0_6_load_1 | 1 | 0.0059904 | 0.0015013 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1361-3_0_6_load_3 | 3 | 0.0043239 | 0.0010837 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1361-3_0_6_load_12 | 5 | 0.0014825 | 0.00037154 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1361-3_0_6_load_11 | 6 | 0.0050497 | 0.0012656 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1361-3_0_6_load_109 | 8 | 0.00651 | 0.0016316 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1361-3_0_6_load_113 | 9 | 0.0010229 | 0.00025636 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1361-3_0_6_load_5 | 11 | 0.0054304 | 0.001361 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1361-3_0_6_load_6 | 12 | 0.0026687 | 0.00066883 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1361-3_0_6_load_7 | 13 | 0.0018578 | 0.00046561 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1361-3_0_6_load_8 | 14 | 0.0012195 | 0.00030564 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1361-3_0_6_load_112 | 16 | 0.0014231 | 0.00035666 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1361-3_0_6_load_111 | 17 | 0.003515 | 0.00088093 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1361-3_0_6_load_114 | 18 | 0.0045237 | 0.0011338 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1361-3_0_6_load_110 | 19 | 0.0012413 | 0.00031111 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1361-3_0_6_load_14 | 22 | 0.00046602 | 0.0001168 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1361-3_0_6_load_51 | 23 | 0.00017518 | 4.3904e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1361-3_0_6_load_50 | 25 | 0.00064256 | 0.00016104 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1361-3_0_6_load_45 | 26 | 0.0015254 | 0.0003823 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1361-3_0_6_load_43 | 28 | 0.0020307 | 0.00050895 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1361-3_0_6_load_56 | 29 | 0.0031739 | 0.00079546 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1361-3_0_6_load_17 | 30 | 0.0010269 | 0.00025737 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1361-3_0_6_load_18 | 31 | 0.00071144 | 0.0001783 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1361-3_0_6_load_19 | 32 | 0.0014477 | 0.00036282 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1361-3_0_6_load_21 | 34 | 0.0010388 | 0.00026035 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1361-3_0_6_load_22 | 35 | 0.0010181 | 0.00025515 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1361-3_0_6_load_23 | 36 | 0.00071472 | 0.00017913 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1361-3_0_6_load_24 | 37 | 0.0017458 | 0.00043754 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1361-3_0_6_load_67 | 40 | 0.0013818 | 0.00034631 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1361-3_0_6_load_95 | 41 | 0.00055606 | 0.00013936 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1361-3_0_6_load_36 | 42 | 0.0053772 | 0.0013476 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1361-3_0_6_load_86 | 43 | 0.0033439 | 0.00083807 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1361-3_0_6_load_68 | 44 | 0.0015395 | 0.00038583 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1361-3_0_6_load_25 | 45 | 0.0001625 | 4.0725e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1361-3_0_6_load_26 | 46 | 0.0002546 | 6.3809e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1361-3_0_6_load_28 | 48 | 0.00044401 | 0.00011128 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1361-3_0_6_load_29 | 49 | 0.0005036 | 0.00012621 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1361-3_0_6_load_32 | 51 | 0.00050421 | 0.00012637 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1361-3_0_6_load_30 | 52 | 0.00036164 | 9.0636e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1361-3_0_6_load_48 | 53 | 0.00032491 | 8.1431e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1361-3_0_6_load_64 | 54 | 0.00075502 | 0.00018923 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1361-3_0_6_load_75 | 55 | 0.0016574 | 0.00041539 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1361-3_0_6_load_117 | 56 | 0.0019626 | 0.00049187 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1361-3_0_6_load_49 | 57 | 0.0012642 | 0.00031684 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1361-3_0_6_load_66 | 58 | 0.00016314 | 4.0886e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1361-3_0_6_load_33 | 60 | 0.0020112 | 0.00050405 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1361-3_0_6_load_34 | 61 | 0.0021183 | 0.0005309 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1361-3_0_6_load_37 | 63 | 0.0029984 | 0.00075148 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1361-3_0_6_load_38 | 64 | 0.0016743 | 0.00041963 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1361-3_0_6_load_41 | 65 | 0.0080107 | 0.0020077 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1361-3_0_6_load_82 | 66 | 0.0026303 | 0.00065921 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1361-3_0_6_load_96 | 67 | 0.00616 | 0.0015439 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1361-3_0_6_load_80 | 68 | 0.00064299 | 0.00016115 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1361-3_0_6_load_42 | 69 | 0.0018603 | 0.00046624 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1361-3_0_6_load_44 | 70 | 0.001689 | 0.00042331 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1361-3_0_6_load_46 | 71 | 0.0020555 | 0.00051516 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1361-3_0_6_load_47 | 72 | 0.0010683 | 0.00026774 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1361-3_0_6_load_52 | 73 | 0.00083172 | 0.00020845 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1361-3_0_6_load_53 | 74 | 0.00031874 | 7.9884e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1361-3_0_6_load_61 | 76 | 0.002396 | 0.00060049 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1361-3_0_6_load_57 | 77 | 0.00055634 | 0.00013943 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1361-3_0_6_load_58 | 78 | 0.00061796 | 0.00015488 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1361-3_0_6_load_60 | 79 | 0.001005 | 0.00025188 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1361-3_0_6_load_62 | 80 | 0.0011858 | 0.00029719 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1361-3_0_6_load_63 | 81 | 0.0018086 | 0.00045327 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1361-3_0_6_load_91 | 82 | 0.001168 | 0.00029272 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1361-3_0_6_load_90 | 83 | 0.00054746 | 0.00013721 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1361-3_0_6_load_71 | 84 | 0.0015739 | 0.00039445 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1361-3_0_6_load_72 | 85 | 0.0034144 | 0.00085573 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1361-3_0_6_load_69 | 86 | 0.017 | 0.0042606 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1361-3_0_6_load_97 | 87 | 0.0027441 | 0.00068774 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1361-3_0_6_load_73 | 89 | 0.0091712 | 0.0022985 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1361-3_0_6_load_98 | 90 | 0.0019569 | 0.00049045 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1361-3_0_6_load_103 | 91 | 0.0025407 | 0.00063677 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1361-3_0_6_load_78 | 92 | 0.0026439 | 0.00066262 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1361-3_0_6_load_79 | 93 | 0.00098183 | 0.00024607 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1361-3_0_6_load_83 | 95 | 0.0015748 | 0.00039469 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1361-3_0_6_load_99 | 97 | 0.00086891 | 0.00021777 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1361-3_0_6_load_92 | 98 | 0.001012 | 0.00025364 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1361-3_0_6_load_89 | 99 | 0.0011522 | 0.00028878 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1361-3_0_6_load_100 | 100 | 0.0015418 | 0.0003864 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1361-3_0_6_load_93 | 101 | 0.0020265 | 0.0005079 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1361-3_0_6_load_85 | 102 | 0.0040082 | 0.0010046 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1361-3_0_6_load_87 | 103 | 0.0019059 | 0.00047766 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1361-3_0_6_load_101 | 104 | 0.001614 | 0.00040451 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1361-3_0_6_load_102 | 105 | 0.0017706 | 0.00044376 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1361-3_0_6_load_104 | 106 | 0.0021636 | 0.00054226 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1361-3_0_6_load_105 | 107 | 0.0007273 | 0.00018228 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1361-3_0_6_load_106 | 108 | 0.00089428 | 0.00022413 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1361-3_0_6_load_108 | 109 | 0.0028934 | 0.00072516 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1361-3_0_6_load_115 | 110 | 0.0047495 | 0.0011903 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1361-3_0_6_load_116 | 111 | 0.006052 | 0.0015168 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1361-3_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.030616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1361-3_0_6_line_1 | NAYY 4x150 SE | 1 | 2 | 0.040402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1361-3_0_6_line_2 | NAYY 4x150 SE | 2 | 3 | 0.080447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1361-3_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.02227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1361-3_0_6_line_4 | NAYY 4x150 SE | 3 | 5 | 0.024348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1361-3_0_6_line_5 | NAYY 4x150 SE | 4 | 6 | 0.014769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1361-3_0_6_line_6 | NAYY 4x150 SE | 6 | 10 | 0.027148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1361-3_0_6_line_7 | NAYY 4x150 SE | 7 | 8 | 0.031586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1361-3_0_6_line_8 | NAYY 4x150 SE | 7 | 9 | 0.017763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1361-3_0_6_line_9 | NAYY 4x150 SE | 8 | 20 | 0.026742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1361-3_0_6_line_10 | NAYY 4x150 SE | 9 | 21 | 0.028731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1361-3_0_6_line_11 | NAYY 4x150 SE | 10 | 15 | 0.051104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1361-3_0_6_line_12 | NAYY 4x150 SE | 10 | 13 | 0.032637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1361-3_0_6_line_13 | NAYY 4x150 SE | 11 | 12 | 0.034442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1361-3_0_6_line_14 | NAYY 4x150 SE | 11 | 13 | 0.013478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1361-3_0_6_line_15 | NAYY 4x150 SE | 12 | 14 | 0.015301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1361-3_0_6_line_16 | NAYY 4x150 SE | 15 | 16 | 0.034533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1361-3_0_6_line_17 | NAYY 4x150 SE | 15 | 17 | 0.016487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1361-3_0_6_line_18 | NAYY 4x150 SE | 16 | 18 | 0.0081815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1361-3_0_6_line_19 | NAYY 4x150 SE | 17 | 19 | 0.0026856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1361-3_0_6_line_20 | NAYY 4x150 SE | 18 | 110 | 0.024816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1361-3_0_6_line_21 | NAYY 4x150 SE | 19 | 109 | 0.025643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1361-3_0_6_line_22 | NAYY 4x150 SE | 20 | 109 | 0.0043759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1361-3_0_6_line_23 | NAYY 4x150 SE | 20 | 108 | 0.014873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1361-3_0_6_line_24 | NAYY 4x150 SE | 21 | 86 | 0.033919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1361-3_0_6_line_25 | NAYY 4x150 SE | 22 | 23 | 0.15635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1361-3_0_6_line_26 | NAYY 4x150 SE | 23 | 24 | 0.14683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1361-3_0_6_line_27 | NAYY 4x150 SE | 23 | 25 | 0.13211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1361-3_0_6_line_28 | NAYY 4x150 SE | 24 | 29 | 0.087774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1361-3_0_6_line_29 | NAYY 4x150 SE | 24 | 27 | 0.047878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1361-3_0_6_line_30 | NAYY 4x150 SE | 25 | 73 | 0.18984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1361-3_0_6_line_31 | NAYY 4x150 SE | 26 | 27 | 0.14865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1361-3_0_6_line_32 | NAYY 4x150 SE | 26 | 28 | 0.019343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1361-3_0_6_line_33 | NAYY 4x150 SE | 28 | 69 | 0.0017487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1361-3_0_6_line_34 | NAYY 4x150 SE | 30 | 31 | 0.0061097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1361-3_0_6_line_35 | NAYY 4x150 SE | 30 | 32 | 0.046825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1361-3_0_6_line_36 | NAYY 4x150 SE | 31 | 33 | 0.012747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_1361-3_0_6_line_37 | NAYY 4x150 SE | 32 | 34 | 0.00039359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1361-3_0_6_line_38 | NAYY 4x150 SE | 33 | 35 | 0.023901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1361-3_0_6_line_39 | NAYY 4x150 SE | 33 | 36 | 0.018841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1361-3_0_6_line_40 | NAYY 4x150 SE | 34 | 37 | 0.0012069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1361-3_0_6_line_41 | NAYY 4x150 SE | 35 | 38 | 0.022724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1361-3_0_6_line_42 | NAYY 4x150 SE | 36 | 39 | 0.099618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1361-3_0_6_line_43 | NAYY 4x150 SE | 37 | 40 | 0.019549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_1361-3_0_6_line_44 | NAYY 4x150 SE | 38 | 41 | 0.018761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1361-3_0_6_line_45 | NAYY 4x150 SE | 38 | 42 | 0.0087796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_1361-3_0_6_line_46 | NAYY 4x150 SE | 39 | 43 | 0.046997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1361-3_0_6_line_47 | NAYY 4x150 SE | 40 | 44 | 0.013962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1361-3_0_6_line_48 | NAYY 4x150 SE | 41 | 67 | 0.12468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1361-3_0_6_line_49 | NAYY 4x150 SE | 42 | 61 | 0.026379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1361-3_0_6_line_50 | NAYY 4x150 SE | 43 | 102 | 0.024828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1361-3_0_6_line_51 | NAYY 4x150 SE | 44 | 84 | 0.0011011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1361-3_0_6_line_52 | NAYY 4x150 SE | 45 | 46 | 0.023733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1361-3_0_6_line_53 | NAYY 4x150 SE | 45 | 47 | 0.090283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1361-3_0_6_line_54 | NAYY 4x150 SE | 46 | 48 | 0.11189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1361-3_0_6_line_55 | NAYY 4x150 SE | 47 | 49 | 0.16171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1361-3_0_6_line_56 | NAYY 4x150 SE | 47 | 50 | 0.15862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1361-3_0_6_line_57 | NAYY 4x150 SE | 48 | 52 | 0.010123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1361-3_0_6_line_58 | NAYY 4x150 SE | 50 | 51 | 0.082607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1361-3_0_6_line_59 | NAYY 4x150 SE | 51 | 58 | 0.1025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1361-3_0_6_line_60 | NAYY 4x150 SE | 51 | 54 | 0.029773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1361-3_0_6_line_61 | NAYY 4x150 SE | 52 | 53 | 0.019051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1361-3_0_6_line_62 | NAYY 4x150 SE | 53 | 57 | 0.021641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1361-3_0_6_line_63 | NAYY 4x150 SE | 55 | 56 | 0.21209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1361-3_0_6_line_64 | NAYY 4x150 SE | 56 | 57 | 0.35649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1361-3_0_6_line_65 | NAYY 4x150 SE | 58 | 59 | 0.11359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1361-3_0_6_line_66 | NAYY 4x150 SE | 59 | 74 | 0.069575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1361-3_0_6_line_67 | NAYY 4x150 SE | 60 | 61 | 0.0018427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_1361-3_0_6_line_68 | NAYY 4x150 SE | 60 | 62 | 0.019034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_1361-3_0_6_line_69 | NAYY 4x150 SE | 62 | 63 | 0.02709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1361-3_0_6_line_70 | NAYY 4x150 SE | 62 | 64 | 0.016146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
71 | LV_1361-3_0_6_line_71 | NAYY 4x150 SE | 64 | 65 | 0.0087156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_1361-3_0_6_line_72 | NAYY 4x150 SE | 65 | 66 | 0.041198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_1361-3_0_6_line_73 | NAYY 4x150 SE | 66 | 68 | 0.057757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_1361-3_0_6_line_74 | NAYY 4x150 SE | 68 | 92 | 0.026285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_1361-3_0_6_line_75 | NAYY 4x150 SE | 69 | 70 | 0.021348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_1361-3_0_6_line_76 | NAYY 4x150 SE | 70 | 71 | 0.0035551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1361-3_0_6_line_77 | NAYY 4x150 SE | 71 | 72 | 0.017304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_1361-3_0_6_line_78 | NAYY 4x150 SE | 72 | 75 | 0.017843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_1361-3_0_6_line_79 | NAYY 4x150 SE | 73 | 74 | 0.064439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1361-3_0_6_line_80 | NAYY 4x150 SE | 75 | 76 | 0.012673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_1361-3_0_6_line_81 | NAYY 4x150 SE | 75 | 77 | 0.010192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1361-3_0_6_line_82 | NAYY 4x150 SE | 76 | 81 | 0.042215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1361-3_0_6_line_83 | NAYY 4x150 SE | 77 | 78 | 0.015891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1361-3_0_6_line_84 | NAYY 4x150 SE | 78 | 79 | 0.010486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1361-3_0_6_line_85 | NAYY 4x150 SE | 79 | 80 | 0.0023337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1361-3_0_6_line_86 | NAYY 4x150 SE | 81 | 82 | 0.047462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_1361-3_0_6_line_87 | NAYY 4x150 SE | 82 | 83 | 0.015597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1361-3_0_6_line_88 | NAYY 4x150 SE | 83 | 99 | 0.015064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_1361-3_0_6_line_89 | NAYY 4x150 SE | 84 | 85 | 0.022404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1361-3_0_6_line_90 | NAYY 4x150 SE | 85 | 89 | 0.021287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1361-3_0_6_line_91 | NAYY 4x150 SE | 87 | 88 | 0.024578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1361-3_0_6_line_92 | NAYY 4x150 SE | 88 | 90 | 0.00074927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1361-3_0_6_line_93 | NAYY 4x150 SE | 88 | 89 | 0.03909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
94 | LV_1361-3_0_6_line_94 | NAYY 4x150 SE | 90 | 91 | 0.01627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1361-3_0_6_line_95 | NAYY 4x150 SE | 91 | 105 | 0.018206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1361-3_0_6_line_96 | NAYY 4x150 SE | 92 | 93 | 0.026298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1361-3_0_6_line_97 | NAYY 4x150 SE | 93 | 94 | 0.053345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_1361-3_0_6_line_98 | NAYY 4x150 SE | 94 | 95 | 0.023948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1361-3_0_6_line_99 | NAYY 4x150 SE | 94 | 96 | 0.089953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1361-3_0_6_line_100 | NAYY 4x150 SE | 95 | 97 | 0.022131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1361-3_0_6_line_101 | NAYY 4x150 SE | 96 | 98 | 0.063493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1361-3_0_6_line_102 | NAYY 4x150 SE | 96 | 99 | 0.011989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_1361-3_0_6_line_103 | NAYY 4x150 SE | 97 | 100 | 0.0061507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1361-3_0_6_line_104 | NAYY 4x150 SE | 98 | 101 | 0.010452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1361-3_0_6_line_105 | NAYY 4x150 SE | 101 | 104 | 0.012459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1361-3_0_6_line_106 | NAYY 4x150 SE | 102 | 103 | 0.0082034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1361-3_0_6_line_107 | NAYY 4x150 SE | 105 | 106 | 0.013045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1361-3_0_6_line_108 | NAYY 4x150 SE | 106 | 107 | 0.0019686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1361-3_0_6_line_109 | NAYY 4x150 SE | 107 | 108 | 0.013829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1361-3_0_6_line_110 | NAYY 4x150 SE | 110 | 111 | 0.0023183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1361-3_0_6_trafo_22 | 0.25 MVA 20/0.4 kV | 112 | 35 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2697157.2525 | 1214224.7351 | 2697155.4798 | 1214222.83 | 2697149.3016 | 1214215.9801 | 2697137.669 | 1214201.2252
1 | 2697115.888 | 1214167.3022 | 2697122.934 | 1214180.5706 | 2697134.5429 | 1214197.2601 | 2697137.669 | 1214201.2252
2 | 2697115.888 | 1214167.3022 | 2697114.46 | 1214161.2303 | 2697113.4817 | 1214155.9996 | 2697112.9454 | 1214151.6212 | 2697112.882 | 1214148.051 | 2697113.1452 | 1214144.4861 | 2697113.7334 | 1214141.0267 | 2697114.7144 | 1214137.6959 | 2697116.538 | 1214133.4782 | 2697121.0221 | 1214125.4234 | 2697126.6147 | 1214117.876 | 2697128.8907 | 1214112.4649 | 2697130.5009 | 1214103.1624 | 2697134.075 | 1214092.68 | 2697134.5302 | 1214092.0753
3 | 2697097.1489 | 1214179.3276 | 2697098.6908 | 1214178.4076 | 2697111.393 | 1214169.4971 | 2697115.888 | 1214167.3022
4 | 2697151.9849 | 1214075.9479 | 2697143.2685 | 1214080.4658 | 2697134.5302 | 1214092.0753
5 | 2697097.1489 | 1214179.3276 | 2697085.0992 | 1214187.8674
6 | 2697062.9495 | 1214203.5653 | 2697085.0992 | 1214187.8674
7 | 2697061.7485 | 1214093.5474 | 2697033.3643 | 1214107.4034
8 | 2697061.7485 | 1214093.5474 | 2697055.298 | 1214081.0115 | 2697054.465 | 1214077.4421
9 | 2697009.333 | 1214119.1344 | 2697033.3643 | 1214107.4034
10 | 2697049.7925 | 1214049.1665 | 2697050.9379 | 1214062.3276 | 2697054.465 | 1214077.4421
11 | 2697032.2345 | 1214162.6594 | 2697062.9495 | 1214203.5653
12 | 2697062.9495 | 1214203.5653 | 2697081.926 | 1214230.1184
13 | 2697089.7629 | 1214241.0844 | 2697093.75 | 1214246.6633 | 2697107.8733 | 1214270.3582
14 | 2697089.7629 | 1214241.0844 | 2697081.926 | 1214230.1184
15 | 2697107.8733 | 1214270.3582 | 2697107.9913 | 1214270.5562 | 2697115.4758 | 1214283.6364
16 | 2697032.2345 | 1214162.6594 | 2697023.4731 | 1214171.6786 | 2697016.5256 | 1214180.3382 | 2697022.8747 | 1214189.1451
17 | 2697032.2345 | 1214162.6594 | 2697027.8896 | 1214155.1724 | 2697024.3047 | 1214148.2104
18 | 2697027.6592 | 1214195.7818 | 2697022.8747 | 1214189.1451
19 | 2697023.0753 | 1214145.8227 | 2697024.3047 | 1214148.2104
20 | 2697027.6592 | 1214195.7818 | 2697030.0385 | 1214199.0822 | 2697040.8331 | 1214216.8002
21 | 2697023.0753 | 1214145.8227 | 2697011.3362 | 1214123.0249
22 | 2697009.333 | 1214119.1344 | 2697011.3362 | 1214123.0249
23 | 2697009.333 | 1214119.1344 | 2697002.1747 | 1214106.0975
24 | 2697049.7925 | 1214049.1665 | 2697048.7683 | 1214037.4195 | 2697048.4047 | 1214027.0953 | 2697048.8167 | 1214015.3058
25 | 2696729.883 | 1213013.3407 | 2696873.7914 | 1212952.2176
26 | 2696788.3595 | 1213147.7729 | 2696750.1523 | 1213069.9326 | 2696739.9559 | 1213042.7819 | 2696730.5344 | 1213015.6326 | 2696729.883 | 1213013.3407
27 | 2696701.6693 | 1212884.4023 | 2696705.9126 | 1212912.4066 | 2696721.5714 | 1212984.0988 | 2696729.883 | 1213013.3407
28 | 2696788.3595 | 1213147.7729 | 2696783.8952 | 1213149.913 | 2696777.3597 | 1213150.9299 | 2696770.7787 | 1213150.5451 | 2696761.8989 | 1213148.0771 | 2696747.9709 | 1213143.4702 | 2696741.1007 | 1213144.048 | 2696736.8093 | 1213146.3022 | 2696728.4866 | 1213151.6375 | 2696719.5491 | 1213152.7267 | 2696712.1587 | 1213151.6505 | 2696704.644 | 1213149.3382
29 | 2696788.3595 | 1213147.7729 | 2696789.5877 | 1213150.2723 | 2696792.9209 | 1213157.4313 | 2696796.731 | 1213165.6322 | 2696798.2222 | 1213168.7808 | 2696807.9858 | 1213188.8642 | 2696809.0231 | 1213190.9603
30 | 2696701.6693 | 1212884.4023 | 2696684.0278 | 1212695.3821
31 | 2696744.9995 | 1213325.1211 | 2696809.0231 | 1213190.9603
32 | 2696744.9995 | 1213325.1211 | 2696745.6088 | 1213329.7047 | 2696749.2912 | 1213343.9555
33 | 2696749.7287 | 1213345.6486 | 2696749.2912 | 1213343.9555
34 | 2696919.4246 | 1213892.8102 | 2696918.1603 | 1213886.8327
35 | 2696919.4246 | 1213892.8102 | 2696924.8204 | 1213918.3212 | 2696930.4247 | 1213938.2999
36 | 2696915.5226 | 1213874.362 | 2696918.1603 | 1213886.8327
37 | 2696930.531 | 1213938.6789 | 2696930.4247 | 1213938.2999
38 | 2696915.5226 | 1213874.362 | 2696914.8587 | 1213861.4645 | 2696915.0578 | 1213850.4801
39 | 2696915.5226 | 1213874.362 | 2696897.4098 | 1213879.5494
40 | 2696930.531 | 1213938.6789 | 2696930.857 | 1213939.8409
41 | 2696916.5531 | 1213827.8132 | 2696915.1545 | 1213845.1469 | 2696915.0578 | 1213850.4801
42 | 2696872.542 | 1213963.4585 | 2696874.3564 | 1213946.2428 | 2696871.8912 | 1213922.642 | 2696870.7327 | 1213899.9741 | 2696880.879 | 1213884.2837 | 2696897.4098 | 1213879.5494
43 | 2696930.857 | 1213939.8409 | 2696934.8156 | 1213953.9528 | 2696936.3237 | 1213958.6065
44 | 2696916.5531 | 1213827.8132 | 2696901.2738 | 1213818.1137 | 2696900.857 | 1213817.5986
45 | 2696916.5531 | 1213827.8132 | 2696917.2573 | 1213819.0619
46 | 2696872.542 | 1213963.4585 | 2696890.1886 | 1214001.3492 | 2696891.7982 | 1214006.292
47 | 2696936.3237 | 1213958.6065 | 2696940.6279 | 1213971.8888
48 | 2696855.5401 | 1213702.6466 | 2696870.8995 | 1213762.126 | 2696894.5191 | 1213809.7649 | 2696900.857 | 1213817.5986
49 | 2696917.2573 | 1213819.0619 | 2696919.373 | 1213792.7678
50 | 2696899.4857 | 1214029.8998 | 2696891.7982 | 1214006.292
51 | 2696940.9674 | 1213972.9363 | 2696940.6279 | 1213971.8888
52 | 2696341.2515 | 1212689.8632 | 2696341.2515 | 1212689.8632 | 2696343.0135 | 1212685.2107 | 2696341.9371 | 1212677.9995 | 2696339.7474 | 1212670.092 | 2696339.3564 | 1212666.8533
53 | 2696284.543 | 1212602.9433 | 2696288.0574 | 1212611.6394 | 2696292.2612 | 1212618.1117 | 2696296.7529 | 1212624.6331 | 2696302.8211 | 1212629.5233 | 2696320.3307 | 1212636.8778 | 2696326.3965 | 1212639.0884 | 2696330.1996 | 1212642.1408 | 2696334.9426 | 1212647.6879 | 2696337.8777 | 1212654.6067 | 2696339.3564 | 1212666.8533
54 | 2696328.866 | 1212752.7569 | 2696329.0641 | 1212752.3649 | 2696328.0914 | 1212743.91 | 2696301.2571 | 1212692.4636 | 2696304.6417 | 1212685.2021 | 2696341.2515 | 1212689.8632
55 | 2696284.543 | 1212602.9433 | 2696282.3505 | 1212604.1421 | 2696280.0762 | 1212605.2284 | 2696273.7125 | 1212605.4591 | 2696267.9681 | 1212604.0432 | 2696253.4542 | 1212599.3836 | 2696243.4826 | 1212597.1767 | 2696234.2318 | 1212595.5041 | 2696228.7597 | 1212593.6923 | 2696225.9611 | 1212590.545 | 2696217.5779 | 1212575.6106 | 2696213.058 | 1212572.2354 | 2696205.7869 | 1212571.2508 | 2696199.2897 | 1212571.2793 | 2696190.7649 | 1212573.5879 | 2696177.7375 | 1212579.9266 | 2696143.9168 | 1212600.6289
56 | 2696421.0204 | 1212522.1146 | 2696284.543 | 1212602.9433
57 | 2696328.866 | 1212752.7569 | 2696327.0076 | 1212756.4345 | 2696321.1367 | 1212757.685 | 2696321.1367 | 1212757.685
58 | 2696421.0204 | 1212522.1146 | 2696422.083 | 1212524.5335 | 2696425.1387 | 1212526.8178 | 2696430.4504 | 1212528.6827 | 2696443.7219 | 1212531.2323 | 2696449.8174 | 1212531.142 | 2696456.9565 | 1212530.4236 | 2696467.3015 | 1212528.345 | 2696471.8959 | 1212528.0413 | 2696478.0645 | 1212529.5421 | 2696483.3594 | 1212532.4409 | 2696486.4805 | 1212536.3162 | 2696491.0339 | 1212546.5686
59 | 2696491.0339 | 1212546.5686 | 2696580.5924 | 1212496.7232
60 | 2696499.3579 | 1212574.94 | 2696498.882 | 1212569.6064 | 2696497.2103 | 1212562.5634 | 2696495.3441 | 1212556.2734 | 2696491.0339 | 1212546.5686
61 | 2696305.1225 | 1212747.8129 | 2696312.1136 | 1212750.4009 | 2696321.1367 | 1212757.685
62 | 2696286.4468 | 1212737.2108 | 2696297.604 | 1212745.0296 | 2696305.1225 | 1212747.8129
63 | 2695866.3871 | 1212992.2862 | 2696075.9476 | 1213024.9141
64 | 2696286.4468 | 1212737.2108 | 2696075.9476 | 1213024.9141
65 | 2696580.5924 | 1212496.7232 | 2696673.7153 | 1212561.7654
66 | 2696673.7153 | 1212561.7654 | 2696679.0692 | 1212631.1346
67 | 2696919.5207 | 1213790.931 | 2696919.373 | 1213792.7678
68 | 2696921.0473 | 1213771.9587 | 2696919.5207 | 1213790.931
69 | 2696921.0473 | 1213771.9587 | 2696947.9895 | 1213774.7817
70 | 2696921.0473 | 1213771.9587 | 2696921.8161 | 1213755.8309
71 | 2696922.2312 | 1213747.1252 | 2696921.8161 | 1213755.8309
72 | 2696922.2312 | 1213747.1252 | 2696922.4079 | 1213743.4167 | 2696920.4717 | 1213705.9816 | 2696920.4717 | 1213705.9816
73 | 2696920.4717 | 1213705.9816 | 2696913.8527 | 1213648.6055
74 | 2696910.8405 | 1213622.4939 | 2696913.8527 | 1213648.6055
75 | 2696749.7287 | 1213345.6486 | 2696755.0697 | 1213366.3179
76 | 2696755.9592 | 1213369.7599 | 2696755.0697 | 1213366.3179
77 | 2696755.9592 | 1213369.7599 | 2696760.2883 | 1213386.5133
78 | 2696764.7523 | 1213403.7887 | 2696760.2883 | 1213386.5133
79 | 2696684.0278 | 1212695.3821 | 2696679.0692 | 1212631.1346
80 | 2696764.7523 | 1213403.7887 | 2696770.6236 | 1213404.818 | 2696777.325 | 1213405.2042
81 | 2696764.7523 | 1213403.7887 | 2696754.6939 | 1213402.1435
82 | 2696819.4132 | 1213408.3351 | 2696804.7349 | 1213406.784 | 2696777.325 | 1213405.2042
83 | 2696754.6939 | 1213402.1435 | 2696739.0115 | 1213399.5785
84 | 2696739.0115 | 1213399.5785 | 2696728.6626 | 1213397.8858
85 | 2696726.3595 | 1213397.5091 | 2696728.6626 | 1213397.8858
86 | 2696819.4132 | 1213408.3351 | 2696836.0664 | 1213410.095 | 2696850.477 | 1213427.0407 | 2696857.0984 | 1213432.3245
87 | 2696857.0984 | 1213432.3245 | 2696869.2897 | 1213442.0531
88 | 2696882.5953 | 1213448.928 | 2696872.025 | 1213444.2358 | 2696869.2897 | 1213442.0531
89 | 2696940.9674 | 1213972.9363 | 2696944.5087 | 1213983.8644 | 2696948.3956 | 1213994.0649
90 | 2696948.3956 | 1213994.0649 | 2696955.9751 | 1214013.9563
91 | 2696972.6468 | 1214049.2449 | 2696994.9508 | 1214038.919
92 | 2696972.9938 | 1214049.909 | 2696972.6468 | 1214049.2449
93 | 2696972.6468 | 1214049.2449 | 2696960.7558 | 1214026.5025 | 2696955.9751 | 1214013.9563
94 | 2696972.9938 | 1214049.909 | 2696980.529 | 1214064.3292
95 | 2696988.8171 | 1214080.5388 | 2696982.3273 | 1214067.7707 | 2696980.529 | 1214064.3292
96 | 2696910.8405 | 1213622.4939 | 2696907.8267 | 1213596.3695
97 | 2696901.7983 | 1213543.3658 | 2696906.0093 | 1213580.6155 | 2696907.8267 | 1213596.3695
98 | 2696901.7983 | 1213543.3658 | 2696924.7325 | 1213536.4728
99 | 2696893.5528 | 1213453.7921 | 2696896.3394 | 1213485.6705 | 2696901.7983 | 1213543.3658
100 | 2696924.7325 | 1213536.4728 | 2696945.9265 | 1213530.1029
101 | 2696893.5528 | 1213453.7921 | 2696891.1697 | 1213425.1336 | 2696888.3776 | 1213409.0105 | 2696882.7103 | 1213391.5342
102 | 2696893.5528 | 1213453.7921 | 2696882.5953 | 1213448.928
103 | 2696951.8276 | 1213528.3685 | 2696946.1938 | 1213530.0225 | 2696945.9265 | 1213530.1029
104 | 2696882.7103 | 1213391.5342 | 2696879.486 | 1213381.5916 | 2696879.486 | 1213381.5916
105 | 2696875.465 | 1213369.799 | 2696879.486 | 1213381.5916
106 | 2696902.0258 | 1214037.7 | 2696899.4857 | 1214029.8998
107 | 2696988.8171 | 1214080.5388 | 2696994.7277 | 1214092.1674
108 | 2696995.6197 | 1214093.9224 | 2696994.7277 | 1214092.1674
109 | 2697002.1747 | 1214106.0975 | 2696997.2406 | 1214097.1113 | 2696995.6197 | 1214093.9224
110 | 2697042.0393 | 1214218.78 | 2697040.8331 | 1214216.8002

## bus_geodata
| x | y | coords
0 | 2697157.2525 | 1214224.7351
1 | 2697137.669 | 1214201.2252
2 | 2697115.888 | 1214167.3022
3 | 2697134.5302 | 1214092.0753
4 | 2697097.1489 | 1214179.3276
5 | 2697151.9849 | 1214075.9479
6 | 2697085.0992 | 1214187.8674
7 | 2697061.7485 | 1214093.5474
8 | 2697033.3643 | 1214107.4034
9 | 2697054.465 | 1214077.4421
10 | 2697062.9495 | 1214203.5653
11 | 2697089.7629 | 1214241.0844
12 | 2697107.8733 | 1214270.3582
13 | 2697081.926 | 1214230.1184
14 | 2697115.4758 | 1214283.6364
15 | 2697032.2345 | 1214162.6594
16 | 2697022.8747 | 1214189.1451
17 | 2697024.3047 | 1214148.2104
18 | 2697027.6592 | 1214195.7818
19 | 2697023.0753 | 1214145.8227
20 | 2697009.333 | 1214119.1344
21 | 2697049.7925 | 1214049.1665
22 | 2696873.7914 | 1212952.2176
23 | 2696729.883 | 1213013.3407
24 | 2696788.3595 | 1213147.7729
25 | 2696701.6693 | 1212884.4023
26 | 2696744.9995 | 1213325.1211
27 | 2696809.0231 | 1213190.9603
28 | 2696749.2912 | 1213343.9555
29 | 2696704.644 | 1213149.3382
30 | 2696919.4246 | 1213892.8102
31 | 2696918.1603 | 1213886.8327
32 | 2696930.4247 | 1213938.2999
33 | 2696915.5226 | 1213874.362
34 | 2696930.531 | 1213938.6789
35 | 2696915.0578 | 1213850.4801
36 | 2696897.4098 | 1213879.5494
37 | 2696930.857 | 1213939.8409
38 | 2696916.5531 | 1213827.8132
39 | 2696872.542 | 1213963.4585
40 | 2696936.3237 | 1213958.6065
41 | 2696900.857 | 1213817.5986
42 | 2696917.2573 | 1213819.0619
43 | 2696891.7982 | 1214006.292
44 | 2696940.6279 | 1213971.8888
45 | 2696339.3564 | 1212666.8533
46 | 2696341.2515 | 1212689.8632
47 | 2696284.543 | 1212602.9433
48 | 2696328.866 | 1212752.7569
49 | 2696143.9168 | 1212600.6289
50 | 2696421.0204 | 1212522.1146
51 | 2696491.0339 | 1212546.5686
52 | 2696321.1367 | 1212757.685
53 | 2696305.1225 | 1212747.8129
54 | 2696499.3579 | 1212574.94
55 | 2695866.3871 | 1212992.2862
56 | 2696075.9476 | 1213024.9141
57 | 2696286.4468 | 1212737.2108
58 | 2696580.5924 | 1212496.7232
59 | 2696673.7153 | 1212561.7654
60 | 2696919.5207 | 1213790.931
61 | 2696919.373 | 1213792.7678
62 | 2696921.0473 | 1213771.9587
63 | 2696947.9895 | 1213774.7817
64 | 2696921.8161 | 1213755.8309
65 | 2696922.2312 | 1213747.1252
66 | 2696920.4717 | 1213705.9816
67 | 2696855.5401 | 1213702.6466
68 | 2696913.8527 | 1213648.6055
69 | 2696749.7287 | 1213345.6486
70 | 2696755.0697 | 1213366.3179
71 | 2696755.9592 | 1213369.7599
72 | 2696760.2883 | 1213386.5133
73 | 2696684.0278 | 1212695.3821
74 | 2696679.0692 | 1212631.1346
75 | 2696764.7523 | 1213403.7887
76 | 2696777.325 | 1213405.2042
77 | 2696754.6939 | 1213402.1435
78 | 2696739.0115 | 1213399.5785
79 | 2696728.6626 | 1213397.8858
80 | 2696726.3595 | 1213397.5091
81 | 2696819.4132 | 1213408.3351
82 | 2696857.0984 | 1213432.3245
83 | 2696869.2897 | 1213442.0531
84 | 2696940.9674 | 1213972.9363
85 | 2696948.3956 | 1213994.0649
86 | 2697048.8167 | 1214015.3058
87 | 2696994.9508 | 1214038.919
88 | 2696972.6468 | 1214049.2449
89 | 2696955.9751 | 1214013.9563
90 | 2696972.9938 | 1214049.909
91 | 2696980.529 | 1214064.3292
92 | 2696910.8405 | 1213622.4939
93 | 2696907.8267 | 1213596.3695
94 | 2696901.7983 | 1213543.3658
95 | 2696924.7325 | 1213536.4728
96 | 2696893.5528 | 1213453.7921
97 | 2696945.9265 | 1213530.1029
98 | 2696882.7103 | 1213391.5342
99 | 2696882.5953 | 1213448.928
100 | 2696951.8276 | 1213528.3685
101 | 2696879.486 | 1213381.5916
102 | 2696899.4857 | 1214029.8998
103 | 2696902.0258 | 1214037.7
104 | 2696875.465 | 1213369.799
105 | 2696988.8171 | 1214080.5388
106 | 2696994.7277 | 1214092.1674
107 | 2696995.6197 | 1214093.9224
108 | 2697002.1747 | 1214106.0975
109 | 2697011.3362 | 1214123.0249
110 | 2697040.8331 | 1214216.8002
111 | 2697042.0393 | 1214218.78
112 | 2696916.5531 | 1213827.8132

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97112 | -0.20325 | 0.0013358 | 0.00033478
1 | 0.97118 | -0.20282 | 0.0059904 | 0.0015013
2 | 0.97161 | -0.19968 | 0 | 0
3 | 0.97093 | -0.20463 | 0.0043239 | 0.0010837
4 | 0.97204 | -0.19659 | 0 | 0
5 | 0.97087 | -0.20501 | 0.0014825 | 0.00037154
6 | 0.97232 | -0.19454 | 0.0050497 | 0.0012656
7 | 0.97702 | -0.16086 | 0 | 0
8 | 0.97786 | -0.15491 | 0.00651 | 0.0016316
9 | 0.97656 | -0.16421 | 0.0010229 | 0.00025636
10 | 0.97305 | -0.18933 | 0 | 0
11 | 0.97233 | -0.1945 | 0.0054304 | 0.001361
12 | 0.97213 | -0.19592 | 0.0026687 | 0.00066883
13 | 0.97251 | -0.19318 | 0.0018578 | 0.00046561
14 | 0.97211 | -0.19611 | 0.0012195 | 0.00030564
15 | 0.97525 | -0.17353 | 0 | 0
16 | 0.9744 | -0.1796 | 0.0014231 | 0.00035666
17 | 0.97636 | -0.16555 | 0.003515 | 0.00088093
18 | 0.97422 | -0.18092 | 0.0045237 | 0.0011338
19 | 0.97656 | -0.16416 | 0.0012413 | 0.00031111
20 | 0.97881 | -0.14807 | 0 | 0
21 | 0.97584 | -0.16933 | 0 | 0
22 | 0.98515 | -0.10523 | 0.00046602 | 0.0001168
23 | 0.98525 | -0.10446 | 0.00017518 | 4.3904e-05
24 | 0.98602 | -0.098916 | 0 | 0
25 | 0.9846 | -0.10915 | 0.00064256 | 0.00016104
26 | 0.98736 | -0.089335 | 0.0015254 | 0.0003823
27 | 0.98635 | -0.096583 | 0 | 0
28 | 0.9875 | -0.088291 | 0.0020307 | 0.00050895
29 | 0.98562 | -0.10178 | 0.0031739 | 0.00079546
30 | 0.99752 | -0.017075 | 0.0010269 | 0.00025737
31 | 0.99786 | -0.014756 | 0.00071144 | 0.0001783
32 | 0.99496 | -0.034733 | 0.0014477 | 0.00036282
33 | 0.99856 | -0.0098939 | 0 | 0
34 | 0.99494 | -0.03488 | 0.0010388 | 0.00026035
35 | 1 | 0 | -0.20712 | -0.052038
36 | 0.99829 | -0.011779 | 0.00071472 | 0.00017913
37 | 0.99488 | -0.035327 | 0.0017458 | 0.00043754
38 | 0.99914 | -0.006024 | 0 | 0
39 | 0.99697 | -0.021039 | 0 | 0
40 | 0.99385 | -0.042447 | 0.0013818 | 0.00034631
41 | 0.99896 | -0.0072863 | 0.00055606 | 0.00013936
42 | 0.99883 | -0.008157 | 0.0053772 | 0.0013476
43 | 0.99635 | -0.025414 | 0.0033439 | 0.00083807
44 | 0.99313 | -0.047477 | 0.0015395 | 0.00038583
45 | 0.97437 | -0.18299 | 0.0001625 | 4.0725e-05
46 | 0.97415 | -0.18457 | 0.0002546 | 6.3809e-05
47 | 0.97522 | -0.17682 | 0 | 0
48 | 0.97316 | -0.19173 | 0.00044401 | 0.00011128
49 | 0.9751 | -0.17769 | 0.0005036 | 0.00012621
50 | 0.97683 | -0.16513 | 0 | 0
51 | 0.97767 | -0.15905 | 0.00050421 | 0.00012637
52 | 0.97308 | -0.19233 | 0.00036164 | 9.0636e-05
53 | 0.97293 | -0.19339 | 0.00032491 | 8.1431e-05
54 | 0.97764 | -0.15928 | 0.00075502 | 0.00018923
55 | 0.97037 | -0.21204 | 0.0016574 | 0.00041539
56 | 0.97088 | -0.20829 | 0.0019626 | 0.00049187
57 | 0.97278 | -0.19452 | 0.0012642 | 0.00031684
58 | 0.9789 | -0.15016 | 0.00016314 | 4.0886e-05
59 | 0.98029 | -0.14012 | 0 | 0
60 | 0.99793 | -0.014502 | 0.0020112 | 0.00050405
61 | 0.99798 | -0.014099 | 0.0021183 | 0.0005309
62 | 0.99735 | -0.018533 | 0 | 0
63 | 0.99724 | -0.019348 | 0.0029984 | 0.00075148
64 | 0.99689 | -0.021794 | 0.0016743 | 0.00041963
65 | 0.99664 | -0.023506 | 0.0080107 | 0.0020077
66 | 0.99565 | -0.030503 | 0.0026303 | 0.00065921
67 | 0.99786 | -0.014984 | 0.00616 | 0.0015439
68 | 0.99433 | -0.039822 | 0.00064299 | 0.00016115
69 | 0.98752 | -0.088184 | 0.0018603 | 0.00046624
70 | 0.98772 | -0.086749 | 0.001689 | 0.00042331
71 | 0.98775 | -0.086489 | 0.0020555 | 0.00051516
72 | 0.98795 | -0.085104 | 0.0010683 | 0.00026774
73 | 0.98196 | -0.1281 | 0.00083172 | 0.00020845
74 | 0.98114 | -0.13399 | 0.00031874 | 7.9884e-05
75 | 0.98816 | -0.083612 | 0 | 0
76 | 0.98832 | -0.082407 | 0.002396 | 0.00060049
77 | 0.98811 | -0.083963 | 0.00055634 | 0.00013943
78 | 0.98804 | -0.08442 | 0.00061796 | 0.00015488
79 | 0.98801 | -0.084654 | 0.001005 | 0.00025188
80 | 0.988 | -0.084683 | 0.0011858 | 0.00029719
81 | 0.98893 | -0.07805 | 0.0018086 | 0.00045327
82 | 0.98966 | -0.072864 | 0.001168 | 0.00029272
83 | 0.98991 | -0.0711 | 0.00054746 | 0.00013721
84 | 0.99307 | -0.047868 | 0.0015739 | 0.00039445
85 | 0.99194 | -0.055719 | 0.0034144 | 0.00085573
86 | 0.975 | -0.17538 | 0.017 | 0.0042606
87 | 0.9882 | -0.081795 | 0.0027441 | 0.00068774
88 | 0.9883 | -0.081106 | 0 | 0
89 | 0.9909 | -0.062948 | 0.0091712 | 0.0022985
90 | 0.98821 | -0.081783 | 0.0019569 | 0.00049045
91 | 0.98615 | -0.096188 | 0.0025407 | 0.00063677
92 | 0.99373 | -0.044013 | 0.0026439 | 0.00066262
93 | 0.99317 | -0.047976 | 0.00098183 | 0.00024607
94 | 0.99206 | -0.05585 | 0 | 0
95 | 0.99192 | -0.056819 | 0.0015748 | 0.00039469
96 | 0.99035 | -0.067943 | 0 | 0
97 | 0.99185 | -0.05736 | 0.00086891 | 0.00021777
98 | 0.98993 | -0.070954 | 0.001012 | 0.00025364
99 | 0.99015 | -0.069368 | 0.0011522 | 0.00028878
100 | 0.99183 | -0.057457 | 0.0015418 | 0.0003864
101 | 0.98987 | -0.071341 | 0.0020265 | 0.0005079
102 | 0.99614 | -0.026891 | 0.0040082 | 0.0010046
103 | 0.99612 | -0.027048 | 0.0019059 | 0.00047766
104 | 0.98985 | -0.071546 | 0.001614 | 0.00040451
105 | 0.98392 | -0.1119 | 0.0017706 | 0.00044376
106 | 0.98235 | -0.12297 | 0.0021636 | 0.00054226
107 | 0.98212 | -0.12459 | 0.0007273 | 0.00018228
108 | 0.98052 | -0.13595 | 0.00089428 | 0.00022413
109 | 0.97847 | -0.15052 | 0.0028934 | 0.00072516
110 | 0.97383 | -0.18374 | 0.0047495 | 0.0011903
111 | 0.97381 | -0.18389 | 0.006052 | 0.0015168
112 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0013358 | -0.00033478 | 0.0013359 | 0.00033443 | 8.0028e-08 | -3.4803e-07 | 0.0020468 | 0.0020466 | 0.0020468 | 0.97112 | -0.20325 | 0.97118 | -0.20282 | 0.75806
1 | -0.0073262 | -0.0018358 | 0.0073294 | 0.0018365 | 3.1765e-06 | 7.2159e-07 | 0.011225 | 0.011225 | 0.011225 | 0.97118 | -0.20282 | 0.97161 | -0.19968 | 4.1574
2 | 0.0058104 | 0.0014555 | -0.0058064 | -0.0014549 | 3.9749e-06 | 5.3318e-07 | 0.0088983 | 0.0088987 | 0.0088987 | 0.97161 | -0.19968 | 0.97093 | -0.20463 | 3.2958
3 | -0.01314 | -0.0032919 | 0.013145 | 0.0032938 | 5.6272e-06 | 1.8884e-06 | 0.020123 | 0.020123 | 0.020123 | 0.97161 | -0.19968 | 0.97204 | -0.19659 | 7.453
4 | 0.0014826 | 0.00037127 | -0.0014825 | -0.00037154 | 7.8434e-08 | -2.7094e-07 | 0.002272 | 0.0022721 | 0.0022721 | 0.97093 | -0.20463 | 0.97087 | -0.20501 | 0.84153
5 | -0.013145 | -0.0032938 | 0.013149 | 0.0032951 | 3.7318e-06 | 1.2522e-06 | 0.020123 | 0.020123 | 0.020123 | 0.97204 | -0.19659 | 0.97232 | -0.19454 | 7.453
6 | -0.018199 | -0.0045607 | 0.018212 | 0.0045654 | 1.314e-05 | 4.717e-06 | 0.027851 | 0.027851 | 0.027851 | 0.97232 | -0.19454 | 0.97305 | -0.18933 | 10.3151
7 | -0.018058 | -0.0045293 | 0.018073 | 0.0045347 | 1.4909e-05 | 5.3382e-06 | 0.027503 | 0.027503 | 0.027503 | 0.97702 | -0.16086 | 0.97786 | -0.15491 | 10.1864
8 | 0.018058 | 0.0045293 | -0.018049 | -0.0045263 | 8.3846e-06 | 3.0025e-06 | 0.027503 | 0.027503 | 0.027503 | 0.97702 | -0.16086 | 0.97656 | -0.16421 | 10.1864
9 | -0.024583 | -0.0061662 | 0.024606 | 0.0061749 | 2.3353e-05 | 8.646e-06 | 0.03741 | 0.037409 | 0.03741 | 0.97786 | -0.15491 | 0.97881 | -0.14807 | 13.8554
10 | 0.017026 | 0.00427 | -0.017014 | -0.0042657 | 1.2068e-05 | 4.2824e-06 | 0.025945 | 0.025945 | 0.025945 | 0.97656 | -0.16421 | 0.97584 | -0.16933 | 9.6092
11 | -0.029397 | -0.0073685 | 0.029461 | 0.0073927 | 6.4445e-05 | 2.415e-05 | 0.044955 | 0.044955 | 0.044955 | 0.97305 | -0.18933 | 0.97525 | -0.17353 | 16.65
12 | 0.011185 | 0.0028031 | -0.011179 | -0.0028012 | 5.9581e-06 | 1.8864e-06 | 0.017104 | 0.017104 | 0.017104 | 0.97305 | -0.18933 | 0.97251 | -0.19318 | 6.3349
13 | 0.003889 | 0.00097416 | -0.0038882 | -0.00097429 | 7.6122e-07 | -1.3433e-07 | 0.0059513 | 0.0059515 | 0.0059515 | 0.97233 | -0.1945 | 0.97213 | -0.19592 | 2.2043
14 | -0.0093194 | -0.0023352 | 0.0093211 | 0.0023356 | 1.7107e-06 | 4.9075e-07 | 0.014262 | 0.014262 | 0.014262 | 0.97233 | -0.1945 | 0.97251 | -0.19318 | 5.2822
15 | 0.0012196 | 0.00030546 | -0.0012195 | -0.00030564 | 3.3269e-08 | -1.769e-07 | 0.0018667 | 0.0018667 | 0.0018667 | 0.97213 | -0.19592 | 0.97211 | -0.19611 | 0.69138
16 | 0.01677 | 0.0042048 | -0.016756 | -0.0041999 | 1.4108e-05 | 4.9958e-06 | 0.025588 | 0.025588 | 0.025588 | 0.97525 | -0.17353 | 0.9744 | -0.1796 | 9.4769
17 | -0.046231 | -0.011598 | 0.046282 | 0.011617 | 5.1195e-05 | 1.9484e-05 | 0.070542 | 0.070542 | 0.070542 | 0.97525 | -0.17353 | 0.97636 | -0.16555 | 26.1267
18 | 0.015332 | 0.0038432 | -0.01533 | -0.0038422 | 2.7989e-06 | 9.7461e-07 | 0.023414 | 0.023414 | 0.023414 | 0.9744 | -0.1796 | 0.97422 | -0.18092 | 8.672
19 | -0.049797 | -0.012498 | 0.049807 | 0.012502 | 9.6537e-06 | 3.6793e-06 | 0.075899 | 0.075899 | 0.075899 | 0.97636 | -0.16555 | 0.97656 | -0.16416 | 28.1108
20 | 0.010806 | 0.0027085 | -0.010802 | -0.0027071 | 4.2184e-06 | 1.3136e-06 | 0.016505 | 0.016505 | 0.016505 | 0.97422 | -0.18092 | 0.97383 | -0.18374 | 6.113
21 | -0.051048 | -0.012813 | 0.051145 | 0.01285 | 9.6828e-05 | 3.692e-05 | 0.07779 | 0.07779 | 0.07779 | 0.97656 | -0.16416 | 0.97847 | -0.15052 | 28.8113
22 | 0.054057 | 0.013582 | -0.054038 | -0.013575 | 1.8446e-05 | 7.0396e-06 | 0.082191 | 0.082191 | 0.082191 | 0.97881 | -0.14807 | 0.97847 | -0.15052 | 30.4409
23 | -0.078663 | -0.019757 | 0.078795 | 0.019808 | 0.00013275 | 5.0871e-05 | 0.1196 | 0.1196 | 0.1196 | 0.97881 | -0.14807 | 0.98052 | -0.13595 | 44.2963
24 | 0.017014 | 0.0042657 | -0.017 | -0.0042606 | 1.4247e-05 | 5.0563e-06 | 0.025945 | 0.025945 | 0.025945 | 0.97584 | -0.16933 | 0.975 | -0.17538 | 9.6093
25 | -0.00046602 | -0.0001168 | 0.00046607 | 0.00011482 | 4.8291e-08 | -1.9724e-06 | 0.0007039 | 0.00070319 | 0.0007039 | 0.98515 | -0.10523 | 0.98525 | -0.10446 | 0.2607
26 | -0.010899 | -0.0027161 | 0.010907 | 0.0027137 | 8.2687e-06 | -2.434e-06 | 0.016455 | 0.016453 | 0.016455 | 0.98525 | -0.10446 | 0.98602 | -0.098916 | 2.0315
27 | 0.010258 | 0.0025574 | -0.010251 | -0.0025599 | 6.5916e-06 | -2.5086e-06 | 0.015487 | 0.015489 | 0.015489 | 0.98525 | -0.10446 | 0.9846 | -0.10915 | 1.9122
28 | 0.0031752 | 0.00079482 | -0.0031739 | -0.00079546 | 1.2575e-06 | -6.3546e-07 | 0.0047914 | 0.0047917 | 0.0047917 | 0.98602 | -0.098916 | 0.98562 | -0.10178 | 1.7747
29 | -0.014082 | -0.0035085 | 0.014087 | 0.0035084 | 4.4944e-06 | -1.0404e-07 | 0.021244 | 0.021244 | 0.021244 | 0.98602 | -0.098916 | 0.98635 | -0.096583 | 2.6228
30 | 0.0096085 | 0.0023988 | -0.0095836 | -0.0023916 | 2.497e-05 | 7.1958e-06 | 0.014518 | 0.014519 | 0.014519 | 0.9846 | -0.10915 | 0.98196 | -0.1281 | 5.3773
31 | 0.014101 | 0.0035081 | -0.014087 | -0.0035084 | 1.3953e-05 | -3.314e-07 | 0.021242 | 0.021244 | 0.021244 | 0.98736 | -0.089335 | 0.98635 | -0.096583 | 2.6227
32 | -0.015626 | -0.0038904 | 0.015628 | 0.0038905 | 2.2295e-06 | 1.1524e-07 | 0.023541 | 0.02354 | 0.023541 | 0.98736 | -0.089335 | 0.9875 | -0.088291 | 2.9063
33 | -0.017659 | -0.0043994 | 0.017659 | 0.0043994 | 2.5737e-07 | 3.1871e-08 | 0.0266 | 0.0266 | 0.0266 | 0.9875 | -0.088291 | 0.98752 | -0.088184 | 3.284
34 | -0.11552 | -0.029216 | 0.11556 | 0.029231 | 3.7777e-05 | 1.429e-05 | 0.17241 | 0.17241 | 0.17241 | 0.99752 | -0.017075 | 0.99786 | -0.014756 | 21.2856
35 | 0.11449 | 0.028959 | -0.11421 | -0.028851 | 0.0002844 | 0.00010756 | 0.17088 | 0.17088 | 0.17088 | 0.99752 | -0.017075 | 0.99496 | -0.034733 | 21.0966
36 | -0.11627 | -0.029409 | 0.11635 | 0.029439 | 7.9786e-05 | 3.0187e-05 | 0.17347 | 0.17347 | 0.17347 | 0.99786 | -0.014756 | 0.99856 | -0.0098939 | 21.4166
37 | 0.11276 | 0.028489 | -0.11276 | -0.028488 | 2.3304e-06 | 8.8096e-07 | 0.16872 | 0.16872 | 0.16872 | 0.99496 | -0.034733 | 0.99494 | -0.03488 | 20.8293
38 | -0.12634 | -0.031944 | 0.12652 | 0.032011 | 0.00017639 | 6.6904e-05 | 0.18837 | 0.18837 | 0.18837 | 0.99856 | -0.0098939 | 1 | 0 | 23.2552
39 | 0.0099941 | 0.002505 | -0.0099915 | -0.0025043 | 2.6077e-06 | 7.5654e-07 | 0.014893 | 0.014893 | 0.014893 | 0.99856 | -0.0098939 | 0.99829 | -0.011779 | 5.5159
40 | 0.11172 | 0.028227 | -0.11171 | -0.028225 | 7.0148e-06 | 2.651e-06 | 0.16716 | 0.16716 | 0.16716 | 0.99494 | -0.03488 | 0.99488 | -0.035327 | 20.6375
41 | 0.079807 | 0.020027 | -0.07974 | -0.020002 | 6.6667e-05 | 2.4748e-05 | 0.11876 | 0.11876 | 0.11876 | 1 | 0 | 0.99914 | -0.006024 | 14.6621
42 | 0.0092768 | 0.0023251 | -0.0092649 | -0.0023219 | 1.1886e-05 | 3.2708e-06 | 0.013828 | 0.013828 | 0.013828 | 0.99829 | -0.011779 | 0.99697 | -0.021039 | 5.1215
43 | 0.10996 | 0.027787 | -0.10985 | -0.027746 | 0.0001101 | 4.1585e-05 | 0.16455 | 0.16455 | 0.16455 | 0.99488 | -0.035327 | 0.99385 | -0.042447 | 20.3152
44 | 0.0067238 | 0.0016843 | -0.0067227 | -0.0016841 | 1.1738e-06 | 2.0582e-07 | 0.010014 | 0.010014 | 0.010014 | 0.99914 | -0.006024 | 0.99896 | -0.0072863 | 3.7087
45 | 0.073016 | 0.018318 | -0.072995 | -0.01831 | 2.1597e-05 | 7.9617e-06 | 0.10875 | 0.10875 | 0.10875 | 0.99914 | -0.006024 | 0.99883 | -0.008157 | 13.4259
46 | 0.0092649 | 0.0023219 | -0.0092593 | -0.0023203 | 5.6077e-06 | 1.5444e-06 | 0.013828 | 0.013828 | 0.013828 | 0.99697 | -0.021039 | 0.99635 | -0.025414 | 5.1216
47 | 0.10847 | 0.027399 | -0.1084 | -0.02737 | 7.6673e-05 | 2.8947e-05 | 0.16248 | 0.16248 | 0.16248 | 0.99385 | -0.042447 | 0.99313 | -0.047477 | 20.0598
48 | 0.0061666 | 0.0015447 | -0.00616 | -0.0015439 | 6.5644e-06 | 8.9426e-07 | 0.0091853 | 0.0091859 | 0.0091859 | 0.99896 | -0.0072863 | 0.99786 | -0.014984 | 3.4022
49 | 0.067618 | 0.016962 | -0.067562 | -0.016942 | 5.5683e-05 | 2.0382e-05 | 0.10074 | 0.10074 | 0.10074 | 0.99883 | -0.008157 | 0.99798 | -0.014099 | 12.437
50 | 0.0059154 | 0.0014823 | -0.0059141 | -0.0014821 | 1.2091e-06 | 1.4177e-07 | 0.0088343 | 0.0088344 | 0.0088344 | 0.99635 | -0.025414 | 0.99614 | -0.026891 | 3.272
51 | 0.10686 | 0.026985 | -0.10685 | -0.026982 | 5.8763e-06 | 2.2174e-06 | 0.16018 | 0.16018 | 0.16018 | 0.99313 | -0.047477 | 0.99307 | -0.047868 | 19.775
52 | 0.0062864 | 0.0015684 | -0.006285 | -0.0015682 | 1.3642e-06 | 2.2917e-07 | 0.0095978 | 0.0095979 | 0.0095979 | 0.97437 | -0.18299 | 0.97415 | -0.18457 | 3.5548
53 | -0.0064489 | -0.0016092 | 0.0064543 | 0.0016101 | 5.4612e-06 | 9.7497e-07 | 0.0098459 | 0.0098455 | 0.0098459 | 0.97437 | -0.18299 | 0.97522 | -0.17682 | 3.6466
54 | 0.0060304 | 0.0015044 | -0.0060245 | -0.0015035 | 5.9214e-06 | 8.8587e-07 | 0.009209 | 0.0092095 | 0.0092095 | 0.97415 | -0.18457 | 0.97316 | -0.19173 | 3.4109
55 | 0.00050366 | 0.00012422 | -0.0005036 | -0.00012621 | 5.9539e-08 | -1.9946e-06 | 0.00076778 | 0.0007685 | 0.0007685 | 0.97522 | -0.17682 | 0.9751 | -0.17769 | 0.28463
56 | -0.006958 | -0.0017344 | 0.0069691 | 0.0017367 | 1.1148e-05 | 2.3054e-06 | 0.010613 | 0.010613 | 0.010613 | 0.97522 | -0.17682 | 0.97683 | -0.16513 | 3.9309
57 | 0.0055805 | 0.0013922 | -0.00558 | -0.0013922 | 4.5968e-07 | 5.1037e-08 | 0.0085306 | 0.0085306 | 0.0085306 | 0.97316 | -0.19173 | 0.97308 | -0.19233 | 3.1595
58 | -0.0069691 | -0.0017367 | 0.0069749 | 0.0017379 | 5.8054e-06 | 1.1978e-06 | 0.010613 | 0.010612 | 0.010613 | 0.97683 | -0.16513 | 0.97767 | -0.15905 | 3.9306
59 | -0.0082342 | -0.0020531 | 0.0082442 | 0.0020557 | 1.0039e-05 | 2.5742e-06 | 0.012529 | 0.012528 | 0.012529 | 0.97767 | -0.15905 | 0.9789 | -0.15016 | 4.6403
60 | 0.00075504 | 0.00018886 | -0.00075502 | -0.00018923 | 2.4532e-08 | -3.6391e-07 | 0.001149 | 0.0011492 | 0.0011492 | 0.97767 | -0.15905 | 0.97764 | -0.15928 | 0.42562
61 | 0.0052184 | 0.0013015 | -0.0052176 | -0.0013015 | 7.5658e-07 | 5.4366e-08 | 0.0079776 | 0.0079777 | 0.0079777 | 0.97308 | -0.19233 | 0.97293 | -0.19339 | 2.9547
62 | 0.0048927 | 0.0012201 | -0.004892 | -0.00122 | 7.5573e-07 | 2.195e-08 | 0.0074808 | 0.0074809 | 0.0074809 | 0.97293 | -0.19339 | 0.97278 | -0.19452 | 2.7707
63 | -0.0016574 | -0.00041539 | 0.0016583 | 0.0004131 | 8.5458e-07 | -2.2927e-06 | 0.0025416 | 0.0025407 | 0.0025416 | 0.97037 | -0.21204 | 0.97088 | -0.20829 | 0.94134
64 | -0.0036209 | -0.00090497 | 0.0036277 | 0.00090319 | 6.8466e-06 | -1.7838e-06 | 0.0055486 | 0.005547 | 0.0055486 | 0.97088 | -0.20829 | 0.97278 | -0.19452 | 2.055
65 | -0.0084074 | -0.0020965 | 0.0084189 | 0.0020996 | 1.1569e-05 | 3.0197e-06 | 0.012776 | 0.012776 | 0.012776 | 0.9789 | -0.15016 | 0.98029 | -0.14012 | 4.7319
66 | -0.0084189 | -0.0020996 | 0.008426 | 0.0021014 | 7.086e-06 | 1.8475e-06 | 0.012776 | 0.012775 | 0.012776 | 0.98029 | -0.14012 | 0.98114 | -0.13399 | 4.7317
67 | -0.06544 | -0.016409 | 0.065444 | 0.016411 | 3.6496e-06 | 1.3315e-06 | 0.097581 | 0.097581 | 0.097581 | 0.99793 | -0.014502 | 0.99798 | -0.014099 | 12.0471
68 | 0.063429 | 0.015905 | -0.063393 | -0.015893 | 3.5416e-05 | 1.2876e-05 | 0.094582 | 0.094583 | 0.094583 | 0.99793 | -0.014502 | 0.99735 | -0.018533 | 11.6769
69 | 0.0029988 | 0.00075125 | -0.0029984 | -0.00075148 | 3.3836e-07 | -2.2334e-07 | 0.0044739 | 0.0044741 | 0.0044741 | 0.99735 | -0.018533 | 0.99724 | -0.019348 | 1.6571
70 | 0.060395 | 0.015141 | -0.060367 | -0.015131 | 2.7269e-05 | 9.8562e-06 | 0.090109 | 0.090109 | 0.090109 | 0.99735 | -0.018533 | 0.99689 | -0.021794 | 11.1245
71 | 0.058693 | 0.014712 | -0.058679 | -0.014707 | 1.3914e-05 | 5.0109e-06 | 0.08761 | 0.08761 | 0.08761 | 0.99689 | -0.021794 | 0.99664 | -0.023506 | 10.816
72 | 0.050668 | 0.012699 | -0.050619 | -0.012682 | 4.904e-05 | 1.7253e-05 | 0.07565 | 0.07565 | 0.07565 | 0.99664 | -0.023506 | 0.99565 | -0.030503 | 9.3395
73 | 0.047989 | 0.012023 | -0.047927 | -0.012001 | 6.1793e-05 | 2.1516e-05 | 0.071719 | 0.07172 | 0.07172 | 0.99565 | -0.030503 | 0.99433 | -0.039822 | 8.8543
74 | 0.047284 | 0.01184 | -0.047257 | -0.01183 | 2.7373e-05 | 9.5058e-06 | 0.070758 | 0.070758 | 0.070758 | 0.99433 | -0.039822 | 0.99373 | -0.044013 | 8.7356
75 | -0.01952 | -0.0048657 | 0.019524 | 0.0048663 | 3.839e-06 | 6.57e-07 | 0.029404 | 0.029403 | 0.029404 | 0.98752 | -0.088184 | 0.98772 | -0.086749 | 3.6301
76 | -0.021213 | -0.0052897 | 0.021213 | 0.0052898 | 7.5473e-07 | 1.5377e-07 | 0.031948 | 0.031948 | 0.031948 | 0.98772 | -0.086749 | 0.98775 | -0.086489 | 3.9442
77 | -0.023269 | -0.005805 | 0.023273 | 0.005806 | 4.4201e-06 | 1.0355e-06 | 0.035044 | 0.035044 | 0.035044 | 0.98775 | -0.086489 | 0.98795 | -0.085104 | 4.3265
78 | -0.024342 | -0.0060737 | 0.024347 | 0.006075 | 4.9859e-06 | 1.2321e-06 | 0.036653 | 0.036653 | 0.036653 | 0.98795 | -0.085104 | 0.98816 | -0.083612 | 4.5251
79 | 0.0087518 | 0.0021832 | -0.0087448 | -0.0021813 | 7.0685e-06 | 1.9042e-06 | 0.013258 | 0.013259 | 0.013259 | 0.98196 | -0.1281 | 0.98114 | -0.13399 | 4.9107
80 | -0.027712 | -0.006918 | 0.027717 | 0.0069193 | 4.5884e-06 | 1.2776e-06 | 0.041721 | 0.04172 | 0.041721 | 0.98816 | -0.083612 | 0.98832 | -0.082407 | 5.1507
81 | 0.0033655 | 0.00084304 | -0.0033654 | -0.0008431 | 1.6334e-07 | -6.7734e-08 | 0.0050678 | 0.0050679 | 0.0050679 | 0.98816 | -0.083612 | 0.98811 | -0.083963 | 1.877
82 | -0.030113 | -0.0075198 | 0.030131 | 0.0075251 | 1.8041e-05 | 5.3149e-06 | 0.045328 | 0.045327 | 0.045328 | 0.98832 | -0.082407 | 0.98893 | -0.07805 | 5.596
83 | 0.002809 | 0.00070367 | -0.0028088 | -0.00070381 | 1.7743e-07 | -1.3529e-07 | 0.0042301 | 0.0042301 | 0.0042301 | 0.98811 | -0.083963 | 0.98804 | -0.08442 | 1.5667
84 | 0.0021909 | 0.00054893 | -0.0021908 | -0.00054904 | 7.1237e-08 | -1.069e-07 | 0.0032995 | 0.0032995 | 0.0032995 | 0.98804 | -0.08442 | 0.98801 | -0.084654 | 1.222
85 | 0.0011858 | 0.00029716 | -0.0011858 | -0.00029719 | 4.6447e-09 | -2.8101e-08 | 0.0017859 | 0.0017859 | 0.0017859 | 0.98801 | -0.084654 | 0.988 | -0.084683 | 0.66145
86 | -0.031939 | -0.0079784 | 0.031962 | 0.0079853 | 2.2791e-05 | 6.9375e-06 | 0.048049 | 0.048048 | 0.048049 | 0.98893 | -0.07805 | 0.98966 | -0.072864 | 5.9319
87 | -0.03313 | -0.008278 | 0.033138 | 0.0082805 | 8.0471e-06 | 2.4936e-06 | 0.049804 | 0.049804 | 0.049804 | 0.98966 | -0.072864 | 0.98991 | -0.0711 | 6.1486
88 | -0.033686 | -0.0084177 | 0.033694 | 0.0084202 | 8.0311e-06 | 2.5077e-06 | 0.050627 | 0.050627 | 0.050627 | 0.98991 | -0.0711 | 0.99015 | -0.069368 | 6.2502
89 | 0.10528 | 0.026588 | -0.10516 | -0.026544 | 0.00011606 | 4.3772e-05 | 0.15782 | 0.15782 | 0.15782 | 0.99307 | -0.047868 | 0.99194 | -0.055719 | 19.4839
90 | 0.10175 | 0.025688 | -0.10164 | -0.025649 | 0.00010324 | 3.8883e-05 | 0.1527 | 0.1527 | 0.1527 | 0.99194 | -0.055719 | 0.9909 | -0.062948 | 18.8516
91 | -0.0027441 | -0.00068774 | 0.0027444 | 0.00068752 | 2.6185e-07 | -2.1421e-07 | 0.004132 | 0.0041319 | 0.004132 | 0.9882 | -0.081795 | 0.9883 | -0.081106 | 1.5304
92 | 0.089493 | 0.022574 | -0.089484 | -0.022571 | 8.495e-06 | 3.2577e-06 | 0.13479 | 0.13479 | 0.13479 | 0.9883 | -0.081106 | 0.98821 | -0.081783 | 49.9238
93 | -0.092237 | -0.023261 | 0.092472 | 0.023351 | 0.00023539 | 8.9529e-05 | 0.13893 | 0.13893 | 0.13893 | 0.9883 | -0.081106 | 0.9909 | -0.062948 | 25.7271
94 | 0.087527 | 0.02208 | -0.087351 | -0.022013 | 0.00017649 | 6.7673e-05 | 0.13185 | 0.13185 | 0.13185 | 0.98821 | -0.081783 | 0.98615 | -0.096188 | 48.8325
95 | 0.08481 | 0.021376 | -0.084624 | -0.021304 | 0.00018617 | 7.1372e-05 | 0.12801 | 0.12801 | 0.12801 | 0.98615 | -0.096188 | 0.98392 | -0.1119 | 47.4126
96 | 0.044613 | 0.011168 | -0.044589 | -0.01116 | 2.4408e-05 | 8.366e-06 | 0.066799 | 0.066799 | 0.066799 | 0.99373 | -0.044013 | 0.99317 | -0.047976 | 8.2468
97 | 0.043607 | 0.010913 | -0.04356 | -0.010897 | 4.7355e-05 | 1.6145e-05 | 0.065328 | 0.065329 | 0.065329 | 0.99317 | -0.047976 | 0.99206 | -0.05585 | 8.0653
98 | 0.0039862 | 0.00099847 | -0.0039857 | -0.00099858 | 5.3419e-07 | -1.0371e-07 | 0.0059789 | 0.005979 | 0.005979 | 0.99206 | -0.05585 | 0.99192 | -0.056819 | 2.2144
99 | 0.039573 | 0.0098988 | -0.039507 | -0.0098769 | 6.5907e-05 | 2.1871e-05 | 0.05935 | 0.059352 | 0.059352 | 0.99206 | -0.05585 | 0.99035 | -0.067943 | 7.3273
100 | 0.0024109 | 0.00060388 | -0.0024107 | -0.0006041 | 1.8062e-07 | -2.1617e-07 | 0.0036165 | 0.0036166 | 0.0036166 | 0.99192 | -0.056819 | 0.99185 | -0.05736 | 1.3395
101 | 0.0046548 | 0.0011658 | -0.0046528 | -0.0011658 | 1.9378e-06 | -7.1315e-08 | 0.0069935 | 0.0069938 | 0.0069938 | 0.99035 | -0.067943 | 0.98993 | -0.070954 | 2.5903
102 | 0.034853 | 0.0087112 | -0.034846 | -0.008709 | 6.836e-06 | 2.1665e-06 | 0.052358 | 0.052358 | 0.052358 | 0.99035 | -0.067943 | 0.99015 | -0.069368 | 6.464
103 | 0.0015418 | 0.00038633 | -0.0015418 | -0.0003864 | 2.0534e-08 | -7.1483e-08 | 0.002313 | 0.002313 | 0.002313 | 0.99185 | -0.05736 | 0.99183 | -0.057457 | 0.85668
104 | 0.0036408 | 0.0009122 | -0.0036406 | -0.00091226 | 1.9534e-07 | -5.9243e-08 | 0.0054726 | 0.0054726 | 0.0054726 | 0.98993 | -0.070954 | 0.98987 | -0.071341 | 2.0269
105 | 0.0016141 | 0.00040437 | -0.001614 | -0.00040451 | 4.5767e-08 | -1.4255e-07 | 0.0024263 | 0.0024263 | 0.0024263 | 0.98987 | -0.071341 | 0.98985 | -0.071546 | 0.89863
106 | 0.0019059 | 0.00047757 | -0.0019059 | -0.00047766 | 4.1491e-08 | -9.0833e-08 | 0.002847 | 0.002847 | 0.002847 | 0.99614 | -0.026891 | 0.99612 | -0.027048 | 1.0545
107 | 0.082853 | 0.020861 | -0.082725 | -0.020812 | 0.00012787 | 4.9015e-05 | 0.12534 | 0.12534 | 0.12534 | 0.98392 | -0.1119 | 0.98235 | -0.12297 | 46.4208
108 | 0.080562 | 0.020269 | -0.080543 | -0.020262 | 1.8301e-05 | 7.014e-06 | 0.12206 | 0.12206 | 0.12206 | 0.98235 | -0.12297 | 0.98212 | -0.12459 | 45.207
109 | 0.079816 | 0.02008 | -0.07969 | -0.020032 | 0.00012625 | 4.8383e-05 | 0.12096 | 0.12096 | 0.12096 | 0.98212 | -0.12459 | 0.98052 | -0.13595 | 44.7989
110 | 0.0060521 | 0.0015168 | -0.006052 | -0.0015168 | 1.2372e-07 | 1.874e-08 | 0.0092477 | 0.0092477 | 0.0092477 | 0.97383 | -0.18374 | 0.97381 | -0.18389 | 3.4251

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20814 | 0.052293

## res_load
| p_mw | q_mvar
0 | 0.0013358 | 0.00033478
1 | 0.0059904 | 0.0015013
2 | 0.0043239 | 0.0010837
3 | 0.0014825 | 0.00037154
4 | 0.0050497 | 0.0012656
5 | 0.00651 | 0.0016316
6 | 0.0010229 | 0.00025636
7 | 0.0054304 | 0.001361
8 | 0.0026687 | 0.00066883
9 | 0.0018578 | 0.00046561
10 | 0.0012195 | 0.00030564
11 | 0.0014231 | 0.00035666
12 | 0.003515 | 0.00088093
13 | 0.0045237 | 0.0011338
14 | 0.0012413 | 0.00031111
15 | 0.00046602 | 0.0001168
16 | 0.00017518 | 4.3904e-05
17 | 0.00064256 | 0.00016104
18 | 0.0015254 | 0.0003823
19 | 0.0020307 | 0.00050895
20 | 0.0031739 | 0.00079546
21 | 0.0010269 | 0.00025737
22 | 0.00071144 | 0.0001783
23 | 0.0014477 | 0.00036282
24 | 0.0010388 | 0.00026035
25 | 0.0010181 | 0.00025515
26 | 0.00071472 | 0.00017913
27 | 0.0017458 | 0.00043754
28 | 0.0013818 | 0.00034631
29 | 0.00055606 | 0.00013936
30 | 0.0053772 | 0.0013476
31 | 0.0033439 | 0.00083807
32 | 0.0015395 | 0.00038583
33 | 0.0001625 | 4.0725e-05
34 | 0.0002546 | 6.3809e-05
35 | 0.00044401 | 0.00011128
36 | 0.0005036 | 0.00012621
37 | 0.00050421 | 0.00012637
38 | 0.00036164 | 9.0636e-05
39 | 0.00032491 | 8.1431e-05
40 | 0.00075502 | 0.00018923
41 | 0.0016574 | 0.00041539
42 | 0.0019626 | 0.00049187
43 | 0.0012642 | 0.00031684
44 | 0.00016314 | 4.0886e-05
45 | 0.0020112 | 0.00050405
46 | 0.0021183 | 0.0005309
47 | 0.0029984 | 0.00075148
48 | 0.0016743 | 0.00041963
49 | 0.0080107 | 0.0020077
50 | 0.0026303 | 0.00065921
51 | 0.00616 | 0.0015439
52 | 0.00064299 | 0.00016115
53 | 0.0018603 | 0.00046624
54 | 0.001689 | 0.00042331
55 | 0.0020555 | 0.00051516
56 | 0.0010683 | 0.00026774
57 | 0.00083172 | 0.00020845
58 | 0.00031874 | 7.9884e-05
59 | 0.002396 | 0.00060049
60 | 0.00055634 | 0.00013943
61 | 0.00061796 | 0.00015488
62 | 0.001005 | 0.00025188
63 | 0.0011858 | 0.00029719
64 | 0.0018086 | 0.00045327
65 | 0.001168 | 0.00029272
66 | 0.00054746 | 0.00013721
67 | 0.0015739 | 0.00039445
68 | 0.0034144 | 0.00085573
69 | 0.017 | 0.0042606
70 | 0.0027441 | 0.00068774
71 | 0.0091712 | 0.0022985
72 | 0.0019569 | 0.00049045
73 | 0.0025407 | 0.00063677
74 | 0.0026439 | 0.00066262
75 | 0.00098183 | 0.00024607
76 | 0.0015748 | 0.00039469
77 | 0.00086891 | 0.00021777
78 | 0.001012 | 0.00025364
79 | 0.0011522 | 0.00028878
80 | 0.0015418 | 0.0003864
81 | 0.0020265 | 0.0005079
82 | 0.0040082 | 0.0010046
83 | 0.0019059 | 0.00047766
84 | 0.001614 | 0.00040451
85 | 0.0017706 | 0.00044376
86 | 0.0021636 | 0.00054226
87 | 0.0007273 | 0.00018228
88 | 0.00089428 | 0.00022413
89 | 0.0028934 | 0.00072516
90 | 0.0047495 | 0.0011903
91 | 0.006052 | 0.0015168

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1