## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1363-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1363-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1363-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1363-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1363-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1363-1_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1363-1_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1363-1_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1363-1_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1363-1_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1363-1_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1363-1_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1363-1_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1363-1_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1363-1_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1363-1_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1363-1_0_4_node_122 | 0.4 | n |  | TRUE
17 | bus_LV_1363-1_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1363-1_0_4_node_71 | 0.4 | n |  | TRUE
19 | bus_LV_1363-1_0_4_node_72 | 0.4 | n |  | TRUE
20 | bus_LV_1363-1_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1363-1_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1363-1_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1363-1_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1363-1_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1363-1_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1363-1_0_4_node_119 | 0.4 | n |  | TRUE
27 | bus_LV_1363-1_0_4_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1363-1_0_4_node_101 | 0.4 | n |  | TRUE
29 | bus_LV_1363-1_0_4_node_100 | 0.4 | n |  | TRUE
30 | bus_LV_1363-1_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1363-1_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1363-1_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1363-1_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1363-1_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1363-1_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1363-1_0_4_node_49 | 0.4 | n |  | TRUE
37 | bus_LV_1363-1_0_4_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_1363-1_0_4_node_120 | 0.4 | n |  | TRUE
39 | bus_LV_1363-1_0_4_node_121 | 0.4 | n |  | TRUE
40 | bus_LV_1363-1_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_1363-1_0_4_node_77 | 0.4 | n |  | TRUE
42 | bus_LV_1363-1_0_4_node_76 | 0.4 | n |  | TRUE
43 | bus_LV_1363-1_0_4_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_1363-1_0_4_node_110 | 0.4 | n |  | TRUE
45 | bus_LV_1363-1_0_4_node_73 | 0.4 | n |  | TRUE
46 | bus_LV_1363-1_0_4_node_75 | 0.4 | n |  | TRUE
47 | bus_LV_1363-1_0_4_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_1363-1_0_4_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_1363-1_0_4_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1363-1_0_4_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_1363-1_0_4_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_1363-1_0_4_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_1363-1_0_4_node_103 | 0.4 | n |  | TRUE
54 | bus_LV_1363-1_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1363-1_0_4_node_95 | 0.4 | n |  | TRUE
56 | bus_LV_1363-1_0_4_node_69 | 0.4 | n |  | TRUE
57 | bus_LV_1363-1_0_4_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_1363-1_0_4_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_1363-1_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_1363-1_0_4_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_1363-1_0_4_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_1363-1_0_4_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_1363-1_0_4_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_1363-1_0_4_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_1363-1_0_4_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_1363-1_0_4_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_1363-1_0_4_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_1363-1_0_4_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_1363-1_0_4_node_87 | 0.4 | n |  | TRUE
70 | bus_LV_1363-1_0_4_node_81 | 0.4 | n |  | TRUE
71 | bus_LV_1363-1_0_4_node_82 | 0.4 | n |  | TRUE
72 | bus_LV_1363-1_0_4_node_79 | 0.4 | n |  | TRUE
73 | bus_LV_1363-1_0_4_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_1363-1_0_4_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_1363-1_0_4_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_1363-1_0_4_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_1363-1_0_4_node_114 | 0.4 | n |  | TRUE
78 | bus_LV_1363-1_0_4_node_84 | 0.4 | n |  | TRUE
79 | bus_LV_1363-1_0_4_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_1363-1_0_4_node_83 | 0.4 | n |  | TRUE
81 | bus_LV_1363-1_0_4_node_78 | 0.4 | n |  | TRUE
82 | bus_LV_1363-1_0_4_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_1363-1_0_4_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_1363-1_0_4_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_1363-1_0_4_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_1363-1_0_4_node_60 | 0.4 | n |  | TRUE
87 | bus_LV_1363-1_0_4_node_118 | 0.4 | n |  | TRUE
88 | bus_LV_1363-1_0_4_node_117 | 0.4 | n |  | TRUE
89 | bus_LV_1363-1_0_4_node_62 | 0.4 | n |  | TRUE
90 | bus_LV_1363-1_0_4_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_1363-1_0_4_node_66 | 0.4 | n |  | TRUE
92 | bus_LV_1363-1_0_4_node_80 | 0.4 | n |  | TRUE
93 | bus_LV_1363-1_0_4_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_1363-1_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_1363-1_0_4_node_104 | 0.4 | n |  | TRUE
96 | bus_LV_1363-1_0_4_node_108 | 0.4 | n |  | TRUE
97 | bus_LV_1363-1_0_4_node_107 | 0.4 | n |  | TRUE
98 | bus_LV_1363-1_0_4_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_1363-1_0_4_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_1363-1_0_4_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_1363-1_0_4_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_1363-1_0_4_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_1363-1_0_4_node_96 | 0.4 | n |  | TRUE
104 | bus_LV_1363-1_0_4_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_1363-1_0_4_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_1363-1_0_4_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_1363-1_0_4_node_111 | 0.4 | n |  | TRUE
108 | bus_LV_1363-1_0_4_node_112 | 0.4 | n |  | TRUE
109 | bus_LV_1363-1_0_4_node_99 | 0.4 | n |  | TRUE
110 | bus_LV_1363-1_0_4_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_1363-1_0_4_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_1363-1_0_4_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_1363-1_0_4_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_1363-1_0_4_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1363-1_0_4_node_113 | 0.4 | n |  | TRUE
116 | bus_LV_1363-1_0_4_node_115 | 0.4 | n |  | TRUE
117 | bus_LV_1363-1_0_4_node_116 | 0.4 | n |  | TRUE
118 | bus_MV_134_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1363-1_0_4_load_0 | 0 | 0.00028121 | 7.0477e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1363-1_0_4_load_3 | 3 | 0.00074993 | 0.00018795 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1363-1_0_4_load_4 | 4 | 0.00043099 | 0.00010802 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1363-1_0_4_load_8 | 7 | 0.0025097 | 0.00062899 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1363-1_0_4_load_9 | 8 | 0.0024901 | 0.00062408 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1363-1_0_4_load_12 | 10 | 0.00066502 | 0.00016667 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1363-1_0_4_load_10 | 11 | 0.00075115 | 0.00018826 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1363-1_0_4_load_11 | 12 | 0.00095124 | 0.0002384 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1363-1_0_4_load_15 | 14 | 0.00035829 | 8.9796e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1363-1_0_4_load_13 | 15 | 0.00026132 | 6.5494e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1363-1_0_4_load_122 | 16 | 0.00026042 | 6.5268e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1363-1_0_4_load_14 | 17 | 0.00022132 | 5.5467e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1363-1_0_4_load_17 | 20 | 0.0012456 | 0.00031218 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1363-1_0_4_load_18 | 21 | 0.00068882 | 0.00017264 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1363-1_0_4_load_20 | 23 | 0.0012951 | 0.00032459 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1363-1_0_4_load_21 | 24 | 0.00021704 | 5.4395e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1363-1_0_4_load_119 | 26 | 0.00069278 | 0.00017363 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1363-1_0_4_load_25 | 27 | 0.00060333 | 0.00015121 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1363-1_0_4_load_101 | 28 | 0.00023485 | 5.886e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1363-1_0_4_load_23 | 30 | 0.00067236 | 0.00016851 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1363-1_0_4_load_24 | 31 | 0.0013373 | 0.00033516 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1363-1_0_4_load_27 | 32 | 0.00025163 | 6.3063e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1363-1_0_4_load_28 | 33 | 0.00014093 | 3.5321e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1363-1_0_4_load_29 | 34 | 0.0028074 | 0.0007036 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1363-1_0_4_load_49 | 36 | 0.0017402 | 0.00043613 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1363-1_0_4_load_47 | 37 | 0.0012302 | 0.00030833 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1363-1_0_4_load_121 | 39 | 0.0010174 | 0.00025498 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1363-1_0_4_load_31 | 40 | 0.00066186 | 0.00016588 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1363-1_0_4_load_77 | 41 | 0.00035236 | 8.8309e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1363-1_0_4_load_76 | 42 | 0.00030042 | 7.5292e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1363-1_0_4_load_110 | 44 | 0.00027505 | 6.8933e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1363-1_0_4_load_73 | 45 | 0.00071805 | 0.00017996 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1363-1_0_4_load_75 | 46 | 0.00059106 | 0.00014813 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1363-1_0_4_load_34 | 47 | 0.0027426 | 0.00068736 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1363-1_0_4_load_35 | 48 | 0.0021751 | 0.00054513 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1363-1_0_4_load_37 | 50 | 0.0012522 | 0.00031382 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1363-1_0_4_load_38 | 51 | 0.0016783 | 0.00042063 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1363-1_0_4_load_41 | 52 | 0.0034515 | 0.00086502 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1363-1_0_4_load_103 | 53 | 0.0016109 | 0.00040372 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1363-1_0_4_load_69 | 56 | 0.00020823 | 5.2187e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1363-1_0_4_load_68 | 57 | 0.0050484 | 0.0012652 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1363-1_0_4_load_43 | 58 | 0.0015836 | 0.0003969 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1363-1_0_4_load_50 | 60 | 0.0043664 | 0.0010943 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1363-1_0_4_load_45 | 61 | 0.00092732 | 0.00023241 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1363-1_0_4_load_46 | 62 | 0.0012786 | 0.00032045 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1363-1_0_4_load_51 | 64 | 0.0041728 | 0.0010458 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1363-1_0_4_load_61 | 68 | 0.0011743 | 0.0002943 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1363-1_0_4_load_81 | 70 | 0.0045944 | 0.0011515 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1363-1_0_4_load_82 | 71 | 0.003989 | 0.00099974 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1363-1_0_4_load_79 | 72 | 0.0041128 | 0.0010308 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1363-1_0_4_load_70 | 75 | 0.0034414 | 0.00086251 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1363-1_0_4_load_59 | 76 | 0.004294 | 0.0010762 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1363-1_0_4_load_114 | 77 | 0.0014355 | 0.00035978 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1363-1_0_4_load_67 | 79 | 0.00365 | 0.00091479 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1363-1_0_4_load_83 | 80 | 0.0032833 | 0.00082288 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1363-1_0_4_load_78 | 81 | 0.0051294 | 0.0012855 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1363-1_0_4_load_56 | 83 | 0.0017731 | 0.00044439 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1363-1_0_4_load_57 | 84 | 0.0013573 | 0.00034017 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1363-1_0_4_load_58 | 85 | 0.0010825 | 0.0002713 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1363-1_0_4_load_60 | 86 | 0.0013592 | 0.00034064 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1363-1_0_4_load_118 | 87 | 0.0011648 | 0.00029193 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1363-1_0_4_load_62 | 89 | 0.0060386 | 0.0015134 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1363-1_0_4_load_63 | 90 | 0.0059789 | 0.0014985 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1363-1_0_4_load_66 | 91 | 0.005653 | 0.0014168 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1363-1_0_4_load_80 | 92 | 0.003744 | 0.00093834 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1363-1_0_4_load_85 | 93 | 0.0031547 | 0.00079065 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1363-1_0_4_load_86 | 94 | 0.012618 | 0.0031623 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1363-1_0_4_load_104 | 95 | 0.0021412 | 0.00053663 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1363-1_0_4_load_108 | 96 | 0.0033586 | 0.00084175 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1363-1_0_4_load_88 | 98 | 0.0012682 | 0.00031783 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1363-1_0_4_load_89 | 99 | 0.0011415 | 0.00028609 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1363-1_0_4_load_90 | 100 | 0.0012183 | 0.00030533 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1363-1_0_4_load_91 | 101 | 0.0015368 | 0.00038515 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1363-1_0_4_load_96 | 103 | 0.0013672 | 0.00034266 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1363-1_0_4_load_93 | 104 | 0.0015406 | 0.00038611 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1363-1_0_4_load_102 | 105 | 0.001168 | 0.00029273 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1363-1_0_4_load_94 | 106 | 0.002192 | 0.00054936 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1363-1_0_4_load_111 | 107 | 0.0033072 | 0.00082886 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1363-1_0_4_load_112 | 108 | 0.0037481 | 0.00093935 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1363-1_0_4_load_99 | 109 | 0.0015595 | 0.00039084 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1363-1_0_4_load_97 | 110 | 0.00079661 | 0.00019965 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1363-1_0_4_load_98 | 111 | 0.0016914 | 0.00042391 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1363-1_0_4_load_105 | 112 | 0.0030442 | 0.00076294 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1363-1_0_4_load_106 | 113 | 0.0023422 | 0.00058702 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1363-1_0_4_load_113 | 115 | 0.0044575 | 0.0011172 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1363-1_0_4_load_115 | 116 | 0.0010916 | 0.00027357 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1363-1_0_4_load_116 | 117 | 0.00061823 | 0.00015494 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1363-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.051429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1363-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.054911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1363-1_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.030891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1363-1_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.012153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1363-1_0_4_line_4 | NAYY 4x150 SE | 1 | 5 | 0.073393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1363-1_0_4_line_5 | NAYY 4x150 SE | 2 | 6 | 0.012068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1363-1_0_4_line_6 | NAYY 4x150 SE | 2 | 7 | 0.049277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1363-1_0_4_line_7 | NAYY 4x150 SE | 3 | 8 | 0.013411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1363-1_0_4_line_8 | NAYY 4x150 SE | 5 | 12 | 0.21006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1363-1_0_4_line_9 | NAYY 4x150 SE | 5 | 11 | 0.016287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1363-1_0_4_line_10 | NAYY 4x150 SE | 6 | 13 | 0.11099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1363-1_0_4_line_11 | NAYY 4x150 SE | 6 | 14 | 0.06677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1363-1_0_4_line_12 | NAYY 4x150 SE | 9 | 10 | 0.010946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1363-1_0_4_line_13 | NAYY 4x150 SE | 9 | 11 | 0.010084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1363-1_0_4_line_14 | NAYY 4x150 SE | 12 | 15 | 0.24999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1363-1_0_4_line_15 | NAYY 4x150 SE | 13 | 16 | 0.01447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1363-1_0_4_line_16 | NAYY 4x150 SE | 15 | 17 | 0.019067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1363-1_0_4_line_17 | NAYY 4x150 SE | 17 | 18 | 0.031938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1363-1_0_4_line_18 | NAYY 4x150 SE | 18 | 19 | 0.06828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1363-1_0_4_line_19 | NAYY 4x150 SE | 19 | 45 | 0.056022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1363-1_0_4_line_20 | NAYY 4x150 SE | 19 | 38 | 0.29101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1363-1_0_4_line_21 | NAYY 4x150 SE | 20 | 21 | 0.0026277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1363-1_0_4_line_22 | NAYY 4x150 SE | 20 | 22 | 0.033978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1363-1_0_4_line_23 | NAYY 4x150 SE | 21 | 23 | 0.037308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1363-1_0_4_line_24 | NAYY 4x150 SE | 22 | 24 | 0.076461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1363-1_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.038804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1363-1_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.23001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1363-1_0_4_line_27 | NAYY 4x150 SE | 25 | 27 | 0.19876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1363-1_0_4_line_28 | NAYY 4x150 SE | 26 | 29 | 0.17994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1363-1_0_4_line_29 | NAYY 4x150 SE | 27 | 31 | 0.071775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1363-1_0_4_line_30 | NAYY 4x150 SE | 28 | 29 | 0.16265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1363-1_0_4_line_31 | NAYY 4x150 SE | 29 | 110 | 0.37733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1363-1_0_4_line_32 | NAYY 4x150 SE | 30 | 31 | 0.036673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1363-1_0_4_line_33 | NAYY 4x150 SE | 32 | 33 | 0.16967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1363-1_0_4_line_34 | NAYY 4x150 SE | 32 | 34 | 0.080281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1363-1_0_4_line_35 | NAYY 4x150 SE | 33 | 35 | 0.14297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_1363-1_0_4_line_36 | NAYY 4x150 SE | 33 | 36 | 0.2205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_1363-1_0_4_line_37 | NAYY 4x150 SE | 35 | 40 | 0.032561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_1363-1_0_4_line_38 | NAYY 4x150 SE | 36 | 37 | 0.061394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_1363-1_0_4_line_39 | NAYY 4x150 SE | 37 | 51 | 0.14504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1363-1_0_4_line_40 | NAYY 4x150 SE | 38 | 39 | 0.005078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1363-1_0_4_line_41 | NAYY 4x150 SE | 40 | 41 | 0.20118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1363-1_0_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.010594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1363-1_0_4_line_43 | NAYY 4x150 SE | 42 | 45 | 0.2425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1363-1_0_4_line_44 | NAYY 4x150 SE | 42 | 43 | 0.068669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1363-1_0_4_line_45 | NAYY 4x150 SE | 43 | 44 | 0.15385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1363-1_0_4_line_46 | NAYY 4x150 SE | 44 | 46 | 0.038332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1363-1_0_4_line_47 | NAYY 4x150 SE | 47 | 48 | 0.011102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1363-1_0_4_line_48 | NAYY 4x150 SE | 47 | 49 | 0.017835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1363-1_0_4_line_49 | NAYY 4x150 SE | 49 | 50 | 0.088966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1363-1_0_4_line_50 | NAYY 4x150 SE | 49 | 51 | 0.16686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1363-1_0_4_line_51 | NAYY 4x150 SE | 50 | 52 | 0.013174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1363-1_0_4_line_52 | NAYY 4x150 SE | 51 | 53 | 0.14382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1363-1_0_4_line_53 | NAYY 4x150 SE | 52 | 54 | 0.0091987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1363-1_0_4_line_54 | NAYY 4x150 SE | 53 | 55 | 0.016712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_1363-1_0_4_line_55 | NAYY 4x150 SE | 54 | 58 | 0.017234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1363-1_0_4_line_56 | NAYY 4x150 SE | 54 | 59 | 0.006384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1363-1_0_4_line_57 | NAYY 4x150 SE | 55 | 107 | 0.030805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_1363-1_0_4_line_58 | NAYY 4x150 SE | 55 | 106 | 0.15836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1363-1_0_4_line_59 | NAYY 4x150 SE | 56 | 57 | 0.016825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1363-1_0_4_line_60 | NAYY 4x150 SE | 57 | 74 | 0.0161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1363-1_0_4_line_61 | NAYY 4x150 SE | 58 | 60 | 0.052548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1363-1_0_4_line_62 | NAYY 4x150 SE | 59 | 61 | 0.020166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1363-1_0_4_line_63 | NAYY 4x150 SE | 60 | 63 | 0.065789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1363-1_0_4_line_64 | NAYY 4x150 SE | 62 | 63 | 0.070146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1363-1_0_4_line_65 | NAYY 4x150 SE | 64 | 65 | 0.029025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1363-1_0_4_line_66 | NAYY 4x150 SE | 65 | 66 | 0.003188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1363-1_0_4_line_67 | NAYY 4x150 SE | 66 | 70 | 0.014671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1363-1_0_4_line_68 | NAYY 4x150 SE | 66 | 71 | 0.016156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1363-1_0_4_line_69 | NAYY 4x150 SE | 66 | 72 | 0.015326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1363-1_0_4_line_70 | NAYY 4x150 SE | 67 | 68 | 0.01205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1363-1_0_4_line_71 | NAYY 4x150 SE | 67 | 69 | 0.008088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1363-1_0_4_line_72 | NAYY 4x150 SE | 68 | 76 | 0.020678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1363-1_0_4_line_73 | NAYY 4x150 SE | 69 | 77 | 0.033139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1363-1_0_4_line_74 | NAYY 4x150 SE | 69 | 78 | 0.003612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1363-1_0_4_line_75 | NAYY 4x150 SE | 70 | 79 | 0.021482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1363-1_0_4_line_76 | NAYY 4x150 SE | 71 | 80 | 0.020676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1363-1_0_4_line_77 | NAYY 4x150 SE | 72 | 81 | 0.018798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1363-1_0_4_line_78 | NAYY 4x150 SE | 73 | 74 | 0.003264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1363-1_0_4_line_79 | NAYY 4x150 SE | 73 | 75 | 0.075939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1363-1_0_4_line_80 | NAYY 4x150 SE | 74 | 82 | 0.00188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1363-1_0_4_line_81 | NAYY 4x150 SE | 76 | 84 | 0.21873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1363-1_0_4_line_82 | NAYY 4x150 SE | 78 | 93 | 0.032215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1363-1_0_4_line_83 | NAYY 4x150 SE | 78 | 94 | 0.022029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1363-1_0_4_line_84 | NAYY 4x150 SE | 78 | 80 | 0.011901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1363-1_0_4_line_85 | NAYY 4x150 SE | 79 | 82 | 0.028414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1363-1_0_4_line_86 | NAYY 4x150 SE | 81 | 92 | 0.0235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1363-1_0_4_line_87 | NAYY 4x150 SE | 82 | 91 | 0.01838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1363-1_0_4_line_88 | NAYY 4x150 SE | 82 | 89 | 0.029837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1363-1_0_4_line_89 | NAYY 4x150 SE | 83 | 84 | 0.00053882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1363-1_0_4_line_90 | NAYY 4x150 SE | 83 | 85 | 0.016129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1363-1_0_4_line_91 | NAYY 4x150 SE | 85 | 86 | 0.011771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1363-1_0_4_line_92 | NAYY 4x150 SE | 86 | 87 | 0.023118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1363-1_0_4_line_93 | NAYY 4x150 SE | 87 | 88 | 0.0098694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1363-1_0_4_line_94 | NAYY 4x150 SE | 88 | 117 | 0.024026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1363-1_0_4_line_95 | NAYY 4x150 SE | 89 | 90 | 0.0094561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1363-1_0_4_line_96 | NAYY 4x150 SE | 93 | 95 | 0.00041837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1363-1_0_4_line_97 | NAYY 4x150 SE | 94 | 96 | 0.041303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1363-1_0_4_line_98 | NAYY 4x150 SE | 96 | 97 | 0.016534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1363-1_0_4_line_99 | NAYY 4x150 SE | 97 | 114 | 0.00316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1363-1_0_4_line_100 | NAYY 4x150 SE | 97 | 112 | 0.04156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1363-1_0_4_line_101 | NAYY 4x150 SE | 98 | 99 | 0.0089543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1363-1_0_4_line_102 | NAYY 4x150 SE | 99 | 100 | 0.011602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1363-1_0_4_line_103 | NAYY 4x150 SE | 100 | 101 | 0.011099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1363-1_0_4_line_104 | NAYY 4x150 SE | 101 | 102 | 0.019087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1363-1_0_4_line_105 | NAYY 4x150 SE | 102 | 103 | 0.010363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1363-1_0_4_line_106 | NAYY 4x150 SE | 102 | 104 | 0.033214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1363-1_0_4_line_107 | NAYY 4x150 SE | 103 | 105 | 0.029994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1363-1_0_4_line_108 | NAYY 4x150 SE | 104 | 106 | 0.087762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1363-1_0_4_line_109 | NAYY 4x150 SE | 105 | 109 | 0.016854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1363-1_0_4_line_110 | NAYY 4x150 SE | 107 | 108 | 0.022457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
111 | LV_1363-1_0_4_line_111 | NAYY 4x150 SE | 108 | 115 | 0.031622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
112 | LV_1363-1_0_4_line_112 | NAYY 4x150 SE | 109 | 111 | 0.021516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1363-1_0_4_line_113 | NAYY 4x150 SE | 110 | 111 | 0.0084093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1363-1_0_4_line_114 | NAYY 4x150 SE | 112 | 113 | 0.020506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1363-1_0_4_line_115 | NAYY 4x150 SE | 114 | 115 | 0.027125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
116 | LV_1363-1_0_4_line_116 | NAYY 4x150 SE | 116 | 117 | 0.0089987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1363-1_0_4_trafo_103 | 0.25 MVA 20/0.4 kV | 118 | 53 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2697351.1143 | 1206209.0371 | 2697356.721 | 1206215.533 | 2697359.4422 | 1206221.2479 | 2697359.1016 | 1206257.7652
1 | 2697358.5894 | 1206312.6738 | 2697359.1016 | 1206257.7652
2 | 2697351.1143 | 1206209.0371 | 2697352.2288 | 1206202.2729 | 2697356.4901 | 1206195.1821 | 2697367.2288 | 1206183.6427
3 | 2697351.1143 | 1206209.0371 | 2697338.9664 | 1206209.3697
4 | 2697351.1143 | 1206209.0371 | 2697370.6378 | 1206206.4204 | 2697382.7067 | 1206203.8043 | 2697394.8287 | 1206189.5479 | 2697399.6583 | 1206186.7915 | 2697410.7028 | 1206173.7739
5 | 2697369.7923 | 1206308.1089 | 2697358.5894 | 1206312.6738
6 | 2697358.5894 | 1206312.6738 | 2697325.7188 | 1206349.3852
7 | 2697376.3651 | 1206173.825 | 2697367.2288 | 1206183.6427
8 | 2697410.7028 | 1206173.7739 | 2697409.4207 | 1206169.8392 | 2697407.4056 | 1206160.4778 | 2697396.6196 | 1206146.4701 | 2697393.8796 | 1206139.1093 | 2697434.7166 | 1206062.4791 | 2697431.9122 | 1206034.3699 | 2697433.0911 | 1206012.0184 | 2697431.0474 | 1205987.1682 | 2697430.8342 | 1205978.7526
9 | 2697410.7028 | 1206173.7739 | 2697417.2922 | 1206170.8572 | 2697426.3585 | 1206170.3414
10 | 2697369.7923 | 1206308.1089 | 2697388.5407 | 1206289.5799 | 2697410.3867 | 1206273.7477 | 2697428.4193 | 1206252.483 | 2697453.3064 | 1206235.8334
11 | 2697369.7923 | 1206308.1089 | 2697377.6667 | 1206308.482 | 2697386.2544 | 1206308.4887 | 2697395.3814 | 1206309.4716 | 2697395.4933 | 1206319.8583 | 2697381.1122 | 1206347.0174
12 | 2697436.4258 | 1206169.7687 | 2697437.3058 | 1206168.9825 | 2697446.2468 | 1206165.0543
13 | 2697436.4258 | 1206169.7687 | 2697426.3585 | 1206170.3414
14 | 2697430.8342 | 1205978.7526 | 2697678.9264 | 1205947.9733
15 | 2697464.7808 | 1206228.6269 | 2697464.087 | 1206228.2598 | 2697462.6002 | 1206231.2709 | 2697453.3064 | 1206235.8334
16 | 2697695.1504 | 1205937.9569 | 2697678.9264 | 1205947.9733
17 | 2697723.5303 | 1205923.4378 | 2697705.1442 | 1205931.787 | 2697695.1504 | 1205937.9569
18 | 2697760.4281 | 1205871.6844 | 2697761.5379 | 1205874.0597 | 2697761.6349 | 1205880.6769 | 2697758.66 | 1205890.4571 | 2697750.2125 | 1205902.7494 | 2697738.367 | 1205913.9742 | 2697727.3011 | 1205921.7206 | 2697723.5303 | 1205923.4378
19 | 2697760.4281 | 1205871.6844 | 2697758.4369 | 1205867.3933 | 2697752.8769 | 1205862.6991 | 2697742.86 | 1205860.7338 | 2697733.3905 | 1205861.5794 | 2697717.842 | 1205865.7278 | 2697709.7694 | 1205867.2078
20 | 2697760.4281 | 1205871.6844 | 2697980.0613 | 1206062.5917
21 | 2699114.6711 | 1205222.0189 | 2699113.6274 | 1205219.6073
22 | 2699100.1317 | 1205188.4242 | 2699113.6274 | 1205219.6073
23 | 2699114.6711 | 1205222.0189 | 2699120.222 | 1205234.8448 | 2699129.5857 | 1205240.4485 | 2699141.9228 | 1205239.0141
24 | 2699100.1317 | 1205188.4242 | 2699096.4543 | 1205190.876 | 2699092.3977 | 1205192.7989 | 2699086.8235 | 1205193.5624 | 2699080.3641 | 1205192.1988 | 2699071.0121 | 1205190.0088 | 2699057.0009 | 1205185.7068 | 2699046.4624 | 1205181.6626 | 2699034.1772 | 1205181.0918 | 2699026.8432 | 1205183.3717
25 | 2699180.5601 | 1205237.6596 | 2699162.3863 | 1205236.6349 | 2699141.9228 | 1205239.0141
26 | 2699026.8432 | 1205183.3717 | 2698797.1291 | 1205195.075
27 | 2699180.5601 | 1205237.6596 | 2699313.9342 | 1205385.0264
28 | 2698623.5012 | 1205242.3039 | 2698797.1291 | 1205195.075
29 | 2699367.687 | 1205344.672 | 2699367.6914 | 1205352.0818 | 2699357.6434 | 1205364.7566 | 2699340.1763 | 1205373.4052 | 2699313.9342 | 1205385.0264
30 | 2698623.5012 | 1205242.3039 | 2698629.7983 | 1205264.5453 | 2698653.5882 | 1205300.4515 | 2698690.6602 | 1205340.558 | 2698707.8972 | 1205361.4015 | 2698712.1109 | 1205375.7254
31 | 2698322.1406 | 1205015.2353 | 2698623.5012 | 1205242.3039
32 | 2699382.9342 | 1205315.0248 | 2699373.8215 | 1205318.8389 | 2699367.683 | 1205337.9609 | 2699367.687 | 1205344.672
33 | 2698155.218 | 1205669.7077 | 2698150.1593 | 1205667.639 | 2698116.8449 | 1205638.1159 | 2698090.0201 | 1205625.2109 | 2698075.4173 | 1205608.7932 | 2698066.009 | 1205585.0559 | 2698058.369 | 1205576.8471 | 2698029.1253 | 1205565.9661
34 | 2698231.8878 | 1205691.5547 | 2698194.8035 | 1205685.8965 | 2698155.218 | 1205669.7077
35 | 2697901.4649 | 1205503.0337 | 2697927.2546 | 1205513.7082 | 2697984.4644 | 1205549.3487 | 2698029.1253 | 1205565.9661
36 | 2698121.2665 | 1205365.6425 | 2698029.1253 | 1205565.9661
37 | 2697901.4649 | 1205503.0337 | 2697905.1976 | 1205508.2985 | 2697905.1087 | 1205513.7118 | 2697902.3882 | 1205520.4829 | 2697897.506 | 1205523.6161 | 2697891.4814 | 1205523.117 | 2697890.1923 | 1205522.2563
38 | 2698086.6835 | 1205314.9399 | 2698095.2954 | 1205328.8074 | 2698121.2665 | 1205365.6425
39 | 2698181.255 | 1205204.9693 | 2698086.6835 | 1205314.9399
40 | 2697980.0613 | 1206062.5917 | 2697984.5794 | 1206064.9341
41 | 2697714.4384 | 1205620.161 | 2697890.1923 | 1205522.2563
42 | 2697714.4384 | 1205620.161 | 2697704.8937 | 1205624.758
43 | 2697704.8937 | 1205624.758 | 2697709.7694 | 1205867.2078
44 | 2697642.5936 | 1205627.1239 | 2697654.6996 | 1205635.8055 | 2697669.2098 | 1205638.8893 | 2697682.6775 | 1205636.8749 | 2697698.006 | 1205628.0753 | 2697704.8937 | 1205624.758
45 | 2697642.5936 | 1205627.1239 | 2697492.9065 | 1205662.6912
46 | 2697492.9065 | 1205662.6912 | 2697481.8752 | 1205688.3396 | 2697473.7384 | 1205694.8359
47 | 2698040.1933 | 1205140.3695 | 2698039.0678 | 1205132.7844 | 2698037.842 | 1205129.5771
48 | 2698047.3188 | 1205155.2462 | 2698041.8214 | 1205151.3422 | 2698040.1933 | 1205140.3695
49 | 2698047.3188 | 1205155.2462 | 2698040.7325 | 1205164.3665 | 2698031.2795 | 1205176.6418 | 2698019.702 | 1205183.4675 | 2698008.409 | 1205185.4836 | 2697992.1181 | 1205185.6163 | 2697971.7168 | 1205180.5552
50 | 2698047.3188 | 1205155.2462 | 2698057.2707 | 1205149.1944 | 2698084.1814 | 1205139.4185 | 2698091.2311 | 1205139.1341 | 2698095.4229 | 1205141.0043 | 2698099.0805 | 1205146.2123 | 2698103.9524 | 1205160.3908 | 2698107.8344 | 1205169.0716 | 2698114.7941 | 1205173.8003 | 2698122.213 | 1205175.1231 | 2698140.8821 | 1205177.0422 | 2698150.8681 | 1205181.4093 | 2698181.255 | 1205204.9693
51 | 2697958.9299 | 1205177.3831 | 2697971.7168 | 1205180.5552
52 | 2698181.255 | 1205204.9693 | 2698181.255 | 1205204.9693 | 2698186.4507 | 1205206.856 | 2698193.1259 | 1205204.364 | 2698194.6527 | 1205197.5734 | 2698190.5425 | 1205190.2898 | 2698185.4029 | 1205184.9906 | 2698145.945 | 1205150.4519 | 2698135.1462 | 1205134.4413 | 2698132.8602 | 1205126.7874 | 2698133.8379 | 1205116.3742 | 2698134.6506 | 1205113.6857 | 2698139.0178 | 1205098.8559
53 | 2697949.9382 | 1205175.473 | 2697954.0579 | 1205176.1744 | 2697958.9299 | 1205177.3831
54 | 2698142.3523 | 1205082.5467 | 2698141.4838 | 1205090.4823 | 2698139.0178 | 1205098.8559
55 | 2697949.9382 | 1205175.473 | 2697948.608 | 1205180.4991 | 2697938.0033 | 1205186.1892
56 | 2697943.6259 | 1205174.4021 | 2697949.9382 | 1205175.473
57 | 2698142.3523 | 1205082.5467 | 2698144.8635 | 1205072.3366 | 2698151.4127 | 1205064.5612 | 2698159.1873 | 1205058.0761
58 | 2698142.3523 | 1205082.5467 | 2698156.2079 | 1205082.9414 | 2698169.2513 | 1205076.2846 | 2698179.2559 | 1205070.7453 | 2698193.3324 | 1205055.8666 | 2698207.7128 | 1205045.6406 | 2698213.8675 | 1205045.1971 | 2698221.3323 | 1205046.9766 | 2698247.8609 | 1205057.2199 | 2698261.8804 | 1205064.2998 | 2698280.2201 | 1205076.9991
59 | 2698002.7687 | 1204913.4017 | 2697997.788 | 1204911.2011 | 2697987.118 | 1204907.2447
60 | 2698017.4952 | 1204919.9082 | 2698002.7687 | 1204913.4017
61 | 2697938.0033 | 1205186.1892 | 2697926.0378 | 1205237.3564
62 | 2697943.6259 | 1205174.4021 | 2697946.5135 | 1205163.9535 | 2697942.3418 | 1205155.6131
63 | 2697868.112 | 1205268.8281 | 2697893.7107 | 1205255.4942 | 2697926.0378 | 1205237.3564
64 | 2697868.112 | 1205268.8281 | 2697922.8789 | 1205264.8121 | 2697936.846 | 1205270.8891
65 | 2698075.7265 | 1204948.3501 | 2698090.2203 | 1204923.2035
66 | 2698074.1968 | 1204951.1491 | 2698075.7265 | 1204948.3501
67 | 2698074.1968 | 1204951.1491 | 2698061.1289 | 1204944.4807
68 | 2698074.1968 | 1204951.1491 | 2698079.8481 | 1204954.0327 | 2698088.5778 | 1204958.5111
69 | 2698074.1968 | 1204951.1491 | 2698067.8273 | 1204962.808 | 2698068.6865 | 1204964.6592
70 | 2698111.0888 | 1204966.0096 | 2698116.3409 | 1204955.1644
71 | 2698118.7067 | 1204968.6698 | 2698113.8358 | 1204967.3778 | 2698111.0888 | 1204966.0096
72 | 2698125.8536 | 1204936.8082 | 2698118.9094 | 1204949.8604 | 2698116.3409 | 1204955.1644
73 | 2698118.7067 | 1204968.6698 | 2698126.9182 | 1204970.8507 | 2698144.2142 | 1204968.3999 | 2698151.3867 | 1204968.535
74 | 2698118.7067 | 1204968.6698 | 2698118.0245 | 1204972.2166
75 | 2698042.0251 | 1204934.6561 | 2698057.3789 | 1204942.5671 | 2698061.1289 | 1204944.4807
76 | 2698088.5778 | 1204958.5111 | 2698106.9748 | 1204967.9488
77 | 2698082.4281 | 1204976.4544 | 2698080.0525 | 1204974.928 | 2698070.9944 | 1204969.6313 | 2698068.6865 | 1204964.6592
78 | 2698020.4863 | 1204921.2359 | 2698019.3989 | 1204920.74 | 2698017.4952 | 1204919.9082
79 | 2698020.4863 | 1204921.2359 | 2698036.1942 | 1204846.9392
80 | 2698017.4952 | 1204919.9082 | 2698016.7668 | 1204921.6418
81 | 2698207.2818 | 1204947.9059 | 2698200.7327 | 1204958.9114 | 2698194.2218 | 1204959.7271 | 2698186.8438 | 1204956.8261 | 2698184.1815 | 1204949.3884 | 2698185.0334 | 1204935.5263 | 2698188.5122 | 1204911.8341 | 2698194.0623 | 1204894.0466 | 2698193.9863 | 1204880.1693 | 2698191.3342 | 1204872.1091 | 2698182.7365 | 1204867.9538 | 2698174.666 | 1204869.6779 | 2698170.2062 | 1204877.6211 | 2698167.5211 | 1204890.5301 | 2698162.0015 | 1204906.4725 | 2698150.6731 | 1204918.0052 | 2698136.6193 | 1204926.4022 | 2698127.5298 | 1204933.6577 | 2698125.8536 | 1204936.8082
82 | 2698118.0245 | 1204972.2166 | 2698111.924 | 1205003.8482
83 | 2698118.0245 | 1204972.2166 | 2698121.2125 | 1204973.1363 | 2698126.4646 | 1204973.4561 | 2698139.8397 | 1204972.0508
84 | 2698118.0245 | 1204972.2166 | 2698111.8226 | 1204970.4357 | 2698106.9748 | 1204967.9488
85 | 2698016.7668 | 1204921.6418 | 2698042.0251 | 1204934.6561
86 | 2698096.1444 | 1204994.35 | 2698090.4949 | 1204981.6374 | 2698082.4281 | 1204976.4544
87 | 2698016.7668 | 1204921.6418 | 2698008.996 | 1204917.6338 | 2697999.9659 | 1204914.2695
88 | 2698016.7668 | 1204921.6418 | 2698009.4904 | 1204938.9564 | 2698005.6976 | 1204947.9891 | 2698005.2069 | 1204949.1485
89 | 2698207.5574 | 1204947.4429 | 2698207.2818 | 1204947.9059
90 | 2698207.5574 | 1204947.4429 | 2698209.6373 | 1204943.9477 | 2698212.8591 | 1204932.3243
91 | 2698216.0033 | 1204920.9811 | 2698212.8591 | 1204932.3243
92 | 2698224.0742 | 1204899.3326 | 2698216.8684 | 1204917.86 | 2698216.0033 | 1204920.9811
93 | 2698232.6309 | 1204894.4145 | 2698224.0742 | 1204899.3326
94 | 2698232.6309 | 1204894.4145 | 2698244.3202 | 1204898.8653 | 2698247.4245 | 1204909.9572 | 2698247.4245 | 1204909.9572
95 | 2698009.0594 | 1204957.7843 | 2698005.2069 | 1204949.1485
96 | 2698111.8448 | 1205004.259 | 2698111.924 | 1205003.8482
97 | 2698139.8397 | 1204972.0508 | 2698141.1054 | 1204971.9179 | 2698144.0717 | 1204971.5108 | 2698151.5869 | 1204970.7004 | 2698156.6018 | 1204971.5612 | 2698164.127 | 1204974.7648 | 2698176.5688 | 1204985.1561
98 | 2698188.7902 | 1204996.2181 | 2698187.9959 | 1204995.0154 | 2698179.3775 | 1204987.5019 | 2698176.5688 | 1204985.1561
99 | 2698188.7902 | 1204996.2181 | 2698191.3766 | 1204994.3928
100 | 2698188.7902 | 1204996.2181 | 2698185.4496 | 1204998.5648 | 2698155.1916 | 1205020.6788
101 | 2698270.0817 | 1204930.5596 | 2698268.3095 | 1204939.3367
102 | 2698266.0134 | 1204950.7091 | 2698268.3095 | 1204939.3367
103 | 2698266.0134 | 1204950.7091 | 2698263.8168 | 1204961.5881
104 | 2698270.2661 | 1204978.2683 | 2698264.8586 | 1204972.1418 | 2698263.2869 | 1204968.2467 | 2698263.2515 | 1204964.3879 | 2698263.8168 | 1204961.5881
105 | 2698270.2661 | 1204978.2683 | 2698272.9528 | 1204972.6642 | 2698276.2265 | 1204970.117
106 | 2698270.2661 | 1204978.2683 | 2698269.5177 | 1204979.8237 | 2698269.0174 | 1204987.5652 | 2698276.9037 | 1205009.9471
107 | 2698302.2291 | 1204973.1798 | 2698297.2845 | 1204968.0282 | 2698292.2564 | 1204965.6549 | 2698285.7414 | 1204965.3364 | 2698279.4036 | 1204967.6448 | 2698276.2265 | 1204970.117
108 | 2698276.9037 | 1205009.9471 | 2698280.7562 | 1205020.8809 | 2698285.3394 | 1205031.786 | 2698292.8418 | 1205040.9824 | 2698298.032 | 1205050.1407 | 2698300.4233 | 1205059.6976 | 2698296.4155 | 1205073.4521 | 2698288.4586 | 1205078.4579 | 2698280.2201 | 1205076.9991 | 2698280.2201 | 1205076.9991
109 | 2698302.2291 | 1204973.1798 | 2698305.1459 | 1204976.2187 | 2698310.1148 | 1204987.8425
110 | 2698159.1873 | 1205058.0761 | 2698176.4325 | 1205043.6913
111 | 2698176.4325 | 1205043.6913 | 2698187.5299 | 1205034.4345 | 2698195.0557 | 1205024.1846 | 2698196.4467 | 1205019.9526
112 | 2698318.5721 | 1205007.6266 | 2698310.1148 | 1204987.8425
113 | 2698322.1406 | 1205015.2353 | 2698320.2814 | 1205011.6252 | 2698318.5721 | 1205007.6266
114 | 2698155.1916 | 1205020.6788 | 2698138.6356 | 1205032.7787
115 | 2698191.3766 | 1204994.3928 | 2698195.1027 | 1205000.0579 | 2698197.8109 | 1205015.802 | 2698196.4467 | 1205019.9526
116 | 2698244.5714 | 1204918.4917 | 2698247.4245 | 1204909.9572

## bus_geodata
| x | y | coords
0 | 2697359.1016 | 1206257.7652
1 | 2697351.1143 | 1206209.0371
2 | 2697358.5894 | 1206312.6738
3 | 2697367.2288 | 1206183.6427
4 | 2697338.9664 | 1206209.3697
5 | 2697410.7028 | 1206173.7739
6 | 2697369.7923 | 1206308.1089
7 | 2697325.7188 | 1206349.3852
8 | 2697376.3651 | 1206173.825
9 | 2697436.4258 | 1206169.7687
10 | 2697446.2468 | 1206165.0543
11 | 2697426.3585 | 1206170.3414
12 | 2697430.8342 | 1205978.7526
13 | 2697453.3064 | 1206235.8334
14 | 2697381.1122 | 1206347.0174
15 | 2697678.9264 | 1205947.9733
16 | 2697464.7808 | 1206228.6269
17 | 2697695.1504 | 1205937.9569
18 | 2697723.5303 | 1205923.4378
19 | 2697760.4281 | 1205871.6844
20 | 2699113.6274 | 1205219.6073
21 | 2699114.6711 | 1205222.0189
22 | 2699100.1317 | 1205188.4242
23 | 2699141.9228 | 1205239.0141
24 | 2699026.8432 | 1205183.3717
25 | 2699180.5601 | 1205237.6596
26 | 2698797.1291 | 1205195.075
27 | 2699313.9342 | 1205385.0264
28 | 2698712.1109 | 1205375.7254
29 | 2698623.5012 | 1205242.3039
30 | 2699382.9342 | 1205315.0248
31 | 2699367.687 | 1205344.6719
32 | 2698155.218 | 1205669.7077
33 | 2698029.1253 | 1205565.9661
34 | 2698231.8878 | 1205691.5547
35 | 2697901.4649 | 1205503.0337
36 | 2698121.2665 | 1205365.6425
37 | 2698086.6835 | 1205314.9399
38 | 2697980.0613 | 1206062.5917
39 | 2697984.5794 | 1206064.9341
40 | 2697890.1923 | 1205522.2563
41 | 2697714.4384 | 1205620.161
42 | 2697704.8937 | 1205624.758
43 | 2697642.5936 | 1205627.1239
44 | 2697492.9065 | 1205662.6912
45 | 2697709.7694 | 1205867.2078
46 | 2697473.7384 | 1205694.8359
47 | 2698040.1933 | 1205140.3695
48 | 2698037.842 | 1205129.5771
49 | 2698047.3188 | 1205155.2462
50 | 2697971.7168 | 1205180.5552
51 | 2698181.255 | 1205204.9693
52 | 2697958.9299 | 1205177.3831
53 | 2698139.0178 | 1205098.8559
54 | 2697949.9382 | 1205175.473
55 | 2698142.3523 | 1205082.5467
56 | 2697987.118 | 1204907.2447
57 | 2698002.7687 | 1204913.4017
58 | 2697938.0033 | 1205186.1892
59 | 2697943.6259 | 1205174.4021
60 | 2697926.0378 | 1205237.3564
61 | 2697942.3418 | 1205155.6131
62 | 2697936.846 | 1205270.8891
63 | 2697868.112 | 1205268.8281
64 | 2698090.2203 | 1204923.2035
65 | 2698075.7265 | 1204948.3501
66 | 2698074.1968 | 1204951.1491
67 | 2698111.0888 | 1204966.0096
68 | 2698116.3409 | 1204955.1644
69 | 2698118.7067 | 1204968.6698
70 | 2698061.1289 | 1204944.4807
71 | 2698088.5778 | 1204958.5111
72 | 2698068.6865 | 1204964.6592
73 | 2698020.4863 | 1204921.2359
74 | 2698017.4952 | 1204919.9082
75 | 2698036.1942 | 1204846.9392
76 | 2698125.8536 | 1204936.8082
77 | 2698151.3867 | 1204968.535
78 | 2698118.0245 | 1204972.2166
79 | 2698042.0251 | 1204934.6561
80 | 2698106.9748 | 1204967.9488
81 | 2698082.4281 | 1204976.4544
82 | 2698016.7668 | 1204921.6418
83 | 2698207.5574 | 1204947.4429
84 | 2698207.2818 | 1204947.9059
85 | 2698212.8591 | 1204932.3243
86 | 2698216.0033 | 1204920.9811
87 | 2698224.0742 | 1204899.3326
88 | 2698232.6309 | 1204894.4145
89 | 2698005.2069 | 1204949.1485
90 | 2698009.0594 | 1204957.7843
91 | 2697999.9659 | 1204914.2695
92 | 2698096.1444 | 1204994.35
93 | 2698111.924 | 1205003.8482
94 | 2698139.8397 | 1204972.0508
95 | 2698111.8448 | 1205004.259
96 | 2698176.5688 | 1204985.1561
97 | 2698188.7902 | 1204996.2181
98 | 2698270.0817 | 1204930.5596
99 | 2698268.3095 | 1204939.3367
100 | 2698266.0134 | 1204950.7091
101 | 2698263.8168 | 1204961.5881
102 | 2698270.2661 | 1204978.2683
103 | 2698276.2265 | 1204970.117
104 | 2698276.9037 | 1205009.9471
105 | 2698302.2291 | 1204973.1798
106 | 2698280.2201 | 1205076.9991
107 | 2698159.1873 | 1205058.0761
108 | 2698176.4325 | 1205043.6913
109 | 2698310.1148 | 1204987.8425
110 | 2698322.1406 | 1205015.2353
111 | 2698318.5721 | 1205007.6266
112 | 2698155.1916 | 1205020.6788
113 | 2698138.6356 | 1205032.7787
114 | 2698191.3766 | 1204994.3928
115 | 2698196.4467 | 1205019.9526
116 | 2698244.5714 | 1204918.4917
117 | 2698247.4245 | 1204909.9572
118 | 2698142.3523 | 1205082.5467

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97046 | -0.21039 | 0.00028121 | 7.0477e-05
1 | 0.97072 | -0.20852 | 0 | 0
2 | 0.97021 | -0.21223 | 0 | 0
3 | 0.97057 | -0.20958 | 0.00074993 | 0.00018795
4 | 0.97071 | -0.20857 | 0.00043099 | 0.00010802
5 | 0.97148 | -0.20299 | 0 | 0
6 | 0.9702 | -0.21231 | 0 | 0
7 | 0.97003 | -0.21354 | 0.0025097 | 0.00062899
8 | 0.97052 | -0.20993 | 0.0024901 | 0.00062408
9 | 0.97144 | -0.2033 | 0 | 0
10 | 0.97143 | -0.20338 | 0.00066502 | 0.00016667
11 | 0.97145 | -0.20323 | 0.00075115 | 0.00018826
12 | 0.9741 | -0.18403 | 0.00095124 | 0.0002384
13 | 0.97016 | -0.21262 | 0 | 0
14 | 0.97017 | -0.21257 | 0.00035829 | 8.9796e-05
15 | 0.97757 | -0.15907 | 0.00026132 | 6.5494e-05
16 | 0.97015 | -0.21266 | 0.00026042 | 6.5268e-05
17 | 0.97784 | -0.15712 | 0.00022132 | 5.5467e-05
18 | 0.97831 | -0.15378 | 0 | 0
19 | 0.9793 | -0.14664 | 0 | 0
20 | 0.97979 | -0.14339 | 0.0012456 | 0.00031218
21 | 0.97977 | -0.14352 | 0.00068882 | 0.00017264
22 | 0.98008 | -0.14132 | 0 | 0
23 | 0.97956 | -0.14505 | 0.0012951 | 0.00032459
24 | 0.98073 | -0.13664 | 0.00021704 | 5.4395e-05
25 | 0.97941 | -0.14612 | 0 | 0
26 | 0.98275 | -0.12208 | 0.00069278 | 0.00017363
27 | 0.97865 | -0.15157 | 0.00060333 | 0.00015121
28 | 0.98447 | -0.10981 | 0.00023485 | 5.886e-05
29 | 0.98452 | -0.1094 | 0 | 0
30 | 0.97841 | -0.15333 | 0.00067236 | 0.00016851
31 | 0.97844 | -0.15307 | 0.0013373 | 0.00033516
32 | 0.98946 | -0.074258 | 0.00025163 | 6.3063e-05
33 | 0.9902 | -0.068944 | 0.00014093 | 3.5321e-05
34 | 0.98913 | -0.076559 | 0.0028074 | 0.0007036
35 | 0.98876 | -0.079196 | 0 | 0
36 | 0.99294 | -0.049551 | 0.0017402 | 0.00043613
37 | 0.99378 | -0.043622 | 0.0012302 | 0.00030833
38 | 0.97887 | -0.14977 | 0 | 0
39 | 0.97886 | -0.14982 | 0.0010174 | 0.00025498
40 | 0.98843 | -0.081533 | 0.00066186 | 0.00016588
41 | 0.98455 | -0.10914 | 0.00035236 | 8.8309e-05
42 | 0.98435 | -0.11056 | 0.00030042 | 7.5292e-05
43 | 0.98426 | -0.11118 | 0 | 0
44 | 0.98407 | -0.11258 | 0.00027505 | 6.8933e-05
45 | 0.9802 | -0.14019 | 0.00071805 | 0.00017996
46 | 0.98403 | -0.11281 | 0.00059106 | 0.00014813
47 | 0.9915 | -0.059684 | 0.0027426 | 0.00068736
48 | 0.99146 | -0.059929 | 0.0021751 | 0.00054513
49 | 0.99162 | -0.058793 | 0 | 0
50 | 0.98997 | -0.07045 | 0.0012522 | 0.00031382
51 | 0.99589 | -0.028742 | 0.0016783 | 0.00042063
52 | 0.98975 | -0.072011 | 0.0034515 | 0.00086502
53 | 1 | 0 | -0.17864 | -0.044922
54 | 0.98965 | -0.072777 | 0 | 0
55 | 0.99836 | -0.011304 | 0 | 0
56 | 0.9718 | -0.19833 | 0.00020823 | 5.2187e-05
57 | 0.97181 | -0.1983 | 0.0050484 | 0.0012652
58 | 0.98947 | -0.07405 | 0.0015836 | 0.0003969
59 | 0.98964 | -0.072838 | 0 | 0
60 | 0.98904 | -0.077084 | 0.0043664 | 0.0010943
61 | 0.98961 | -0.073029 | 0.00092732 | 0.00023241
62 | 0.98879 | -0.078867 | 0.0012786 | 0.00032045
63 | 0.98892 | -0.077949 | 0 | 0
64 | 0.97455 | -0.17859 | 0.0041728 | 0.0010458
65 | 0.97472 | -0.17732 | 0 | 0
66 | 0.97474 | -0.17718 | 0 | 0
67 | 0.97844 | -0.15075 | 0 | 0
68 | 0.9782 | -0.15251 | 0.0011743 | 0.0002943
69 | 0.97861 | -0.14958 | 0 | 0
70 | 0.974 | -0.18252 | 0.0045944 | 0.0011515
71 | 0.97597 | -0.1684 | 0.003989 | 0.00099974
72 | 0.97445 | -0.17927 | 0.0041128 | 0.0010308
73 | 0.97191 | -0.19752 | 0 | 0
74 | 0.97193 | -0.1974 | 0 | 0
75 | 0.97153 | -0.20029 | 0.0034414 | 0.00086251
76 | 0.97781 | -0.15526 | 0.004294 | 0.0010762
77 | 0.97854 | -0.15008 | 0.0014355 | 0.00035978
78 | 0.97869 | -0.149 | 0 | 0
79 | 0.97305 | -0.18932 | 0.00365 | 0.00091479
80 | 0.97766 | -0.15633 | 0.0032833 | 0.00082288
81 | 0.97421 | -0.18103 | 0.0051294 | 0.0012855
82 | 0.97195 | -0.19723 | 0 | 0
83 | 0.9751 | -0.17468 | 0.0017731 | 0.00044439
84 | 0.97511 | -0.17464 | 0.0013573 | 0.00034017
85 | 0.97498 | -0.17559 | 0.0010825 | 0.0002713
86 | 0.97491 | -0.17611 | 0.0013592 | 0.00034064
87 | 0.97481 | -0.17681 | 0.0011648 | 0.00029193
88 | 0.97478 | -0.17699 | 0 | 0
89 | 0.97143 | -0.20102 | 0.0060386 | 0.0015134
90 | 0.97134 | -0.20162 | 0.0059789 | 0.0014985
91 | 0.9718 | -0.19833 | 0.005653 | 0.0014168
92 | 0.97408 | -0.18195 | 0.003744 | 0.00093834
93 | 0.97844 | -0.15078 | 0.0031547 | 0.00079065
94 | 0.98125 | -0.13074 | 0.012618 | 0.0031623
95 | 0.97844 | -0.15079 | 0.0021412 | 0.00053663
96 | 0.98683 | -0.09141 | 0.0033586 | 0.00084175
97 | 0.98914 | -0.075223 | 0 | 0
98 | 0.98949 | -0.073776 | 0.0012682 | 0.00031783
99 | 0.98951 | -0.07366 | 0.0011415 | 0.00028609
100 | 0.98955 | -0.073375 | 0.0012183 | 0.00030533
101 | 0.98961 | -0.072965 | 0.0015368 | 0.00038515
102 | 0.98975 | -0.071959 | 0 | 0
103 | 0.98954 | -0.073408 | 0.0013672 | 0.00034266
104 | 0.99065 | -0.065574 | 0.0015406 | 0.00038611
105 | 0.98901 | -0.077184 | 0.001168 | 0.00029273
106 | 0.99322 | -0.047385 | 0.002192 | 0.00054936
107 | 0.99583 | -0.028725 | 0.0033072 | 0.00082886
108 | 0.99404 | -0.041106 | 0.0037481 | 0.00093935
109 | 0.98874 | -0.079106 | 0.0015595 | 0.00039084
110 | 0.98835 | -0.081899 | 0.00079661 | 0.00019965
111 | 0.98845 | -0.081218 | 0.0016914 | 0.00042391
112 | 0.98882 | -0.077509 | 0.0030442 | 0.00076294
113 | 0.98875 | -0.077999 | 0.0023422 | 0.00058702
114 | 0.98961 | -0.071964 | 0 | 0
115 | 0.99161 | -0.058012 | 0.0044575 | 0.0011172
116 | 0.97471 | -0.17752 | 0.0010916 | 0.00027357
117 | 0.97472 | -0.17742 | 0.00061823 | 0.00015494
118 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0034109 | -0.00085121 | 0.0034118 | 0.00085091 | 8.7731e-07 | -2.9819e-07 | 0.0052286 | 0.0052284 | 0.0052286 | 0.97046 | -0.21039 | 0.97072 | -0.20852 | 1.9365
1 | 0.0031297 | 0.00078074 | -0.0031289 | -0.00078111 | 7.8866e-07 | -3.7496e-07 | 0.0047975 | 0.0047977 | 0.0047977 | 0.97046 | -0.21039 | 0.97021 | -0.21223 | 1.7769
2 | 0.0032407 | 0.00081172 | -0.0032402 | -0.00081192 | 4.7566e-07 | -1.9888e-07 | 0.0049674 | 0.0049676 | 0.0049676 | 0.97072 | -0.20852 | 0.97057 | -0.20958 | 1.8398
3 | 0.00043099 | 0.00010787 | -0.00043099 | -0.00010802 | 3.3096e-09 | -1.4896e-07 | 0.00066061 | 0.00066066 | 0.00066066 | 0.97072 | -0.20852 | 0.97071 | -0.20857 | 0.24469
4 | -0.0070834 | -0.0017705 | 0.0070888 | 0.0017717 | 5.3976e-06 | 1.168e-06 | 0.010856 | 0.010856 | 0.010856 | 0.97072 | -0.20852 | 0.97148 | -0.20299 | 4.0209
5 | 0.00061874 | 0.00015255 | -0.00061873 | -0.0001527 | 6.7689e-09 | -1.4643e-07 | 0.00094806 | 0.00094811 | 0.00094811 | 0.97021 | -0.21223 | 0.9702 | -0.21231 | 0.35115
6 | 0.0025102 | 0.00062856 | -0.0025097 | -0.00062899 | 4.5572e-07 | -4.3315e-07 | 0.0038496 | 0.0038499 | 0.0038499 | 0.97021 | -0.21223 | 0.97003 | -0.21354 | 1.4259
7 | 0.0024902 | 0.00062397 | -0.0024901 | -0.00062408 | 1.2198e-07 | -1.1882e-07 | 0.0038178 | 0.0038179 | 0.0038179 | 0.97057 | -0.20958 | 0.97052 | -0.20993 | 1.414
8 | -0.008505 | -0.0021262 | 0.0085273 | 0.0021321 | 2.2237e-05 | 5.9446e-06 | 0.013025 | 0.013024 | 0.013025 | 0.97148 | -0.20299 | 0.9741 | -0.18403 | 4.8241
9 | 0.0014162 | 0.00035449 | -0.0014162 | -0.00035467 | 4.7818e-08 | -1.8326e-07 | 0.0021691 | 0.0021691 | 0.0021691 | 0.97148 | -0.20299 | 0.97145 | -0.20323 | 0.80339
10 | 0.00026043 | 6.3723e-05 | -0.00026042 | -6.509e-05 | 1.1033e-08 | -1.3664e-06 | 0.00039888 | 0.00039937 | 0.00039937 | 0.9702 | -0.21231 | 0.97016 | -0.21262 | 0.14791
11 | 0.0003583 | 8.8976e-05 | -0.00035829 | -8.9796e-05 | 1.2575e-08 | -8.1967e-07 | 0.00054924 | 0.00054953 | 0.00054953 | 0.9702 | -0.21231 | 0.97017 | -0.21257 | 0.20353
12 | 0.00066503 | 0.00016654 | -0.00066502 | -0.00016667 | 7.0872e-09 | -1.3279e-07 | 0.0010186 | 0.0010187 | 0.0010187 | 0.97144 | -0.2033 | 0.97143 | -0.20338 | 0.37728
13 | -0.00066503 | -0.00016654 | 0.00066503 | 0.00016641 | 6.5283e-09 | -1.2233e-07 | 0.0010186 | 0.0010186 | 0.0010186 | 0.97144 | -0.2033 | 0.97145 | -0.20323 | 0.37726
14 | -0.0094785 | -0.0023705 | 0.0095112 | 0.00238 | 3.2693e-05 | 9.4511e-06 | 0.014477 | 0.014476 | 0.014477 | 0.9741 | -0.18403 | 0.97757 | -0.15907 | 5.362
15 | 0.00026042 | 6.509e-05 | -0.00026042 | -6.5268e-05 | 1.4404e-09 | -1.7812e-07 | 0.00039937 | 0.00039943 | 0.00039943 | 0.97016 | -0.21262 | 0.97015 | -0.21266 | 0.14794
16 | -0.0097725 | -0.0024454 | 0.0097752 | 0.0024462 | 2.6322e-06 | 7.7326e-07 | 0.014874 | 0.014874 | 0.014874 | 0.97757 | -0.15907 | 0.97784 | -0.15712 | 5.5089
17 | -0.0099965 | -0.0025017 | 0.010001 | 0.0025031 | 4.6109e-06 | 1.3726e-06 | 0.015211 | 0.015211 | 0.015211 | 0.97784 | -0.15712 | 0.97831 | -0.15378 | 5.6336
18 | -0.010001 | -0.0025031 | 0.010011 | 0.002506 | 9.8573e-06 | 2.9331e-06 | 0.015211 | 0.01521 | 0.015211 | 0.97831 | -0.15378 | 0.9793 | -0.14664 | 5.6335
19 | -0.011029 | -0.0027574 | 0.011039 | 0.0027605 | 9.814e-06 | 3.0691e-06 | 0.016755 | 0.016755 | 0.016755 | 0.9793 | -0.14664 | 0.9802 | -0.14019 | 6.2057
20 | 0.0010178 | 0.00025142 | -0.0010174 | -0.00025492 | 4.3394e-07 | -3.4929e-06 | 0.0015452 | 0.0015465 | 0.0015465 | 0.9793 | -0.14664 | 0.97887 | -0.14977 | 0.57279
21 | 0.0046007 | 0.0011487 | -0.0046006 | -0.0011487 | 8.0014e-08 | -2.3193e-09 | 0.0069855 | 0.0069855 | 0.0069855 | 0.97979 | -0.14339 | 0.97977 | -0.14352 | 2.5872
22 | -0.0058463 | -0.0014609 | 0.0058479 | 0.0014611 | 1.6708e-06 | 2.1457e-07 | 0.0088772 | 0.0088771 | 0.0088772 | 0.97979 | -0.14339 | 0.98008 | -0.14132 | 3.2879
23 | 0.0039118 | 0.00097604 | -0.0039109 | -0.0009762 | 8.2127e-07 | -1.5388e-07 | 0.0059394 | 0.0059396 | 0.0059396 | 0.97977 | -0.14352 | 0.97956 | -0.14505 | 2.1998
24 | -0.0058479 | -0.0014611 | 0.0058517 | 0.0014615 | 3.7597e-06 | 4.8184e-07 | 0.0088771 | 0.0088767 | 0.0088771 | 0.98008 | -0.14132 | 0.98073 | -0.13664 | 3.2878
25 | 0.0026158 | 0.0006516 | -0.0026154 | -0.00065194 | 3.8206e-07 | -3.4146e-07 | 0.0039721 | 0.0039723 | 0.0039723 | 0.97956 | -0.14505 | 0.97941 | -0.14612 | 1.4712
26 | -0.0060687 | -0.0015159 | 0.0060809 | 0.0015177 | 1.2163e-05 | 1.7696e-06 | 0.009206 | 0.009205 | 0.009206 | 0.98073 | -0.13664 | 0.98275 | -0.12208 | 3.4096
27 | 0.0026154 | 0.00065194 | -0.0026135 | -0.00065369 | 1.9575e-06 | -1.7465e-06 | 0.0039723 | 0.0039732 | 0.0039732 | 0.97941 | -0.14612 | 0.97865 | -0.15157 | 1.4716
28 | -0.0067737 | -0.0016913 | 0.0067855 | 0.0016936 | 1.1805e-05 | 2.2562e-06 | 0.010254 | 0.010253 | 0.010254 | 0.98275 | -0.12208 | 0.98452 | -0.1094 | 3.7978
29 | 0.0020101 | 0.00050248 | -0.0020097 | -0.00050322 | 4.1829e-07 | -7.408e-07 | 0.0030559 | 0.0030562 | 0.0030562 | 0.97865 | -0.15157 | 0.97844 | -0.15307 | 1.1319
30 | -0.00023485 | -5.886e-05 | 0.00023487 | 5.6797e-05 | 1.2763e-08 | -2.0632e-06 | 0.00035498 | 0.00035426 | 0.00035498 | 0.98447 | -0.10981 | 0.98452 | -0.1094 | 0.13147
31 | -0.0070203 | -0.0017504 | 0.0070468 | 0.0017558 | 2.6488e-05 | 5.3709e-06 | 0.010607 | 0.010606 | 0.010607 | 0.98452 | -0.1094 | 0.98835 | -0.081899 | 3.9287
32 | -0.00067236 | -0.00016851 | 0.00067239 | 0.00016806 | 2.3924e-08 | -4.5138e-07 | 0.0010226 | 0.0010224 | 0.0010226 | 0.97841 | -0.15333 | 0.97844 | -0.15307 | 0.37873
33 | -0.0030599 | -0.00076598 | 0.0030622 | 0.00076466 | 2.2413e-06 | -1.3189e-06 | 0.0046014 | 0.0046007 | 0.0046014 | 0.98946 | -0.074258 | 0.9902 | -0.068944 | 1.7042
34 | 0.0028083 | 0.00070292 | -0.0028074 | -0.0007036 | 8.9347e-07 | -6.8716e-07 | 0.004223 | 0.0042234 | 0.0042234 | 0.98946 | -0.074258 | 0.98913 | -0.076559 | 1.5642
35 | 0.014064 | 0.003522 | -0.014044 | -0.003518 | 1.9923e-05 | 3.9898e-06 | 0.021133 | 0.021134 | 0.021134 | 0.9902 | -0.068944 | 0.98876 | -0.079196 | 3.9138
36 | -0.017267 | -0.004322 | 0.017313 | 0.0043341 | 4.6308e-05 | 1.2122e-05 | 0.025946 | 0.025944 | 0.025946 | 0.9902 | -0.068944 | 0.99294 | -0.049551 | 4.8047
37 | 0.014044 | 0.003518 | -0.014039 | -0.0035171 | 4.5378e-06 | 9.1032e-07 | 0.021134 | 0.021135 | 0.021135 | 0.98876 | -0.079196 | 0.98843 | -0.081533 | 3.9138
38 | -0.019053 | -0.0047702 | 0.019069 | 0.0047746 | 1.5614e-05 | 4.416e-06 | 0.028551 | 0.028551 | 0.028551 | 0.99294 | -0.049551 | 0.99378 | -0.043622 | 5.2873
39 | -0.020299 | -0.005083 | 0.020341 | 0.0050953 | 4.18e-05 | 1.231e-05 | 0.030393 | 0.030392 | 0.030393 | 0.99378 | -0.043622 | 0.99589 | -0.028742 | 5.6283
40 | 0.0010174 | 0.00025492 | -0.0010174 | -0.00025498 | 7.5787e-09 | -6.0919e-08 | 0.0015465 | 0.0015465 | 0.0015465 | 0.97887 | -0.14977 | 0.97886 | -0.14982 | 0.57279
41 | 0.013377 | 0.0033512 | -0.013326 | -0.0033342 | 5.0915e-05 | 1.7014e-05 | 0.020138 | 0.020139 | 0.020139 | 0.98843 | -0.081533 | 0.98455 | -0.10914 | 7.459
42 | 0.012974 | 0.0032459 | -0.012972 | -0.003245 | 2.5413e-06 | 8.4273e-07 | 0.019607 | 0.019607 | 0.019607 | 0.98455 | -0.10914 | 0.98435 | -0.11056 | 7.2618
43 | 0.011805 | 0.0029559 | -0.011757 | -0.0029404 | 4.8185e-05 | 1.5463e-05 | 0.017844 | 0.017845 | 0.017845 | 0.98435 | -0.11056 | 0.9802 | -0.14019 | 6.6093
44 | 0.00086636 | 0.00021385 | -0.00086629 | -0.0002147 | 7.3383e-08 | -8.446e-07 | 0.0013085 | 0.0013088 | 0.0013088 | 0.98435 | -0.11056 | 0.98426 | -0.11118 | 0.48474
45 | 0.00086629 | 0.0002147 | -0.00086613 | -0.00021659 | 1.6454e-07 | -1.8918e-06 | 0.0013088 | 0.0013095 | 0.0013095 | 0.98426 | -0.11118 | 0.98407 | -0.11258 | 0.485
46 | 0.00059108 | 0.00014765 | -0.00059106 | -0.00014813 | 1.9104e-08 | -4.7963e-07 | 0.0008936 | 0.00089378 | 0.00089378 | 0.98407 | -0.11258 | 0.98403 | -0.11281 | 0.33103
47 | 0.0021752 | 0.00054502 | -0.0021751 | -0.00054513 | 7.3823e-08 | -1.1478e-07 | 0.0032644 | 0.0032645 | 0.0032645 | 0.9915 | -0.059684 | 0.99146 | -0.059929 | 1.2091
48 | -0.0049178 | -0.0012324 | 0.0049184 | 0.0012324 | 6.0621e-07 | 3.1041e-09 | 0.0073804 | 0.0073803 | 0.0073804 | 0.9915 | -0.059684 | 0.99162 | -0.058793 | 2.7335
49 | 0.012888 | 0.0032293 | -0.012867 | -0.0032225 | 2.0762e-05 | 6.8398e-06 | 0.019339 | 0.019339 | 0.019339 | 0.99162 | -0.058793 | 0.98997 | -0.07045 | 7.1627
50 | -0.017806 | -0.0044617 | 0.01788 | 0.0044881 | 7.433e-05 | 2.6427e-05 | 0.026719 | 0.026718 | 0.026719 | 0.99162 | -0.058793 | 0.99589 | -0.028742 | 9.896
51 | 0.011615 | 0.0029087 | -0.011612 | -0.0029079 | 2.5054e-06 | 7.9424e-07 | 0.017457 | 0.017457 | 0.017457 | 0.98997 | -0.07045 | 0.98975 | -0.072011 | 6.4657
52 | -0.0399 | -0.010004 | 0.040059 | 0.010062 | 0.00015949 | 5.7583e-05 | 0.059618 | 0.059616 | 0.059618 | 0.99589 | -0.028742 | 1 | 0 | 11.0403
53 | 0.0081608 | 0.0020428 | -0.00816 | -0.0020426 | 8.6393e-07 | 2.1407e-07 | 0.012268 | 0.012268 | 0.012268 | 0.98975 | -0.072011 | 0.98965 | -0.072777 | 4.5438
54 | 0.13778 | 0.03486 | -0.13756 | -0.034776 | 0.00021941 | 8.3952e-05 | 0.20513 | 0.20513 | 0.20513 | 1 | 0 | 0.99836 | -0.011304 | 37.988
55 | 0.0072326 | 0.0018106 | -0.0072313 | -0.0018103 | 1.2716e-06 | 2.6769e-07 | 0.010874 | 0.010874 | 0.010874 | 0.98965 | -0.072777 | 0.98947 | -0.07405 | 4.0275
56 | 0.00092735 | 0.00023208 | -0.00092734 | -0.00023216 | 7.7438e-09 | -7.9049e-08 | 0.0013942 | 0.0013943 | 0.0013943 | 0.98965 | -0.072777 | 0.98964 | -0.072838 | 0.51639
57 | 0.11484 | 0.02907 | -0.11455 | -0.028962 | 0.0002819 | 0.00010762 | 0.17126 | 0.17126 | 0.17126 | 0.99836 | -0.011304 | 0.99583 | -0.028725 | 31.715
58 | 0.022725 | 0.0057061 | -0.022611 | -0.0056646 | 0.00011339 | 4.1553e-05 | 0.033874 | 0.033875 | 0.033875 | 0.99836 | -0.011304 | 0.99322 | -0.047385 | 12.5462
59 | -0.00020823 | -5.2187e-05 | 0.00020823 | 5.1979e-05 | 1.067e-09 | -2.0805e-07 | 0.00031884 | 0.00031877 | 0.00031884 | 0.9718 | -0.19833 | 0.97181 | -0.1983 | 0.11809
60 | -0.0052566 | -0.0013172 | 0.0052572 | 0.0013173 | 6.5082e-07 | 5.0814e-08 | 0.0080488 | 0.0080487 | 0.0080488 | 0.97181 | -0.1983 | 0.97193 | -0.1974 | 2.981
61 | 0.0056477 | 0.0014134 | -0.0056453 | -0.0014132 | 2.365e-06 | 2.3496e-07 | 0.0084926 | 0.0084928 | 0.0084928 | 0.98947 | -0.07405 | 0.98904 | -0.077084 | 3.1455
62 | 0.00092734 | 0.00023216 | -0.00092732 | -0.00023241 | 2.4463e-08 | -2.4969e-07 | 0.0013943 | 0.0013944 | 0.0013944 | 0.98964 | -0.072838 | 0.98961 | -0.073029 | 0.51643
63 | 0.0012789 | 0.00031882 | -0.0012788 | -0.00031961 | 1.5192e-07 | -7.8576e-07 | 0.0019235 | 0.0019238 | 0.0019238 | 0.98904 | -0.077084 | 0.98892 | -0.077949 | 0.71253
64 | -0.0012786 | -0.00032045 | 0.0012788 | 0.00031961 | 1.6203e-07 | -8.3754e-07 | 0.0019241 | 0.0019238 | 0.0019241 | 0.98879 | -0.078867 | 0.98892 | -0.077949 | 0.71265
65 | -0.0041728 | -0.0010458 | 0.0041736 | 0.0010457 | 7.3521e-07 | -7.8936e-08 | 0.0063714 | 0.0063713 | 0.0063714 | 0.97455 | -0.17859 | 0.97472 | -0.17732 | 2.3598
66 | -0.0041736 | -0.0010457 | 0.0041736 | 0.0010457 | 8.0752e-08 | -8.6789e-09 | 0.0063713 | 0.0063713 | 0.0063713 | 0.97472 | -0.17732 | 0.97474 | -0.17718 | 2.3597
67 | 0.034706 | 0.0087076 | -0.03468 | -0.0086979 | 2.5701e-05 | 9.7021e-06 | 0.052984 | 0.052984 | 0.052984 | 0.97474 | -0.17718 | 0.974 | -0.18252 | 19.6239
68 | -0.051872 | -0.01301 | 0.051935 | 0.013034 | 6.322e-05 | 2.4114e-05 | 0.07919 | 0.07919 | 0.07919 | 0.97474 | -0.17718 | 0.97597 | -0.1684 | 29.3296
69 | 0.012993 | 0.0032564 | -0.012989 | -0.0032551 | 3.7623e-06 | 1.2561e-06 | 0.019834 | 0.019834 | 0.019834 | 0.97474 | -0.17718 | 0.97445 | -0.17927 | 7.346
70 | 0.013947 | 0.0034955 | -0.013944 | -0.0034944 | 3.383e-06 | 1.1498e-06 | 0.021211 | 0.021211 | 0.021211 | 0.97844 | -0.15075 | 0.9782 | -0.15251 | 7.856
71 | -0.013947 | -0.0034955 | 0.01395 | 0.0034963 | 2.2707e-06 | 7.7173e-07 | 0.021211 | 0.021211 | 0.021211 | 0.97844 | -0.15075 | 0.97861 | -0.14958 | 7.856
72 | 0.01277 | 0.0032001 | -0.012765 | -0.0031985 | 4.8686e-06 | 1.6131e-06 | 0.019425 | 0.019425 | 0.019425 | 0.9782 | -0.15251 | 0.97781 | -0.15526 | 7.1944
73 | 0.0014356 | 0.0003594 | -0.0014355 | -0.00035978 | 9.8534e-08 | -3.7843e-07 | 0.0021828 | 0.002183 | 0.002183 | 0.97861 | -0.14958 | 0.97854 | -0.15008 | 0.80851
74 | -0.015385 | -0.0038557 | 0.015386 | 0.0038561 | 1.2335e-06 | 4.2904e-07 | 0.023394 | 0.023394 | 0.023394 | 0.97861 | -0.14958 | 0.97869 | -0.149 | 8.6644
75 | 0.030086 | 0.0075464 | -0.030057 | -0.0075358 | 2.8322e-05 | 1.0626e-05 | 0.045965 | 0.045966 | 0.045966 | 0.974 | -0.18252 | 0.97305 | -0.18932 | 17.0243
76 | -0.055924 | -0.014034 | 0.056018 | 0.014069 | 9.3815e-05 | 3.5824e-05 | 0.085272 | 0.085272 | 0.085272 | 0.97597 | -0.1684 | 0.97766 | -0.15633 | 31.5821
77 | 0.008876 | 0.0022244 | -0.0088739 | -0.0022238 | 2.1549e-06 | 5.947e-07 | 0.013554 | 0.013554 | 0.013554 | 0.97445 | -0.17927 | 0.97421 | -0.18103 | 5.02
78 | -0.0034428 | -0.00086207 | 0.0034428 | 0.00086206 | 5.658e-08 | -1.8689e-08 | 0.0052707 | 0.0052706 | 0.0052707 | 0.97191 | -0.19752 | 0.97193 | -0.1974 | 1.9521
79 | 0.0034428 | 0.00086207 | -0.0034414 | -0.00086251 | 1.3165e-06 | -4.3439e-07 | 0.0052707 | 0.005271 | 0.005271 | 0.97191 | -0.19752 | 0.97153 | -0.20029 | 1.9522
80 | -0.0087001 | -0.0021793 | 0.0087003 | 0.0021794 | 2.0812e-07 | 5.6745e-08 | 0.013319 | 0.013319 | 0.013319 | 0.97193 | -0.1974 | 0.97195 | -0.19723 | 4.9331
81 | 0.0084708 | 0.0021223 | -0.0084482 | -0.0021163 | 2.2681e-05 | 5.9875e-06 | 0.012891 | 0.012892 | 0.012892 | 0.97781 | -0.15526 | 0.97511 | -0.17464 | 4.7746
82 | 0.0052972 | 0.0013274 | -0.0052959 | -0.0013273 | 1.3039e-06 | 9.6812e-08 | 0.0080539 | 0.0080541 | 0.0080541 | 0.97869 | -0.149 | 0.97844 | -0.15078 | 2.983
83 | -0.080046 | -0.020099 | 0.080249 | 0.020177 | 0.00020364 | 7.8047e-05 | 0.12172 | 0.12172 | 0.12172 | 0.97869 | -0.149 | 0.98125 | -0.13074 | 45.0803
84 | 0.059362 | 0.014915 | -0.059301 | -0.014892 | 6.0513e-05 | 2.3125e-05 | 0.090269 | 0.090269 | 0.090269 | 0.97869 | -0.149 | 0.97766 | -0.15633 | 33.4329
85 | 0.026407 | 0.006621 | -0.026378 | -0.0066103 | 2.8916e-05 | 1.0769e-05 | 0.040384 | 0.040384 | 0.040384 | 0.97305 | -0.18932 | 0.97195 | -0.19723 | 14.957
86 | 0.0037445 | 0.00093823 | -0.003744 | -0.00093834 | 4.7967e-07 | -1.0807e-07 | 0.0057193 | 0.0057194 | 0.0057194 | 0.97421 | -0.18103 | 0.97408 | -0.18195 | 2.1183
87 | 0.0056539 | 0.0014169 | -0.005653 | -0.0014168 | 8.593e-07 | 1.0274e-07 | 0.0086558 | 0.0086558 | 0.0086558 | 0.97195 | -0.19723 | 0.9718 | -0.19833 | 3.2059
88 | 0.012024 | 0.003014 | -0.012018 | -0.0030119 | 6.3095e-06 | 2.0571e-06 | 0.018409 | 0.018409 | 0.018409 | 0.97195 | -0.19723 | 0.97143 | -0.20102 | 6.8181
89 | -0.0070908 | -0.0017761 | 0.0070908 | 0.0017761 | 3.9365e-08 | 8.4188e-09 | 0.01082 | 0.01082 | 0.01082 | 0.9751 | -0.17468 | 0.97511 | -0.17464 | 4.0075
90 | 0.0053177 | 0.0013317 | -0.005317 | -0.0013317 | 6.6269e-07 | 5.3711e-08 | 0.0081144 | 0.0081145 | 0.0081145 | 0.9751 | -0.17468 | 0.97498 | -0.17559 | 3.0054
91 | 0.0042345 | 0.0010604 | -0.0042342 | -0.0010604 | 3.0675e-07 | -2.8804e-08 | 0.0064624 | 0.0064624 | 0.0064624 | 0.97498 | -0.17559 | 0.97491 | -0.17611 | 2.3935
92 | 0.002875 | 0.00071979 | -0.0028747 | -0.00071997 | 2.7776e-07 | -1.814e-07 | 0.0043879 | 0.004388 | 0.004388 | 0.97491 | -0.17611 | 0.97481 | -0.17681 | 1.6252
93 | 0.0017099 | 0.00042804 | -0.0017099 | -0.00042815 | 4.1953e-08 | -1.069e-07 | 0.00261 | 0.00261 | 0.00261 | 0.97481 | -0.17681 | 0.97478 | -0.17699 | 0.96668
94 | 0.0017099 | 0.00042815 | -0.0017098 | -0.00042841 | 1.0214e-07 | -2.6021e-07 | 0.00261 | 0.0026101 | 0.0026101 | 0.97478 | -0.17699 | 0.97472 | -0.17742 | 0.96672
95 | 0.0059794 | 0.0014985 | -0.0059789 | -0.0014985 | 4.9501e-07 | 7.3327e-08 | 0.0091592 | 0.0091592 | 0.0091592 | 0.97143 | -0.20102 | 0.97134 | -0.20162 | 3.3923
96 | 0.0021412 | 0.00053662 | -0.0021412 | -0.00053663 | 2.7682e-09 | -4.19e-09 | 0.0032563 | 0.0032563 | 0.0032563 | 0.97844 | -0.15078 | 0.97844 | -0.15079 | 1.206
97 | -0.092867 | -0.023339 | 0.093378 | 0.023535 | 0.00051131 | 0.00019613 | 0.14085 | 0.14085 | 0.14085 | 0.98125 | -0.13074 | 0.98683 | -0.09141 | 52.167
98 | -0.096737 | -0.024377 | 0.096957 | 0.024461 | 0.00021967 | 8.4277e-05 | 0.14592 | 0.14591 | 0.14592 | 0.98683 | -0.09141 | 0.98914 | -0.075223 | 54.0426
99 | -0.10235 | -0.025811 | 0.10239 | 0.025829 | 4.6777e-05 | 1.795e-05 | 0.15402 | 0.15402 | 0.15402 | 0.98914 | -0.075223 | 0.98961 | -0.071964 | 57.0447
100 | 0.0053882 | 0.0013499 | -0.0053865 | -0.0013498 | 1.7039e-06 | 1.2206e-07 | 0.0081056 | 0.0081058 | 0.0081058 | 0.98914 | -0.075223 | 0.98882 | -0.077509 | 3.0022
101 | -0.0012682 | -0.00031783 | 0.0012682 | 0.00031773 | 2.0321e-08 | -1.072e-07 | 0.0019071 | 0.0019071 | 0.0019071 | 0.98949 | -0.073776 | 0.98951 | -0.07366 | 0.70633
102 | -0.0024097 | -0.00060382 | 0.0024098 | 0.00060371 | 9.5062e-08 | -1.1247e-07 | 0.0036237 | 0.0036236 | 0.0036237 | 0.98951 | -0.07366 | 0.98955 | -0.073375 | 1.3421
103 | -0.0036281 | -0.00090904 | 0.0036283 | 0.00090897 | 2.0613e-07 | -6.3307e-08 | 0.0054556 | 0.0054556 | 0.0054556 | 0.98955 | -0.073375 | 0.98961 | -0.072965 | 2.0206
104 | -0.0051651 | -0.0012941 | 0.0051658 | 0.0012942 | 7.1837e-07 | 3.103e-08 | 0.0077663 | 0.0077662 | 0.0077663 | 0.98961 | -0.072965 | 0.98975 | -0.071959 | 2.8764
105 | 0.013645 | 0.0034104 | -0.013642 | -0.0034095 | 2.7204e-06 | 9.1317e-07 | 0.020511 | 0.020511 | 0.020511 | 0.98975 | -0.071959 | 0.98954 | -0.073408 | 7.5967
106 | -0.018811 | -0.0047046 | 0.018827 | 0.0047105 | 1.6572e-05 | 5.9467e-06 | 0.028277 | 0.028277 | 0.028277 | 0.98975 | -0.071959 | 0.99065 | -0.065574 | 10.4731
107 | 0.012275 | 0.0030668 | -0.012269 | -0.0030648 | 6.3747e-06 | 2.0667e-06 | 0.018455 | 0.018455 | 0.018455 | 0.98954 | -0.073408 | 0.98901 | -0.077184 | 6.8353
108 | -0.020368 | -0.0050966 | 0.020419 | 0.0051152 | 5.1249e-05 | 1.8578e-05 | 0.030591 | 0.030591 | 0.030591 | 0.99065 | -0.065574 | 0.99322 | -0.047385 | 11.3301
109 | 0.011101 | 0.002772 | -0.011098 | -0.0027711 | 2.9323e-06 | 9.1159e-07 | 0.016698 | 0.016698 | 0.016698 | 0.98901 | -0.077184 | 0.98874 | -0.079106 | 6.1845
110 | 0.11125 | 0.028133 | -0.11105 | -0.02806 | 0.00019382 | 7.3962e-05 | 0.16632 | 0.16632 | 0.16632 | 0.99583 | -0.028725 | 0.99404 | -0.041106 | 30.7999
111 | 0.1073 | 0.02712 | -0.10705 | -0.027023 | 0.00025482 | 9.7189e-05 | 0.16071 | 0.16071 | 0.16071 | 0.99404 | -0.041106 | 0.99161 | -0.058012 | 29.761
112 | 0.0095384 | 0.0023803 | -0.0095356 | -0.0023795 | 2.7652e-06 | 7.8766e-07 | 0.014351 | 0.014351 | 0.014351 | 0.98874 | -0.079106 | 0.98845 | -0.081218 | 5.3153
113 | -0.0078434 | -0.0019554 | 0.0078442 | 0.0019556 | 7.3127e-07 | 1.7348e-07 | 0.011805 | 0.011805 | 0.011805 | 0.98835 | -0.081899 | 0.98845 | -0.081218 | 4.3722
114 | 0.0023424 | 0.00058681 | -0.0023422 | -0.00058702 | 1.5899e-07 | -2.0188e-07 | 0.0035248 | 0.0035249 | 0.0035249 | 0.98882 | -0.077509 | 0.98875 | -0.077999 | 1.3055
115 | -0.10239 | -0.025829 | 0.10259 | 0.025906 | 0.00020076 | 7.6518e-05 | 0.15402 | 0.15402 | 0.15402 | 0.98961 | -0.071964 | 0.99161 | -0.058012 | 28.5223
116 | -0.0010916 | -0.00027357 | 0.0010916 | 0.00027346 | 1.5592e-08 | -1.0617e-07 | 0.0016664 | 0.0016663 | 0.0016664 | 0.97471 | -0.17752 | 0.97472 | -0.17742 | 0.61718

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18025 | 0.045325

## res_load
| p_mw | q_mvar
0 | 0.00028121 | 7.0477e-05
1 | 0.00074993 | 0.00018795
2 | 0.00043099 | 0.00010802
3 | 0.0025097 | 0.00062899
4 | 0.0024901 | 0.00062408
5 | 0.00066502 | 0.00016667
6 | 0.00075115 | 0.00018826
7 | 0.00095124 | 0.0002384
8 | 0.00035829 | 8.9796e-05
9 | 0.00026132 | 6.5494e-05
10 | 0.00026042 | 6.5268e-05
11 | 0.00022132 | 5.5467e-05
12 | 0.0012456 | 0.00031218
13 | 0.00068882 | 0.00017264
14 | 0.0012951 | 0.00032459
15 | 0.00021704 | 5.4395e-05
16 | 0.00069278 | 0.00017363
17 | 0.00060333 | 0.00015121
18 | 0.00023485 | 5.886e-05
19 | 0.00067236 | 0.00016851
20 | 0.0013373 | 0.00033516
21 | 0.00025163 | 6.3063e-05
22 | 0.00014093 | 3.5321e-05
23 | 0.0028074 | 0.0007036
24 | 0.0017402 | 0.00043613
25 | 0.0012302 | 0.00030833
26 | 0.0010174 | 0.00025498
27 | 0.00066186 | 0.00016588
28 | 0.00035236 | 8.8309e-05
29 | 0.00030042 | 7.5292e-05
30 | 0.00027505 | 6.8933e-05
31 | 0.00071805 | 0.00017996
32 | 0.00059106 | 0.00014813
33 | 0.0027426 | 0.00068736
34 | 0.0021751 | 0.00054513
35 | 0.0012522 | 0.00031382
36 | 0.0016783 | 0.00042063
37 | 0.0034515 | 0.00086502
38 | 0.0016109 | 0.00040372
39 | 0.00020823 | 5.2187e-05
40 | 0.0050484 | 0.0012652
41 | 0.0015836 | 0.0003969
42 | 0.0043664 | 0.0010943
43 | 0.00092732 | 0.00023241
44 | 0.0012786 | 0.00032045
45 | 0.0041728 | 0.0010458
46 | 0.0011743 | 0.0002943
47 | 0.0045944 | 0.0011515
48 | 0.003989 | 0.00099974
49 | 0.0041128 | 0.0010308
50 | 0.0034414 | 0.00086251
51 | 0.004294 | 0.0010762
52 | 0.0014355 | 0.00035978
53 | 0.00365 | 0.00091479
54 | 0.0032833 | 0.00082288
55 | 0.0051294 | 0.0012855
56 | 0.0017731 | 0.00044439
57 | 0.0013573 | 0.00034017
58 | 0.0010825 | 0.0002713
59 | 0.0013592 | 0.00034064
60 | 0.0011648 | 0.00029193
61 | 0.0060386 | 0.0015134
62 | 0.0059789 | 0.0014985
63 | 0.005653 | 0.0014168
64 | 0.003744 | 0.00093834
65 | 0.0031547 | 0.00079065
66 | 0.012618 | 0.0031623
67 | 0.0021412 | 0.00053663
68 | 0.0033586 | 0.00084175
69 | 0.0012682 | 0.00031783
70 | 0.0011415 | 0.00028609
71 | 0.0012183 | 0.00030533
72 | 0.0015368 | 0.00038515
73 | 0.0013672 | 0.00034266
74 | 0.0015406 | 0.00038611
75 | 0.001168 | 0.00029273
76 | 0.002192 | 0.00054936
77 | 0.0033072 | 0.00082886
78 | 0.0037481 | 0.00093935
79 | 0.0015595 | 0.00039084
80 | 0.00079661 | 0.00019965
81 | 0.0016914 | 0.00042391
82 | 0.0030442 | 0.00076294
83 | 0.0023422 | 0.00058702
84 | 0.0044575 | 0.0011172
85 | 0.0010916 | 0.00027357
86 | 0.00061823 | 0.00015494

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1