## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1364-28_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1364-28_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1364-28_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1364-28_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1364-28_0_4_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_1364-28_0_4_node_36 | 0.4 | n |  | TRUE
6 | bus_LV_1364-28_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_1364-28_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1364-28_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1364-28_0_4_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_1364-28_0_4_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_1364-28_0_4_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_1364-28_0_4_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_1364-28_0_4_node_33 | 0.4 | n |  | TRUE
14 | bus_LV_1364-28_0_4_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1364-28_0_4_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_1364-28_0_4_node_41 | 0.4 | n |  | TRUE
17 | bus_LV_1364-28_0_4_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_1364-28_0_4_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1364-28_0_4_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1364-28_0_4_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1364-28_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1364-28_0_4_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1364-28_0_4_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_1364-28_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1364-28_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1364-28_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1364-28_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_1364-28_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1364-28_0_4_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1364-28_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1364-28_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1364-28_0_4_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1364-28_0_4_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1364-28_0_4_node_35 | 0.4 | n |  | TRUE
35 | bus_MV_133_0_node_69 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1364-28_0_4_load_0 | 0 | 0.040422 | 0.010131 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1364-28_0_4_load_36 | 5 | 0.0017016 | 0.00042646 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1364-28_0_4_load_13 | 6 | 0.00087697 | 0.00021979 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1364-28_0_4_load_32 | 9 | 0.036695 | 0.0091965 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1364-28_0_4_load_37 | 10 | 0.0022784 | 0.00057102 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1364-28_0_4_load_39 | 12 | 0.00041847 | 0.00010488 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1364-28_0_4_load_33 | 13 | 0.0036772 | 0.00092159 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1364-28_0_4_load_40 | 15 | 0.0041694 | 0.001045 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1364-28_0_4_load_41 | 16 | 0.0078574 | 0.0019692 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1364-28_0_4_load_27 | 17 | 0.011312 | 0.0028352 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1364-28_0_4_load_28 | 18 | 0.0051058 | 0.0012796 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1364-28_0_4_load_17 | 21 | 0.014729 | 0.0036915 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1364-28_0_4_load_26 | 22 | 0.0034445 | 0.00086328 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1364-28_0_4_load_38 | 23 | 0.00034805 | 8.723e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1364-28_0_4_load_14 | 24 | 0.028054 | 0.0070311 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1364-28_0_4_load_16 | 26 | 0.0076166 | 0.0019089 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1364-28_0_4_load_23 | 27 | 0.016129 | 0.0040423 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1364-28_0_4_load_25 | 28 | 0.0078056 | 0.0019563 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1364-28_0_4_load_24 | 29 | 0.0035459 | 0.00088869 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1364-28_0_4_load_29 | 30 | 0.013287 | 0.0033301 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1364-28_0_4_load_30 | 31 | 0.016192 | 0.0040581 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1364-28_0_4_load_34 | 33 | 0.0051004 | 0.0012783 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1364-28_0_4_load_35 | 34 | 0.0068934 | 0.0017276 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1364-28_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.047559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1364-28_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.080773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1364-28_0_4_line_2 | NAYY 4x150 SE | 2 | 6 | 0.041639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1364-28_0_4_line_3 | NAYY 4x150 SE | 2 | 3 | 0.035268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1364-28_0_4_line_4 | NAYY 4x150 SE | 3 | 4 | 0.036254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1364-28_0_4_line_5 | NAYY 4x150 SE | 3 | 5 | 0.0065369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1364-28_0_4_line_6 | NAYY 4x150 SE | 4 | 11 | 0.011919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1364-28_0_4_line_7 | NAYY 4x150 SE | 4 | 12 | 0.02341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1364-28_0_4_line_8 | NAYY 4x150 SE | 5 | 10 | 0.010769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1364-28_0_4_line_9 | NAYY 4x150 SE | 7 | 8 | 0.007183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1364-28_0_4_line_10 | NAYY 4x150 SE | 7 | 9 | 0.011349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1364-28_0_4_line_11 | NAYY 4x150 SE | 8 | 10 | 0.020874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1364-28_0_4_line_12 | NAYY 4x150 SE | 9 | 13 | 0.01089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1364-28_0_4_line_13 | NAYY 4x150 SE | 11 | 22 | 0.018603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1364-28_0_4_line_14 | NAYY 4x150 SE | 11 | 14 | 0.10494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1364-28_0_4_line_15 | NAYY 4x150 SE | 12 | 23 | 0.0014944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1364-28_0_4_line_16 | NAYY 4x150 SE | 13 | 33 | 0.00042828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1364-28_0_4_line_17 | NAYY 4x150 SE | 14 | 15 | 0.032437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1364-28_0_4_line_18 | NAYY 4x150 SE | 15 | 16 | 0.0016318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1364-28_0_4_line_19 | NAYY 4x150 SE | 17 | 18 | 0.0048617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1364-28_0_4_line_20 | NAYY 4x150 SE | 18 | 30 | 0.0034454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1364-28_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.00799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1364-28_0_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.0098906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1364-28_0_4_line_23 | NAYY 4x150 SE | 20 | 27 | 0.01205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1364-28_0_4_line_24 | NAYY 4x150 SE | 20 | 26 | 0.0076973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1364-28_0_4_line_25 | NAYY 4x150 SE | 22 | 28 | 0.020311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1364-28_0_4_line_26 | NAYY 4x150 SE | 24 | 25 | 0.010029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1364-28_0_4_line_27 | NAYY 4x150 SE | 25 | 26 | 0.0051134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1364-28_0_4_line_28 | NAYY 4x150 SE | 27 | 29 | 0.029838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1364-28_0_4_line_29 | NAYY 4x150 SE | 28 | 29 | 0.0059164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1364-28_0_4_line_30 | NAYY 4x150 SE | 30 | 31 | 0.015316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1364-28_0_4_line_31 | NAYY 4x150 SE | 31 | 32 | 0.016963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1364-28_0_4_line_32 | NAYY 4x150 SE | 32 | 33 | 0.015116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1364-28_0_4_line_33 | NAYY 4x150 SE | 32 | 34 | 0.002077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1364-28_0_4_trafo_4 | 0.25 MVA 20/0.4 kV | 35 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2688653.4473 | 1205386.129 | 2688606.052 | 1205382.1904
1 | 2688653.4473 | 1205386.129 | 2688651.3893 | 1205412.5157 | 2688649.9418 | 1205431.0953 | 2688650.7588 | 1205436.0106 | 2688652.219 | 1205444.7491 | 2688657.7401 | 1205465.8671
2 | 2688657.7401 | 1205465.8671 | 2688623.1213 | 1205442.7296
3 | 2688657.7401 | 1205465.8671 | 2688666.989 | 1205473.654 | 2688677.4925 | 1205484.5504 | 2688683.7298 | 1205479.473
4 | 2688655.1005 | 1205501.707 | 2688658.4401 | 1205499.1437 | 2688663.8172 | 1205495.1321 | 2688675.5083 | 1205485.9997 | 2688677.4925 | 1205484.5504 | 2688683.7298 | 1205479.473
5 | 2688683.7298 | 1205479.473 | 2688689.8746 | 1205481.703
6 | 2688644.9829 | 1205504.2584 | 2688649.3992 | 1205506.0363 | 2688655.1005 | 1205501.707
7 | 2688655.1005 | 1205501.707 | 2688658.7343 | 1205505.4522 | 2688673.9158 | 1205512.7936 | 2688675.1539 | 1205513.2746
8 | 2688689.8746 | 1205481.703 | 2688693.9522 | 1205483.1828 | 2688700.2561 | 1205484.4549
9 | 2688727.7957 | 1205489.9233 | 2688720.718 | 1205488.5839
10 | 2688727.7957 | 1205489.9233 | 2688727.3866 | 1205491.8518 | 2688726.0205 | 1205501.1291
11 | 2688720.718 | 1205488.5839 | 2688700.2561 | 1205484.4549
12 | 2688724.3326 | 1205511.8876 | 2688725.4066 | 1205505.2979 | 2688726.0205 | 1205501.1291
13 | 2688644.9829 | 1205504.2584 | 2688627.7229 | 1205497.3196
14 | 2688644.9829 | 1205504.2584 | 2688649.3992 | 1205506.0363 | 2688656.6093 | 1205510.7464 | 2688658.3609 | 1205516.7652 | 2688657.5099 | 1205535.6427 | 2688657.1134 | 1205544.4092 | 2688657.7689 | 1205556.6158 | 2688660.2126 | 1205567.7594 | 2688670.9716 | 1205590.6341 | 2688677.2644 | 1205596.6649
15 | 2688676.5469 | 1205513.8159 | 2688675.1539 | 1205513.2746
16 | 2688724.2637 | 1205512.3103 | 2688724.3326 | 1205511.8876
17 | 2688677.2644 | 1205596.6649 | 2688705.5554 | 1205580.7969
18 | 2688705.5554 | 1205580.7969 | 2688706.7115 | 1205581.9484
19 | 2688750.9419 | 1205547.8034 | 2688754.8365 | 1205550.7133
20 | 2688750.9419 | 1205547.8034 | 2688748.1818 | 1205545.7411
21 | 2688566.284 | 1205467.9893 | 2688558.937 | 1205464.8005
22 | 2688558.937 | 1205464.8005 | 2688554.9676 | 1205473.8595
23 | 2688566.284 | 1205467.9893 | 2688577.0748 | 1205473.3518
24 | 2688566.284 | 1205467.9893 | 2688568.9763 | 1205460.7782
25 | 2688627.7229 | 1205497.3196 | 2688615.0597 | 1205492.2287 | 2688609.093 | 1205489.2635
26 | 2688570.9493 | 1205456.0618 | 2688574.8369 | 1205446.8168
27 | 2688570.9493 | 1205456.0618 | 2688569.3182 | 1205459.8623 | 2688568.9763 | 1205460.7782
28 | 2688577.0748 | 1205473.3518 | 2688603.7948 | 1205486.6305
29 | 2688609.093 | 1205489.2635 | 2688603.7948 | 1205486.6305
30 | 2688748.1818 | 1205545.7411 | 2688736.5357 | 1205537.0396 | 2688735.8876 | 1205536.6084
31 | 2688721.764 | 1205527.2137 | 2688735.8876 | 1205536.6084
32 | 2688721.764 | 1205527.2137 | 2688722.5586 | 1205523.4007 | 2688723.8664 | 1205514.7478 | 2688724.2637 | 1205512.3103
33 | 2688721.764 | 1205527.2137 | 2688719.7598 | 1205526.6686

## bus_geodata
| x | y | coords
0 | 2688606.052 | 1205382.1904
1 | 2688653.4473 | 1205386.129
2 | 2688657.7401 | 1205465.8671
3 | 2688683.7298 | 1205479.473
4 | 2688655.1005 | 1205501.707
5 | 2688689.8746 | 1205481.703
6 | 2688623.1213 | 1205442.7296
7 | 2688727.7956 | 1205489.9233
8 | 2688720.718 | 1205488.5839
9 | 2688726.0205 | 1205501.1291
10 | 2688700.2561 | 1205484.4549
11 | 2688644.9829 | 1205504.2584
12 | 2688675.1539 | 1205513.2746
13 | 2688724.3326 | 1205511.8876
14 | 2688677.2644 | 1205596.6649
15 | 2688705.5554 | 1205580.7969
16 | 2688706.7115 | 1205581.9484
17 | 2688754.8365 | 1205550.7133
18 | 2688750.9419 | 1205547.8034
19 | 2688558.9371 | 1205464.8005
20 | 2688566.284 | 1205467.9893
21 | 2688554.9676 | 1205473.8595
22 | 2688627.7229 | 1205497.3196
23 | 2688676.5469 | 1205513.8159
24 | 2688574.8369 | 1205446.8168
25 | 2688570.9493 | 1205456.0618
26 | 2688568.9763 | 1205460.7782
27 | 2688577.0748 | 1205473.3518
28 | 2688609.093 | 1205489.2635
29 | 2688603.7948 | 1205486.6305
30 | 2688748.1818 | 1205545.7411
31 | 2688735.8876 | 1205536.6084
32 | 2688721.764 | 1205527.2137
33 | 2688724.2637 | 1205512.3103
34 | 2688719.7598 | 1205526.6686
35 | 2688666.989 | 1205473.654

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99255 | -0.052169 | 0.040422 | 0.010131
1 | 0.99531 | -0.032746 | 0 | 0
2 | 1 | 0 | -0.24202 | -0.060924
3 | 0.99498 | -0.034741 | 0 | 0
4 | 0.99002 | -0.069323 | 0 | 0
5 | 0.99401 | -0.041486 | 0.0017016 | 0.00042646
6 | 0.99995 | -0.00036531 | 0.00087697 | 0.00021979
7 | 0.98845 | -0.080492 | 0 | 0
8 | 0.98948 | -0.073289 | 0 | 0
9 | 0.98684 | -0.091903 | 0.036695 | 0.0091965
10 | 0.99245 | -0.052441 | 0.0022784 | 0.00057102
11 | 0.9884 | -0.080675 | 0 | 0
12 | 0.98999 | -0.069506 | 0.00041847 | 0.00010488
13 | 0.98587 | -0.098782 | 0.0036772 | 0.00092159
14 | 0.98658 | -0.093601 | 0 | 0
15 | 0.98601 | -0.097604 | 0.0041694 | 0.001045
16 | 0.986 | -0.097735 | 0.0078574 | 0.0019692
17 | 0.98273 | -0.12112 | 0.011312 | 0.0028352
18 | 0.98281 | -0.12055 | 0.0051058 | 0.0012796
19 | 0.97935 | -0.1448 | 0 | 0
20 | 0.97952 | -0.14358 | 0 | 0
21 | 0.97914 | -0.14632 | 0.014729 | 0.0036915
22 | 0.9862 | -0.096166 | 0.0034445 | 0.00086328
23 | 0.98999 | -0.069511 | 0.00034805 | 8.723e-05
24 | 0.97851 | -0.15086 | 0.028054 | 0.0070311
25 | 0.97892 | -0.14793 | 0 | 0
26 | 0.97912 | -0.14644 | 0.0076166 | 0.0019089
27 | 0.98041 | -0.13727 | 0.016129 | 0.0040423
28 | 0.9839 | -0.11244 | 0.0078056 | 0.0019563
29 | 0.9833 | -0.11672 | 0.0035459 | 0.00088869
30 | 0.98289 | -0.11996 | 0.013287 | 0.0033301
31 | 0.98355 | -0.11526 | 0.016192 | 0.0040581
32 | 0.98468 | -0.10724 | 0 | 0
33 | 0.98583 | -0.099036 | 0.0051004 | 0.0012783
34 | 0.98466 | -0.10739 | 0.0068934 | 0.0017276
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.040422 | -0.010131 | 0.040531 | 0.010172 | 0.00010898 | 4.1301e-05 | 0.0606 | 0.0606 | 0.0606 | 0.99255 | -0.052169 | 0.99531 | -0.032746 | 22.4446
1 | -0.040531 | -0.010172 | 0.040716 | 0.010242 | 0.0001851 | 7.0136e-05 | 0.0606 | 0.0606 | 0.0606 | 0.99531 | -0.032746 | 1 | 0 | 22.4445
2 | 0.00087702 | 0.00021926 | -0.00087697 | -0.00021979 | 4.4244e-08 | -5.2923e-07 | 0.0013048 | 0.001305 | 0.001305 | 1 | 0 | 0.99995 | -0.00036531 | 0.48334
3 | 0.19963 | 0.050462 | -0.19866 | -0.050089 | 0.00097192 | 0.0003729 | 0.2972 | 0.2972 | 0.2972 | 1 | 0 | 0.99498 | -0.034741 | 55.0373
4 | 0.095424 | 0.024086 | -0.094963 | -0.023909 | 0.00046112 | 0.00017688 | 0.14277 | 0.14277 | 0.14277 | 0.99498 | -0.034741 | 0.99002 | -0.069323 | 52.8779
5 | 0.10323 | 0.026003 | -0.10313 | -0.025966 | 9.7281e-05 | 3.7331e-05 | 0.15443 | 0.15443 | 0.15443 | 0.99498 | -0.034741 | 0.99401 | -0.041486 | 57.1968
6 | 0.094197 | 0.023718 | -0.094048 | -0.02366 | 0.00014917 | 5.722e-05 | 0.14162 | 0.14162 | 0.14162 | 0.99002 | -0.069323 | 0.9884 | -0.080675 | 52.4512
7 | 0.00076654 | 0.00019179 | -0.00076652 | -0.00019209 | 1.9388e-08 | -2.9356e-07 | 0.001152 | 0.0011521 | 0.0011521 | 0.99002 | -0.069323 | 0.98999 | -0.069506 | 0.42671
8 | 0.10143 | 0.025539 | -0.10128 | -0.02548 | 0.00015502 | 5.9482e-05 | 0.15188 | 0.15188 | 0.15188 | 0.99401 | -0.041486 | 0.99245 | -0.052441 | 56.2534
9 | -0.098613 | -0.024761 | 0.098712 | 0.024799 | 9.88e-05 | 3.7908e-05 | 0.14847 | 0.14847 | 0.14847 | 0.98845 | -0.080492 | 0.98948 | -0.073289 | 54.9882
10 | 0.098613 | 0.024761 | -0.098457 | -0.024701 | 0.0001561 | 5.9893e-05 | 0.14847 | 0.14847 | 0.14847 | 0.98845 | -0.080492 | 0.98684 | -0.091903 | 54.9882
11 | -0.098712 | -0.024799 | 0.098999 | 0.024909 | 0.00028712 | 0.00011016 | 0.14847 | 0.14847 | 0.14847 | 0.98948 | -0.073289 | 0.99245 | -0.052441 | 54.9882
12 | 0.061762 | 0.015504 | -0.061703 | -0.015482 | 5.895e-05 | 2.2534e-05 | 0.093138 | 0.093138 | 0.093138 | 0.98684 | -0.091903 | 0.98587 | -0.098782 | 34.4955
13 | 0.081992 | 0.020637 | -0.081816 | -0.020569 | 0.00017696 | 6.7823e-05 | 0.12347 | 0.12347 | 0.12347 | 0.9884 | -0.080675 | 0.9862 | -0.096166 | 45.7292
14 | 0.012055 | 0.0030233 | -0.012034 | -0.0030164 | 2.1571e-05 | 6.954e-06 | 0.01815 | 0.01815 | 0.01815 | 0.9884 | -0.080675 | 0.98658 | -0.093601 | 6.7222
15 | 0.00034805 | 8.721e-05 | -0.00034805 | -8.723e-05 | 2.5519e-10 | -1.9117e-08 | 0.00052313 | 0.00052314 | 0.00052314 | 0.98999 | -0.069506 | 0.98999 | -0.069511 | 0.19376
16 | 0.058026 | 0.01456 | -0.058024 | -0.014559 | 2.0502e-06 | 7.8308e-07 | 0.087588 | 0.087588 | 0.087588 | 0.98587 | -0.098782 | 0.98583 | -0.099036 | 32.4399
17 | 0.012034 | 0.0030164 | -0.012027 | -0.0030142 | 6.6678e-06 | 2.1506e-06 | 0.01815 | 0.01815 | 0.01815 | 0.98658 | -0.093601 | 0.98601 | -0.097604 | 6.7223
18 | 0.0078575 | 0.0019693 | -0.0078574 | -0.0019692 | 1.4318e-07 | 3.4255e-08 | 0.011858 | 0.011858 | 0.011858 | 0.98601 | -0.097604 | 0.986 | -0.097735 | 4.3918
19 | -0.011312 | -0.0028352 | 0.011313 | 0.0028355 | 8.901e-07 | 2.8074e-07 | 0.017129 | 0.017129 | 0.017129 | 0.98273 | -0.12112 | 0.98281 | -0.12055 | 6.3441
20 | -0.016419 | -0.0041151 | 0.01642 | 0.0041156 | 1.3287e-06 | 4.6736e-07 | 0.024859 | 0.024859 | 0.024859 | 0.98281 | -0.12055 | 0.98289 | -0.11996 | 9.2072
21 | -0.014732 | -0.0036925 | 0.014735 | 0.0036934 | 2.4981e-06 | 8.6024e-07 | 0.022384 | 0.022384 | 0.022384 | 0.97935 | -0.1448 | 0.97952 | -0.14358 | 8.2904
22 | 0.014732 | 0.0036925 | -0.014729 | -0.0036915 | 3.0923e-06 | 1.0649e-06 | 0.022384 | 0.022384 | 0.022384 | 0.97935 | -0.1448 | 0.97914 | -0.14632 | 8.2904
23 | -0.050437 | -0.012645 | 0.050481 | 0.012662 | 4.4143e-05 | 1.6826e-05 | 0.076622 | 0.076621 | 0.076622 | 0.97952 | -0.14358 | 0.98041 | -0.13727 | 28.3783
24 | 0.035702 | 0.0089518 | -0.035688 | -0.0089464 | 1.4129e-05 | 5.3375e-06 | 0.054238 | 0.054238 | 0.054238 | 0.97952 | -0.14358 | 0.97912 | -0.14644 | 20.088
25 | 0.078371 | 0.019706 | -0.078194 | -0.019638 | 0.00017729 | 6.7929e-05 | 0.11827 | 0.11827 | 0.11827 | 0.9862 | -0.096166 | 0.9839 | -0.11244 | 43.8044
26 | -0.028054 | -0.0070311 | 0.028066 | 0.0070354 | 1.139e-05 | 4.2549e-06 | 0.042662 | 0.042662 | 0.042662 | 0.97851 | -0.15086 | 0.97892 | -0.14793 | 15.8009
27 | -0.028066 | -0.0070354 | 0.028072 | 0.0070375 | 5.8074e-06 | 2.1693e-06 | 0.042662 | 0.042662 | 0.042662 | 0.97892 | -0.14793 | 0.97912 | -0.14644 | 15.8009
28 | -0.06661 | -0.016704 | 0.0668 | 0.016777 | 0.00019031 | 7.2818e-05 | 0.1011 | 0.1011 | 0.1011 | 0.98041 | -0.13727 | 0.9833 | -0.11672 | 37.4448
29 | 0.070388 | 0.017682 | -0.070346 | -0.017666 | 4.1848e-05 | 1.602e-05 | 0.10647 | 0.10647 | 0.10647 | 0.9839 | -0.11244 | 0.9833 | -0.11672 | 39.4322
30 | -0.029708 | -0.0074456 | 0.029727 | 0.0074529 | 1.9332e-05 | 7.2412e-06 | 0.044975 | 0.044975 | 0.044975 | 0.98289 | -0.11996 | 0.98355 | -0.11526 | 16.6575
31 | -0.045919 | -0.011511 | 0.04597 | 0.01153 | 5.1086e-05 | 1.9433e-05 | 0.069472 | 0.069472 | 0.069472 | 0.98355 | -0.11526 | 0.98468 | -0.10724 | 25.7304
32 | -0.052864 | -0.013258 | 0.052924 | 0.013281 | 6.0199e-05 | 2.2961e-05 | 0.079889 | 0.079889 | 0.079889 | 0.98468 | -0.10724 | 0.98583 | -0.099036 | 29.5886
33 | 0.0068935 | 0.0017277 | -0.0068934 | -0.0017276 | 1.4065e-07 | 2.7676e-08 | 0.010417 | 0.010417 | 0.010417 | 0.98468 | -0.10724 | 0.98466 | -0.10739 | 3.8583

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24202 | 0.060924

## res_load
| p_mw | q_mvar
0 | 0.040422 | 0.010131
1 | 0.0017016 | 0.00042646
2 | 0.00087697 | 0.00021979
3 | 0.036695 | 0.0091965
4 | 0.0022784 | 0.00057102
5 | 0.00041847 | 0.00010488
6 | 0.0036772 | 0.00092159
7 | 0.0041694 | 0.001045
8 | 0.0078574 | 0.0019692
9 | 0.011312 | 0.0028352
10 | 0.0051058 | 0.0012796
11 | 0.014729 | 0.0036915
12 | 0.0034445 | 0.00086328
13 | 0.00034805 | 8.723e-05
14 | 0.028054 | 0.0070311
15 | 0.0076166 | 0.0019089
16 | 0.016129 | 0.0040423
17 | 0.0078056 | 0.0019563
18 | 0.0035459 | 0.00088869
19 | 0.013287 | 0.0033301
20 | 0.016192 | 0.0040581
21 | 0.0051004 | 0.0012783
22 | 0.0068934 | 0.0017276

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1