## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1364-30_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1364-30_0_2_node_3 | 0.4 | n |  | TRUE
2 | bus_LV_1364-30_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1364-30_0_2_node_30 | 0.4 | n |  | TRUE
4 | bus_LV_1364-30_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1364-30_0_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1364-30_0_2_node_1 | 0.4 | n |  | TRUE
7 | bus_LV_1364-30_0_2_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_1364-30_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1364-30_0_2_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_1364-30_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1364-30_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1364-30_0_2_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_1364-30_0_2_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_1364-30_0_2_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_1364-30_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1364-30_0_2_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_1364-30_0_2_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1364-30_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1364-30_0_2_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1364-30_0_2_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1364-30_0_2_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1364-30_0_2_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1364-30_0_2_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1364-30_0_2_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1364-30_0_2_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1364-30_0_2_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1364-30_0_2_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1364-30_0_2_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1364-30_0_2_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1364-30_0_2_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1364-30_0_2_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1364-30_0_2_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1364-30_0_2_node_32 | 0.4 | n |  | TRUE
34 | bus_MV_133_0_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1364-30_0_2_load_0 | 0 | 0.070566 | 0.017685 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1364-30_0_2_load_3 | 1 | 0.011781 | 0.0029525 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1364-30_0_2_load_30 | 3 | 0.028228 | 0.0070746 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1364-30_0_2_load_6 | 4 | 0.00047859 | 0.00011995 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1364-30_0_2_load_4 | 5 | 0.001236 | 0.00030976 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1364-30_0_2_load_1 | 6 | 0.0014902 | 0.00037349 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1364-30_0_2_load_28 | 9 | 0.010952 | 0.0027449 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1364-30_0_2_load_35 | 13 | 0.00060435 | 0.00015146 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1364-30_0_2_load_10 | 15 | 0.0013792 | 0.00034566 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1364-30_0_2_load_31 | 16 | 0.006419 | 0.0016088 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1364-30_0_2_load_20 | 17 | 0.0071522 | 0.0017925 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1364-30_0_2_load_9 | 18 | 0.00096081 | 0.0002408 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1364-30_0_2_load_13 | 20 | 0.00098854 | 0.00024775 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1364-30_0_2_load_18 | 23 | 0.00089387 | 0.00022402 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1364-30_0_2_load_25 | 24 | 0.0016292 | 0.00040832 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1364-30_0_2_load_23 | 25 | 0.0045006 | 0.001128 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1364-30_0_2_load_19 | 26 | 0.0062399 | 0.0015639 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1364-30_0_2_load_16 | 27 | 0.00032245 | 8.0814e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1364-30_0_2_load_24 | 28 | 0.0032245 | 0.00080814 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1364-30_0_2_load_15 | 29 | 0.00082032 | 0.00020559 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1364-30_0_2_load_26 | 31 | 0.0014027 | 0.00035156 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1364-30_0_2_load_27 | 32 | 0.0055691 | 0.0013958 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1364-30_0_2_load_32 | 33 | 0.00050001 | 0.00012532 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1364-30_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.081308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1364-30_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.055997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1364-30_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.10013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1364-30_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0057698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1364-30_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0083916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1364-30_0_2_line_5 | NAYY 4x150 SE | 2 | 6 | 0.031196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1364-30_0_2_line_6 | NAYY 4x150 SE | 3 | 9 | 0.087856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1364-30_0_2_line_7 | NAYY 4x150 SE | 4 | 7 | 0.025973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1364-30_0_2_line_8 | NAYY 4x150 SE | 5 | 8 | 0.024457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1364-30_0_2_line_9 | NAYY 4x150 SE | 7 | 15 | 0.023082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1364-30_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.008685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1364-30_0_2_line_11 | NAYY 4x150 SE | 10 | 14 | 0.03349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1364-30_0_2_line_12 | NAYY 4x150 SE | 10 | 13 | 0.035405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1364-30_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.032587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1364-30_0_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.048351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1364-30_0_2_line_15 | NAYY 4x150 SE | 12 | 16 | 0.019222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1364-30_0_2_line_16 | NAYY 4x150 SE | 14 | 17 | 0.032884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1364-30_0_2_line_17 | NAYY 4x150 SE | 15 | 18 | 0.010338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1364-30_0_2_line_18 | NAYY 4x150 SE | 16 | 33 | 0.043805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1364-30_0_2_line_19 | NAYY 4x150 SE | 18 | 19 | 0.0075696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1364-30_0_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.024715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1364-30_0_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.004946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1364-30_0_2_line_22 | NAYY 4x150 SE | 21 | 25 | 0.010724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1364-30_0_2_line_23 | NAYY 4x150 SE | 21 | 26 | 0.040481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1364-30_0_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.01793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1364-30_0_2_line_25 | NAYY 4x150 SE | 22 | 24 | 0.091703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1364-30_0_2_line_26 | NAYY 4x150 SE | 23 | 27 | 0.0096634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1364-30_0_2_line_27 | NAYY 4x150 SE | 24 | 28 | 0.029102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1364-30_0_2_line_28 | NAYY 4x150 SE | 25 | 31 | 0.0018419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1364-30_0_2_line_29 | NAYY 4x150 SE | 26 | 30 | 0.013636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1364-30_0_2_line_30 | NAYY 4x150 SE | 27 | 29 | 0.010345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1364-30_0_2_line_31 | NAYY 4x150 SE | 29 | 30 | 0.043329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1364-30_0_2_line_32 | NAYY 4x150 SE | 31 | 32 | 0.017609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1364-30_0_2_trafo_0 | 0.25 MVA 20/0.4 kV | 34 | 0 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2689571.8561 | 1206086.0066 | 2689543.4916 | 1206009.8065
1 | 2689573.3109 | 1206141.9851 | 2689571.8561 | 1206086.0066
2 | 2689636.9311 | 1206045.7987 | 2689543.4916 | 1206009.8065
3 | 2689573.3109 | 1206141.9851 | 2689578.921 | 1206143.3332
4 | 2689573.3109 | 1206141.9851 | 2689569.5973 | 1206149.5102
5 | 2689573.3109 | 1206141.9851 | 2689578.1832 | 1206138.1668 | 2689583.3037 | 1206135.5419 | 2689591.7605 | 1206133.623 | 2689602.3386 | 1206133.4064
6 | 2689636.9311 | 1206045.7987 | 2689654.4086 | 1205959.6992
7 | 2689580.2255 | 1206159.7005 | 2689582.785 | 1206152.8677 | 2689586.1403 | 1206150.7833 | 2689587.9508 | 1206145.7072 | 2689579.8745 | 1206143.5624 | 2689578.921 | 1206143.3332
8 | 2689558.7741 | 1206171.442 | 2689569.5973 | 1206149.5102
9 | 2689580.2255 | 1206159.7005 | 2689584.7099 | 1206159.4231 | 2689591.8742 | 1206161.0094 | 2689602.4976 | 1206164.715
10 | 2689554.93 | 1206179.2339 | 2689558.7741 | 1206171.442
11 | 2689554.93 | 1206179.2339 | 2689550.2185 | 1206212.385
12 | 2689554.93 | 1206179.2339 | 2689542.815 | 1206176.5616 | 2689528.2995 | 1206175.71 | 2689520.234 | 1206173.1623
13 | 2689475.5622 | 1206131.7017 | 2689507.1159 | 1206140.1913
14 | 2689507.1159 | 1206140.1913 | 2689505.8703 | 1206144.6311 | 2689501.5797 | 1206159.3765 | 2689499.6629 | 1206164.9514 | 2689502.1735 | 1206167.4574 | 2689520.234 | 1206173.1623
15 | 2689475.5622 | 1206131.7017 | 2689469.9468 | 1206150.0852 | 2689469.9468 | 1206150.0852
16 | 2689550.2185 | 1206212.385 | 2689582.734 | 1206217.2944
17 | 2689602.4976 | 1206164.715 | 2689612.2592 | 1206168.12
18 | 2689469.9468 | 1206150.0852 | 2689465.5773 | 1206149.8085 | 2689463.655 | 1206150.6802 | 2689454.8162 | 1206147.1344 | 2689453.1356 | 1206151.6677 | 2689439.0385 | 1206146.7533 | 2689431.7842 | 1206143.3143
19 | 2689619.7849 | 1206168.9335 | 2689612.2592 | 1206168.12
20 | 2689619.7849 | 1206168.9335 | 2689620.2803 | 1206171.9095 | 2689628.521 | 1206180.828 | 2689634.8902 | 1206187.9507
21 | 2689638.5182 | 1206191.3072 | 2689635.3435 | 1206188.4576 | 2689634.8902 | 1206187.9507
22 | 2689638.5182 | 1206191.3072 | 2689638.924 | 1206193.1589 | 2689638.9151 | 1206195.2713 | 2689638.3091 | 1206199.1536 | 2689637.1139 | 1206201.6707
23 | 2689638.5182 | 1206191.3072 | 2689650.6349 | 1206198.416 | 2689661.5025 | 1206204.1162 | 2689666.473 | 1206207.4264 | 2689668.8259 | 1206210.2969 | 2689671.2885 | 1206214.0367
24 | 2689661.7321 | 1206147.3267 | 2689668.8383 | 1206158.8521 | 2689670.2286 | 1206163.0163
25 | 2689661.7321 | 1206147.3267 | 2689671.7553 | 1206143.4191 | 2689748.5879 | 1206117.9453
26 | 2689670.2286 | 1206163.0163 | 2689673.2888 | 1206172.1823
27 | 2689748.5879 | 1206117.9453 | 2689776.2113 | 1206108.7867
28 | 2689637.1139 | 1206201.6707 | 2689636.3238 | 1206203.3345
29 | 2689679.0447 | 1206225.2491 | 2689674.0464 | 1206218.225 | 2689671.2885 | 1206214.0367
30 | 2689673.2888 | 1206172.1823 | 2689675.0762 | 1206177.5359 | 2689675.8757 | 1206182.1681
31 | 2689679.0447 | 1206225.2491 | 2689679.3082 | 1206217.3368 | 2689678.5468 | 1206197.6457 | 2689675.8757 | 1206182.1681
32 | 2689622.0631 | 1206210.7174 | 2689629.36 | 1206210.5601 | 2689633.7617 | 1206207.6799 | 2689635.8662 | 1206204.2981 | 2689636.3238 | 1206203.3345

## bus_geodata
| x | y | coords
0 | 2689571.8561 | 1206086.0066
1 | 2689543.4916 | 1206009.8065
2 | 2689573.3109 | 1206141.9851
3 | 2689636.9311 | 1206045.7987
4 | 2689578.921 | 1206143.3332
5 | 2689569.5973 | 1206149.5102
6 | 2689602.3386 | 1206133.4064
7 | 2689580.2255 | 1206159.7005
8 | 2689558.7741 | 1206171.442
9 | 2689654.4086 | 1205959.6992
10 | 2689554.93 | 1206179.2339
11 | 2689507.1159 | 1206140.1913
12 | 2689475.5622 | 1206131.7017
13 | 2689520.234 | 1206173.1623
14 | 2689550.2185 | 1206212.385
15 | 2689602.4976 | 1206164.715
16 | 2689469.9468 | 1206150.0852
17 | 2689582.734 | 1206217.2944
18 | 2689612.2592 | 1206168.12
19 | 2689619.785 | 1206168.9335
20 | 2689634.8902 | 1206187.9507
21 | 2689638.5182 | 1206191.3072
22 | 2689661.7321 | 1206147.3267
23 | 2689670.2286 | 1206163.0163
24 | 2689748.5879 | 1206117.9453
25 | 2689637.1139 | 1206201.6707
26 | 2689671.2885 | 1206214.0367
27 | 2689673.2888 | 1206172.1823
28 | 2689776.2113 | 1206108.7867
29 | 2689675.8757 | 1206182.1681
30 | 2689679.0447 | 1206225.2491
31 | 2689636.3238 | 1206203.3345
32 | 2689622.0631 | 1206210.7174
33 | 2689431.7842 | 1206143.3143
34 | 2689571.8561 | 1206086.0066

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.098421 | -0.024567
1 | 0.99403 | -0.04162 | 0.011781 | 0.0029525
2 | 0.99632 | -0.025737 | 0 | 0
3 | 0.98837 | -0.081487 | 0.028228 | 0.0070746
4 | 0.99608 | -0.027388 | 0.00047859 | 0.00011995
5 | 0.99613 | -0.027082 | 0.001236 | 0.00030976
6 | 0.99625 | -0.026205 | 0.0014902 | 0.00037349
7 | 0.99504 | -0.034702 | 0 | 0
8 | 0.99561 | -0.030701 | 0 | 0
9 | 0.98698 | -0.091336 | 0.010952 | 0.0027449
10 | 0.99543 | -0.031986 | 0 | 0
11 | 0.99457 | -0.038055 | 0 | 0
12 | 0.99424 | -0.040333 | 0 | 0
13 | 0.99505 | -0.034676 | 0.00060435 | 0.00015146
14 | 0.99509 | -0.034401 | 0 | 0
15 | 0.99411 | -0.041215 | 0.0013792 | 0.00034566
16 | 0.99405 | -0.041677 | 0.006419 | 0.0016088
17 | 0.99475 | -0.036773 | 0.0071522 | 0.0017925
18 | 0.99372 | -0.043991 | 0.00096081 | 0.0002408
19 | 0.99344 | -0.045952 | 0 | 0
20 | 0.99253 | -0.052361 | 0.00098854 | 0.00024775
21 | 0.99236 | -0.053596 | 0 | 0
22 | 0.99073 | -0.065085 | 0 | 0
23 | 0.99086 | -0.064198 | 0.00089387 | 0.00022402
24 | 0.99009 | -0.069621 | 0.0016292 | 0.00040832
25 | 0.99218 | -0.054843 | 0.0045006 | 0.001128
26 | 0.99159 | -0.058996 | 0.0062399 | 0.0015639
27 | 0.99094 | -0.063632 | 0.00032245 | 8.0814e-05
28 | 0.98995 | -0.070577 | 0.0032245 | 0.00080814
29 | 0.99103 | -0.062993 | 0.00082032 | 0.00020559
30 | 0.99146 | -0.059953 | 0 | 0
31 | 0.99216 | -0.054973 | 0.0014027 | 0.00035156
32 | 0.99202 | -0.055968 | 0.0055691 | 0.0013958
33 | 0.99402 | -0.0419 | 0.00050001 | 0.00012532
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.051492 | 0.012973 | -0.051194 | -0.012859 | 0.00029804 | 0.00011357 | 0.076644 | 0.076645 | 0.076645 | 1 | 0 | 0.99403 | -0.04162 | 28.387
1 | 0.04613 | 0.011594 | -0.045965 | -0.011531 | 0.00016469 | 6.2612e-05 | 0.068653 | 0.068653 | 0.068653 | 1 | 0 | 0.99632 | -0.025737 | 25.4272
2 | 0.039413 | 0.0099066 | -0.039195 | -0.0098242 | 0.00021757 | 8.2391e-05 | 0.05901 | 0.05901 | 0.05901 | 0.99403 | -0.04162 | 0.98837 | -0.081487 | 21.8556
3 | 0.028536 | 0.0071636 | -0.028529 | -0.0071612 | 6.5408e-06 | 2.4406e-06 | 0.042623 | 0.042623 | 0.042623 | 0.99632 | -0.025737 | 0.99608 | -0.027388 | 15.7863
4 | 0.015939 | 0.0039945 | -0.015936 | -0.0039935 | 2.9673e-06 | 1.032e-06 | 0.023805 | 0.023805 | 0.023805 | 0.99632 | -0.025737 | 0.99613 | -0.027082 | 8.8166
5 | 0.0014903 | 0.00037312 | -0.0014902 | -0.00037349 | 9.6439e-08 | -3.6915e-07 | 0.0022257 | 0.0022259 | 0.0022259 | 0.99632 | -0.025737 | 0.99625 | -0.026205 | 0.82439
6 | 0.010967 | 0.0027496 | -0.010952 | -0.0027449 | 1.4947e-05 | 4.6246e-06 | 0.016512 | 0.016512 | 0.016512 | 0.98837 | -0.081487 | 0.98698 | -0.091336 | 6.1157
7 | 0.028051 | 0.0070412 | -0.028022 | -0.0070306 | 2.8464e-05 | 1.061e-05 | 0.041908 | 0.041908 | 0.041908 | 0.99608 | -0.027388 | 0.99504 | -0.034702 | 15.5215
8 | 0.0147 | 0.0036838 | -0.014692 | -0.0036812 | 7.3586e-06 | 2.512e-06 | 0.021959 | 0.021959 | 0.021959 | 0.99613 | -0.027082 | 0.99561 | -0.030701 | 8.1328
9 | 0.028022 | 0.0070306 | -0.027997 | -0.0070212 | 2.5296e-05 | 9.4297e-06 | 0.041908 | 0.041908 | 0.041908 | 0.99504 | -0.034702 | 0.99411 | -0.041215 | 15.5216
10 | 0.014692 | 0.0036812 | -0.01469 | -0.0036803 | 2.6132e-06 | 8.9214e-07 | 0.021959 | 0.021959 | 0.021959 | 0.99561 | -0.030701 | 0.99543 | -0.031986 | 8.1328
11 | 0.0071569 | 0.0017935 | -0.0071545 | -0.001793 | 2.3919e-06 | 4.8476e-07 | 0.010698 | 0.010699 | 0.010699 | 0.99543 | -0.031986 | 0.99509 | -0.034401 | 3.9624
12 | 0.0075329 | 0.0018869 | -0.0075301 | -0.0018863 | 2.8012e-06 | 6.1732e-07 | 0.01126 | 0.01126 | 0.01126 | 0.99543 | -0.031986 | 0.99505 | -0.034676 | 4.1705
13 | 0.0069225 | 0.0017342 | -0.0069204 | -0.0017338 | 2.1812e-06 | 4.1617e-07 | 0.010357 | 0.010357 | 0.010357 | 0.99457 | -0.038055 | 0.99424 | -0.040333 | 3.8359
14 | -0.0069225 | -0.0017342 | 0.0069258 | 0.0017348 | 3.2362e-06 | 6.1693e-07 | 0.010357 | 0.010357 | 0.010357 | 0.99457 | -0.038055 | 0.99505 | -0.034676 | 3.8359
15 | 0.0069204 | 0.0017338 | -0.0069191 | -0.0017335 | 1.2866e-06 | 2.4562e-07 | 0.010357 | 0.010357 | 0.010357 | 0.99424 | -0.040333 | 0.99405 | -0.041677 | 3.836
16 | 0.0071545 | 0.001793 | -0.0071522 | -0.0017925 | 2.3487e-06 | 4.7631e-07 | 0.010699 | 0.010699 | 0.010699 | 0.99509 | -0.034401 | 0.99475 | -0.036773 | 3.9625
17 | 0.026618 | 0.0066755 | -0.026608 | -0.0066717 | 1.0241e-05 | 3.805e-06 | 0.039844 | 0.039844 | 0.039844 | 0.99411 | -0.041215 | 0.99372 | -0.043991 | 14.757
18 | 0.00050003 | 0.00012475 | -0.00050001 | -0.00012532 | 1.531e-08 | -5.6197e-07 | 0.0007483 | 0.0007485 | 0.0007485 | 0.99405 | -0.041677 | 0.99402 | -0.0419 | 0.27722
19 | 0.025647 | 0.0064309 | -0.02564 | -0.0064284 | 6.9669e-06 | 2.5815e-06 | 0.038405 | 0.038405 | 0.038405 | 0.99372 | -0.043991 | 0.99344 | -0.045952 | 14.2242
20 | 0.02564 | 0.0064284 | -0.025617 | -0.0064199 | 2.2747e-05 | 8.4292e-06 | 0.038405 | 0.038405 | 0.038405 | 0.99344 | -0.045952 | 0.99253 | -0.052361 | 14.2242
21 | 0.024628 | 0.0061722 | -0.024624 | -0.0061706 | 4.2076e-06 | 1.5544e-06 | 0.036923 | 0.036923 | 0.036923 | 0.99253 | -0.052361 | 0.99236 | -0.053596 | 13.6753
22 | 0.011475 | 0.002876 | -0.011473 | -0.0028754 | 1.9813e-06 | 6.2352e-07 | 0.017207 | 0.017207 | 0.017207 | 0.99236 | -0.053596 | 0.99218 | -0.054843 | 6.373
23 | 0.013149 | 0.0032946 | -0.013139 | -0.0032914 | 9.8195e-06 | 3.2541e-06 | 0.019716 | 0.019716 | 0.019716 | 0.99236 | -0.053596 | 0.99159 | -0.058996 | 7.3024
24 | -0.0048572 | -0.0012162 | 0.0048578 | 0.0012162 | 5.9538e-07 | -1.9276e-09 | 0.0072948 | 0.0072947 | 0.0072948 | 0.99073 | -0.065085 | 0.99086 | -0.064198 | 2.7018
25 | 0.0048572 | 0.0012162 | -0.0048541 | -0.0012162 | 3.0453e-06 | -8.8655e-09 | 0.0072948 | 0.0072952 | 0.0072952 | 0.99073 | -0.065085 | 0.99009 | -0.069621 | 2.7019
26 | -0.0057517 | -0.0014403 | 0.0057521 | 0.0014403 | 4.4983e-07 | 4.8532e-08 | 0.0086371 | 0.0086371 | 0.0086371 | 0.99086 | -0.064198 | 0.99094 | -0.063632 | 3.1989
27 | 0.0032249 | 0.00080793 | -0.0032245 | -0.00080814 | 4.2659e-07 | -2.1015e-07 | 0.0048467 | 0.0048468 | 0.0048468 | 0.99009 | -0.069621 | 0.98995 | -0.070577 | 1.7951
28 | 0.0069728 | 0.0017474 | -0.0069726 | -0.0017474 | 1.2569e-07 | 2.4554e-08 | 0.010457 | 0.010457 | 0.010457 | 0.99218 | -0.054843 | 0.99216 | -0.054973 | 3.8731
29 | 0.0068992 | 0.0017275 | -0.0068983 | -0.0017273 | 9.1195e-07 | 1.7488e-07 | 0.010353 | 0.010353 | 0.010353 | 0.99159 | -0.058996 | 0.99146 | -0.059953 | 3.8343
30 | -0.0060746 | -0.0015211 | 0.0060751 | 0.0015212 | 5.3705e-07 | 7.3278e-08 | 0.0091213 | 0.0091212 | 0.0091213 | 0.99094 | -0.063632 | 0.99103 | -0.062993 | 3.3782
31 | -0.0068954 | -0.0017268 | 0.0068983 | 0.0017273 | 2.8979e-06 | 5.5604e-07 | 0.010353 | 0.010353 | 0.010353 | 0.99103 | -0.062993 | 0.99146 | -0.059953 | 3.8344
32 | 0.0055699 | 0.0013958 | -0.0055691 | -0.0013958 | 7.6676e-07 | 6.7532e-08 | 0.0083535 | 0.0083536 | 0.0083536 | 0.99216 | -0.054973 | 0.99202 | -0.055968 | 3.0939

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16899 | 0.042252

## res_load
| p_mw | q_mvar
0 | 0.070566 | 0.017685
1 | 0.011781 | 0.0029525
2 | 0.028228 | 0.0070746
3 | 0.00047859 | 0.00011995
4 | 0.001236 | 0.00030976
5 | 0.0014902 | 0.00037349
6 | 0.010952 | 0.0027449
7 | 0.00060435 | 0.00015146
8 | 0.0013792 | 0.00034566
9 | 0.006419 | 0.0016088
10 | 0.0071522 | 0.0017925
11 | 0.00096081 | 0.0002408
12 | 0.00098854 | 0.00024775
13 | 0.00089387 | 0.00022402
14 | 0.0016292 | 0.00040832
15 | 0.0045006 | 0.001128
16 | 0.0062399 | 0.0015639
17 | 0.00032245 | 8.0814e-05
18 | 0.0032245 | 0.00080814
19 | 0.00082032 | 0.00020559
20 | 0.0014027 | 0.00035156
21 | 0.0055691 | 0.0013958
22 | 0.00050001 | 0.00012532

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1