## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1364-33_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1364-33_0_2_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1364-33_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1364-33_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1364-33_0_2_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1364-33_0_2_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1364-33_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1364-33_0_2_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1364-33_0_2_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1364-33_0_2_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1364-33_0_2_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1364-33_0_2_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_1364-33_0_2_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_1364-33_0_2_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_1364-33_0_2_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1364-33_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1364-33_0_2_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1364-33_0_2_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1364-33_0_2_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1364-33_0_2_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1364-33_0_2_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1364-33_0_2_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1364-33_0_2_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1364-33_0_2_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1364-33_0_2_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1364-33_0_2_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1364-33_0_2_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1364-33_0_2_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1364-33_0_2_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1364-33_0_2_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1364-33_0_2_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_1364-33_0_2_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_1364-33_0_2_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1364-33_0_2_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1364-33_0_2_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_1364-33_0_2_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_1364-33_0_2_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1364-33_0_2_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1364-33_0_2_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_1364-33_0_2_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1364-33_0_2_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_1364-33_0_2_node_41 | 0.4 | n |  | TRUE
42 | bus_MV_0_node_20 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1364-33_0_2_load_0 | 0 | 0.00069646 | 0.00017455 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1364-33_0_2_load_3 | 2 | 0.00076384 | 0.00019144 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1364-33_0_2_load_4 | 3 | 0.00068058 | 0.00017057 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1364-33_0_2_load_5 | 4 | 0.0015273 | 0.00038279 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1364-33_0_2_load_6 | 6 | 0.001278 | 0.00032029 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1364-33_0_2_load_8 | 7 | 0.0015766 | 0.00039514 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1364-33_0_2_load_10 | 9 | 0.00034238 | 8.5808e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1364-33_0_2_load_34 | 11 | 0.00040769 | 0.00010218 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1364-33_0_2_load_44 | 12 | 0.0005478 | 0.00013729 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1364-33_0_2_load_31 | 13 | 0.0025356 | 0.00063549 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1364-33_0_2_load_11 | 14 | 0.00068661 | 0.00017208 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1364-33_0_2_load_13 | 16 | 0.00090347 | 0.00022643 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1364-33_0_2_load_14 | 17 | 0.00089112 | 0.00022334 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1364-33_0_2_load_25 | 18 | 0.0010978 | 0.00027514 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1364-33_0_2_load_26 | 19 | 0.0033946 | 0.00085077 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1364-33_0_2_load_27 | 21 | 0.0017832 | 0.00044691 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1364-33_0_2_load_15 | 22 | 0.0021704 | 0.00054396 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1364-33_0_2_load_16 | 23 | 0.00196 | 0.00049123 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1364-33_0_2_load_17 | 24 | 0.0039037 | 0.00097836 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1364-33_0_2_load_18 | 25 | 0.0026355 | 0.00066052 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1364-33_0_2_load_20 | 27 | 0.0023961 | 0.00060052 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1364-33_0_2_load_24 | 29 | 0.00088759 | 0.00022245 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1364-33_0_2_load_32 | 30 | 0.0043406 | 0.0010879 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1364-33_0_2_load_29 | 32 | 0.00054205 | 0.00013585 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1364-33_0_2_load_23 | 33 | 0.0024833 | 0.00062237 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1364-33_0_2_load_39 | 34 | 0.00082502 | 0.00020677 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1364-33_0_2_load_36 | 35 | 0.0015268 | 0.00038265 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1364-33_0_2_load_28 | 36 | 0.00023563 | 5.9055e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1364-33_0_2_load_30 | 37 | 0.00082631 | 0.00020709 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1364-33_0_2_load_40 | 38 | 0.00039068 | 9.7914e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1364-33_0_2_load_38 | 40 | 0.0012397 | 0.0003107 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1364-33_0_2_load_41 | 41 | 0.00066767 | 0.00016733 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1364-33_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.065616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1364-33_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.070955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1364-33_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.067785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1364-33_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0092096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1364-33_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.015433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1364-33_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.012751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1364-33_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.078328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1364-33_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.1065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1364-33_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.021822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1364-33_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.041607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1364-33_0_2_line_10 | NAYY 4x150 SE | 8 | 11 | 0.025348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1364-33_0_2_line_11 | NAYY 4x150 SE | 10 | 12 | 0.022603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1364-33_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.09731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1364-33_0_2_line_13 | NAYY 4x150 SE | 13 | 37 | 0.067545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1364-33_0_2_line_14 | NAYY 4x150 SE | 14 | 15 | 0.062753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1364-33_0_2_line_15 | NAYY 4x150 SE | 14 | 16 | 0.080553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1364-33_0_2_line_16 | NAYY 4x150 SE | 15 | 17 | 0.022529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1364-33_0_2_line_17 | NAYY 4x150 SE | 17 | 21 | 0.036694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1364-33_0_2_line_18 | NAYY 4x150 SE | 18 | 19 | 0.2077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1364-33_0_2_line_19 | NAYY 4x150 SE | 18 | 20 | 0.092183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1364-33_0_2_line_20 | NAYY 4x150 SE | 19 | 21 | 0.0074271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1364-33_0_2_line_21 | NAYY 4x150 SE | 20 | 29 | 0.02943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1364-33_0_2_line_22 | NAYY 4x150 SE | 20 | 26 | 0.01598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1364-33_0_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.018142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1364-33_0_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.0066524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1364-33_0_2_line_25 | NAYY 4x150 SE | 24 | 27 | 0.021776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1364-33_0_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.049167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1364-33_0_2_line_27 | NAYY 4x150 SE | 25 | 27 | 0.013589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1364-33_0_2_line_28 | NAYY 4x150 SE | 26 | 28 | 0.17264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1364-33_0_2_line_29 | NAYY 4x150 SE | 28 | 30 | 0.057907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1364-33_0_2_line_30 | NAYY 4x150 SE | 28 | 31 | 0.21508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1364-33_0_2_line_31 | NAYY 4x150 SE | 28 | 32 | 0.031637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1364-33_0_2_line_32 | NAYY 4x150 SE | 29 | 33 | 0.012704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1364-33_0_2_line_33 | NAYY 4x150 SE | 31 | 34 | 0.027677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1364-33_0_2_line_34 | NAYY 4x150 SE | 31 | 35 | 0.096327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1364-33_0_2_line_35 | NAYY 4x150 SE | 32 | 36 | 0.040485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1364-33_0_2_line_36 | NAYY 4x150 SE | 34 | 38 | 0.013492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1364-33_0_2_line_37 | NAYY 4x150 SE | 35 | 39 | 0.13684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1364-33_0_2_line_38 | NAYY 4x150 SE | 36 | 37 | 0.022024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1364-33_0_2_line_39 | NAYY 4x150 SE | 38 | 41 | 0.047847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1364-33_0_2_line_40 | NAYY 4x150 SE | 39 | 40 | 0.04093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1364-33_0_2_trafo_20 | 0.25 MVA 20/0.4 kV | 42 | 27 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2690559.2643 | 1207017.5354 | 2690618.8159 | 1207045.0874
1 | 2690559.2643 | 1207017.5354 | 2690527.9754 | 1207070.1846 | 2690522.6763 | 1207078.3213
2 | 2690559.2643 | 1207017.5354 | 2690523.2484 | 1207000.2778 | 2690499.0936 | 1206986.419
3 | 2690522.6763 | 1207078.3213 | 2690517.6502 | 1207086.0385 | 2690517.6502 | 1207086.0385
4 | 2690485.7077 | 1206978.7389 | 2690499.0936 | 1206986.419
5 | 2690517.6502 | 1207086.0385 | 2690510.3121 | 1207089.4851 | 2690507.348 | 1207093.06
6 | 2690485.7077 | 1206978.7389 | 2690480.7716 | 1206985.2684 | 2690448.0689 | 1207015.8264 | 2690428.2332 | 1207031.6677
7 | 2690485.7077 | 1206978.7389 | 2690471.6987 | 1206970.699 | 2690396.7257 | 1206919.8965
8 | 2690409.7734 | 1207043.2918 | 2690427.3289 | 1207032.3899 | 2690428.2332 | 1207031.6677
9 | 2690362.0684 | 1206896.7232 | 2690386.6672 | 1206913.1286 | 2690396.7257 | 1206919.8965
10 | 2690396.7257 | 1206919.8965 | 2690402.6761 | 1206911.67 | 2690410.8004 | 1206898.8287
11 | 2690362.0684 | 1206896.7232 | 2690348.648 | 1206914.9108
12 | 2690467.5457 | 1206820.3628 | 2690460.2361 | 1206829.8099 | 2690453.9841 | 1206834.8408 | 2690444.2788 | 1206845.9122 | 2690410.8004 | 1206898.8287
13 | 2690518.0739 | 1206776.1577 | 2690484.505 | 1206800.7696 | 2690469.972 | 1206817.2269 | 2690467.5457 | 1206820.3628
14 | 2690878.3228 | 1206454.4772 | 2690880.2337 | 1206459.3539 | 2690883.9689 | 1206463.8137 | 2690893.2972 | 1206471.0939 | 2690907.9053 | 1206481.79 | 2690922.2092 | 1206492.4815 | 2690925.3895 | 1206494.7412
15 | 2690916.3104 | 1206526.6921 | 2690920.4153 | 1206529.8456 | 2690928.2453 | 1206534.1121 | 2690934.1921 | 1206535.6815 | 2690939.876 | 1206533.5444 | 2690945.2892 | 1206528.2011 | 2690949.1654 | 1206518.9096 | 2690949.2544 | 1206513.0737 | 2690946.3436 | 1206507.926 | 2690937.2734 | 1206503.1847 | 2690925.3895 | 1206494.7412
16 | 2690878.3228 | 1206454.4772 | 2690878.7765 | 1206460.6437 | 2690873.4649 | 1206476.1027
17 | 2690873.4649 | 1206476.1027 | 2690869.9104 | 1206486.4481 | 2690863.3294 | 1206505.5383 | 2690861.2093 | 1206510.6802
18 | 2690845.7404 | 1206724.8604 | 2690858.3781 | 1206517.5466
19 | 2690756.6911 | 1206747.6545 | 2690788.2269 | 1206742.9975 | 2690845.7404 | 1206724.8604
20 | 2690861.2093 | 1206510.6802 | 2690858.3781 | 1206517.5466
21 | 2690756.6911 | 1206747.6545 | 2690784.8716 | 1206756.1394
22 | 2690756.6911 | 1206747.6545 | 2690740.6747 | 1206747.0662
23 | 2690731.8916 | 1206816.0625 | 2690736.5321 | 1206817.9168 | 2690749.6764 | 1206817.8691
24 | 2690725.7142 | 1206813.594 | 2690731.8916 | 1206816.0625
25 | 2690709.3136 | 1206799.2687 | 2690725.7142 | 1206813.594
26 | 2690740.6747 | 1206747.0662 | 2690734.8567 | 1206765.5456 | 2690727.2829 | 1206782.4528 | 2690719.9706 | 1206791.0248
27 | 2690709.3136 | 1206799.2687 | 2690717.4329 | 1206793.9997 | 2690719.9706 | 1206791.0248
28 | 2690740.6747 | 1206747.0662 | 2690695.1116 | 1206733.8652 | 2690610.9782 | 1206706.7143 | 2690574.0086 | 1206702.0614
29 | 2690574.0086 | 1206702.0614 | 2690581.1383 | 1206692.8412 | 2690598.2675 | 1206670.742 | 2690608.7487 | 1206655.6911
30 | 2690506.7205 | 1206599.2397 | 2690465.3278 | 1206690.6284 | 2690465.6981 | 1206696.8047 | 2690530.3077 | 1206697.9181 | 2690556.6859 | 1206699.3413 | 2690574.0086 | 1206702.0614
31 | 2690574.0086 | 1206702.0614 | 2690569.7317 | 1206705.7323 | 2690562.9625 | 1206712.245 | 2690554.6605 | 1206726.6279
32 | 2690797.0366 | 1206759.8021 | 2690784.8716 | 1206756.1394
33 | 2690506.7205 | 1206599.2397 | 2690479.062 | 1206598.22
34 | 2690506.7205 | 1206599.2397 | 2690538.1123 | 1206533.9391 | 2690548.6608 | 1206523.4811 | 2690552.9838 | 1206515.5653
35 | 2690534.3778 | 1206761.6641 | 2690534.9441 | 1206760.7855 | 2690554.6605 | 1206726.6279
36 | 2690479.062 | 1206598.22 | 2690465.5795 | 1206597.723
37 | 2690609.2458 | 1206391.5462 | 2690557.5932 | 1206495.2201 | 2690556.1305 | 1206506.9056 | 2690553.8399 | 1206513.9978 | 2690552.9838 | 1206515.5653
38 | 2690534.3778 | 1206761.6641 | 2690532.1478 | 1206765.1238 | 2690528.4681 | 1206768.5369 | 2690518.0739 | 1206776.1577
39 | 2690420.2021 | 1206582.931 | 2690462.6612 | 1206597.6154 | 2690465.5795 | 1206597.723
40 | 2690609.2458 | 1206391.5462 | 2690569.4503 | 1206381.9769

## bus_geodata
| x | y | coords
0 | 2690618.8159 | 1207045.0874
1 | 2690559.2643 | 1207017.5354
2 | 2690522.6763 | 1207078.3213
3 | 2690499.0936 | 1206986.419
4 | 2690517.6503 | 1207086.0385
5 | 2690485.7077 | 1206978.7389
6 | 2690507.348 | 1207093.06
7 | 2690428.2332 | 1207031.6677
8 | 2690396.7257 | 1206919.8965
9 | 2690409.7734 | 1207043.2918
10 | 2690362.0684 | 1206896.7232
11 | 2690410.8004 | 1206898.8287
12 | 2690348.648 | 1206914.9108
13 | 2690467.5457 | 1206820.3628
14 | 2690925.3895 | 1206494.7412
15 | 2690878.3228 | 1206454.4772
16 | 2690916.3104 | 1206526.6921
17 | 2690873.4649 | 1206476.1027
18 | 2690845.7404 | 1206724.8604
19 | 2690858.3781 | 1206517.5466
20 | 2690756.6911 | 1206747.6545
21 | 2690861.2093 | 1206510.6802
22 | 2690749.6764 | 1206817.8691
23 | 2690731.8916 | 1206816.0625
24 | 2690725.7142 | 1206813.594
25 | 2690719.9706 | 1206791.0248
26 | 2690740.6747 | 1206747.0662
27 | 2690709.3136 | 1206799.2687
28 | 2690574.0086 | 1206702.0614
29 | 2690784.8716 | 1206756.1394
30 | 2690608.7487 | 1206655.6911
31 | 2690506.7205 | 1206599.2397
32 | 2690554.6605 | 1206726.6279
33 | 2690797.0366 | 1206759.8021
34 | 2690479.062 | 1206598.22
35 | 2690552.9838 | 1206515.5653
36 | 2690534.3778 | 1206761.6641
37 | 2690518.0739 | 1206776.1577
38 | 2690465.5795 | 1206597.723
39 | 2690609.2458 | 1206391.5462
40 | 2690569.4503 | 1206381.9769
41 | 2690420.2021 | 1206582.931
42 | 2690709.3136 | 1206799.2687

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98615 | -0.097846 | 0.00069646 | 0.00017455
1 | 0.98622 | -0.097375 | 0 | 0
2 | 0.98585 | -0.099979 | 0.00076384 | 0.00019144
3 | 0.98664 | -0.094397 | 0.00068058 | 0.00017057
4 | 0.98581 | -0.10024 | 0.0015273 | 0.00038279
5 | 0.98675 | -0.093611 | 0 | 0
6 | 0.98579 | -0.10041 | 0.001278 | 0.00032029
7 | 0.98653 | -0.095156 | 0.0015766 | 0.00039514
8 | 0.9878 | -0.086083 | 0 | 0
9 | 0.98652 | -0.095233 | 0.00034238 | 8.5808e-05
10 | 0.98777 | -0.086318 | 0 | 0
11 | 0.98807 | -0.084149 | 0.00040769 | 0.00010218
12 | 0.98775 | -0.086445 | 0.0005478 | 0.00013729
13 | 0.98917 | -0.076322 | 0.0025356 | 0.00063549
14 | 0.99287 | -0.050141 | 0.00068661 | 0.00017208
15 | 0.99302 | -0.049124 | 0 | 0
16 | 0.99277 | -0.050881 | 0.00090347 | 0.00022643
17 | 0.99307 | -0.048758 | 0.00089112 | 0.00022334
18 | 0.99553 | -0.031389 | 0.0010978 | 0.00027514
19 | 0.99324 | -0.047509 | 0.0033946 | 0.00085077
20 | 0.99669 | -0.023228 | 0 | 0
21 | 0.9932 | -0.047831 | 0.0017832 | 0.00044691
22 | 0.99966 | -0.0024152 | 0.0021704 | 0.00054396
23 | 0.99971 | -0.0020218 | 0.00196 | 0.00049123
24 | 0.99975 | -0.0017473 | 0.0039037 | 0.00097836
25 | 0.9993 | -0.0048762 | 0.0026355 | 0.00066052
26 | 0.99696 | -0.021273 | 0 | 0
27 | 1 | 0 | -0.044849 | -0.011051
28 | 0.99175 | -0.058035 | 0 | 0
29 | 0.99654 | -0.024226 | 0.00088759 | 0.00022245
30 | 0.99139 | -0.060588 | 0.0043406 | 0.0010879
31 | 0.99031 | -0.068296 | 0 | 0
32 | 0.99121 | -0.0619 | 0.00054205 | 0.00013585
33 | 0.9965 | -0.024543 | 0.0024833 | 0.00062237
34 | 0.99024 | -0.068829 | 0.00082502 | 0.00020677
35 | 0.98993 | -0.071031 | 0.0015268 | 0.00038265
36 | 0.99054 | -0.066629 | 0.00023563 | 5.9055e-05
37 | 0.99018 | -0.06915 | 0.00082631 | 0.00020709
38 | 0.99022 | -0.068975 | 0.00039068 | 9.7914e-05
39 | 0.98968 | -0.072773 | 0 | 0
40 | 0.98961 | -0.073291 | 0.0012397 | 0.0003107
41 | 0.99017 | -0.069301 | 0.00066767 | 0.00016733
42 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00069646 | -0.00017455 | 0.0006965 | 0.00017373 | 4.5206e-08 | -8.1983e-07 | 0.0010509 | 0.0010506 | 0.0010509 | 0.98615 | -0.097846 | 0.98622 | -0.097375 | 0.38922
1 | 0.0035706 | 0.00089386 | -0.0035693 | -0.00089427 | 1.2849e-06 | -4.1086e-07 | 0.0053869 | 0.0053873 | 0.0053873 | 0.98622 | -0.097375 | 0.98585 | -0.099979 | 1.9953
2 | -0.0042671 | -0.0010676 | 0.0042688 | 0.0010674 | 1.7528e-06 | -1.9115e-07 | 0.0064375 | 0.0064372 | 0.0064375 | 0.98622 | -0.097375 | 0.98664 | -0.094397 | 2.3843
3 | 0.0028054 | 0.00070284 | -0.0028053 | -0.00070292 | 1.0304e-07 | -7.7794e-08 | 0.0042343 | 0.0042344 | 0.0042344 | 0.98585 | -0.099979 | 0.98581 | -0.10024 | 1.5683
4 | -0.0049494 | -0.001238 | 0.0049499 | 0.001238 | 5.3645e-07 | 9.2133e-09 | 0.0074637 | 0.0074636 | 0.0074637 | 0.98664 | -0.094397 | 0.98675 | -0.093611 | 2.7643
5 | 0.001278 | 0.00032013 | -0.001278 | -0.00032028 | 2.9607e-08 | -1.5118e-07 | 0.001929 | 0.001929 | 0.001929 | 0.98581 | -0.10024 | 0.98579 | -0.10041 | 0.71446
6 | 0.0019194 | 0.00047982 | -0.001919 | -0.00048066 | 4.0942e-07 | -8.4286e-07 | 0.002894 | 0.0028944 | 0.0028944 | 0.98675 | -0.093611 | 0.98653 | -0.095156 | 1.072
7 | -0.0068693 | -0.0017178 | 0.0068765 | 0.0017192 | 7.1292e-06 | 1.3801e-06 | 0.010358 | 0.010357 | 0.010358 | 0.98675 | -0.093611 | 0.9878 | -0.086083 | 3.8362
8 | 0.00034238 | 8.553e-05 | -0.00034238 | -8.5807e-05 | 3.631e-09 | -2.7723e-07 | 0.00051633 | 0.00051643 | 0.00051643 | 0.98653 | -0.095156 | 0.98652 | -0.095233 | 0.19127
9 | 0.00054782 | 0.00013648 | -0.0005478 | -0.000137 | 1.7673e-08 | -5.258e-07 | 0.00082494 | 0.00082513 | 0.00082513 | 0.9878 | -0.086083 | 0.98777 | -0.086318 | 0.3056
10 | -0.0074243 | -0.0018557 | 0.0074263 | 0.0018561 | 1.9778e-06 | 4.361e-07 | 0.011182 | 0.011182 | 0.011182 | 0.9878 | -0.086083 | 0.98807 | -0.084149 | 4.1415
11 | 0.0005478 | 0.000137 | -0.0005478 | -0.00013729 | 9.604e-09 | -2.8563e-07 | 0.00082513 | 0.00082524 | 0.00082524 | 0.98777 | -0.086318 | 0.98775 | -0.086445 | 0.30564
12 | -0.007834 | -0.0019583 | 0.0078424 | 0.0019603 | 8.4488e-06 | 2.0018e-06 | 0.011796 | 0.011796 | 0.011796 | 0.98807 | -0.084149 | 0.98917 | -0.076322 | 4.3689
13 | -0.010378 | -0.0025958 | 0.010388 | 0.0025988 | 1.027e-05 | 3.0821e-06 | 0.01561 | 0.01561 | 0.01561 | 0.98917 | -0.076322 | 0.99018 | -0.06915 | 5.7814
14 | -0.0015902 | -0.0003975 | 0.0015904 | 0.00039678 | 2.223e-07 | -7.262e-07 | 0.0023828 | 0.0023825 | 0.0023828 | 0.99287 | -0.050141 | 0.99302 | -0.049124 | 0.88252
15 | 0.00090356 | 0.00022542 | -0.00090347 | -0.00022643 | 9.2149e-08 | -1.0062e-06 | 0.0013538 | 0.0013542 | 0.0013542 | 0.99287 | -0.050141 | 0.99277 | -0.050881 | 0.50154
16 | -0.0015904 | -0.00039678 | 0.0015905 | 0.00039652 | 7.9798e-08 | -2.6078e-07 | 0.0023825 | 0.0023824 | 0.0023825 | 0.99302 | -0.049124 | 0.99307 | -0.048758 | 0.88242
17 | -0.0024816 | -0.00061985 | 0.0024819 | 0.0006195 | 3.1645e-07 | -3.531e-07 | 0.0037177 | 0.0037175 | 0.0037177 | 0.99307 | -0.048758 | 0.9932 | -0.047831 | 1.3769
18 | 0.007677 | 0.001921 | -0.0076599 | -0.0019172 | 1.7063e-05 | 3.8684e-06 | 0.011474 | 0.011475 | 0.011475 | 0.99553 | -0.031389 | 0.99324 | -0.047509 | 4.2499
19 | -0.0087748 | -0.0021962 | 0.0087847 | 0.0021988 | 9.8931e-06 | 2.6051e-06 | 0.013115 | 0.013114 | 0.013115 | 0.99553 | -0.031389 | 0.99669 | -0.023228 | 4.8573
20 | 0.0042653 | 0.0010664 | -0.0042651 | -0.0010664 | 1.8918e-07 | -2.336e-08 | 0.006389 | 0.0063891 | 0.0063891 | 0.99324 | -0.047509 | 0.9932 | -0.047831 | 2.3663
21 | 0.0033714 | 0.00084449 | -0.003371 | -0.00084469 | 4.6525e-07 | -2.0455e-07 | 0.0050333 | 0.0050334 | 0.0050334 | 0.99669 | -0.023228 | 0.99654 | -0.024226 | 1.8642
22 | -0.012156 | -0.0030433 | 0.012159 | 0.0030443 | 3.2839e-06 | 1.0547e-06 | 0.018147 | 0.018147 | 0.018147 | 0.99669 | -0.023228 | 0.99696 | -0.021273 | 6.7213
23 | -0.0021704 | -0.00054396 | 0.0021705 | 0.00054377 | 1.1816e-07 | -1.9241e-07 | 0.0032307 | 0.0032307 | 0.0032307 | 0.99966 | -0.0024152 | 0.99971 | -0.0020218 | 1.1966
24 | -0.0041306 | -0.001035 | 0.0041307 | 0.001035 | 1.569e-07 | -2.688e-08 | 0.0061481 | 0.006148 | 0.0061481 | 0.99971 | -0.0020218 | 0.99975 | -0.0017473 | 2.2771
25 | -0.0080344 | -0.0020133 | 0.0080364 | 0.0020138 | 1.9431e-06 | 4.6173e-07 | 0.011958 | 0.011958 | 0.011958 | 0.99975 | -0.0017473 | 1 | 0 | 4.429
26 | 0.033352 | 0.0083669 | -0.033277 | -0.0083385 | 7.568e-05 | 2.8465e-05 | 0.049666 | 0.049667 | 0.049667 | 0.9993 | -0.0048762 | 0.99696 | -0.021273 | 18.395
27 | -0.035988 | -0.0090275 | 0.036012 | 0.0090366 | 2.4353e-05 | 9.1886e-06 | 0.053591 | 0.053591 | 0.053591 | 0.9993 | -0.0048762 | 1 | 0 | 19.8484
28 | 0.021117 | 0.0052942 | -0.02101 | -0.0052552 | 0.00010702 | 3.8923e-05 | 0.031519 | 0.03152 | 0.03152 | 0.99696 | -0.021273 | 0.99175 | -0.058035 | 11.6741
29 | 0.0043421 | 0.0010877 | -0.0043406 | -0.0010878 | 1.5336e-06 | -1.5709e-07 | 0.0065147 | 0.006515 | 0.006515 | 0.99175 | -0.058035 | 0.99139 | -0.060588 | 2.4129
30 | 0.004658 | 0.0011611 | -0.0046515 | -0.0011613 | 6.5522e-06 | -2.5127e-07 | 0.0069866 | 0.0069876 | 0.0069876 | 0.99175 | -0.058035 | 0.99031 | -0.068296 | 2.588
31 | 0.01201 | 0.0030065 | -0.012004 | -0.0030044 | 6.4095e-06 | 2.0572e-06 | 0.018019 | 0.018019 | 0.018019 | 0.99175 | -0.058035 | 0.99121 | -0.0619 | 6.6736
32 | 0.0024834 | 0.00062224 | -0.0024833 | -0.00062237 | 1.09e-07 | -1.2359e-07 | 0.0037081 | 0.0037081 | 0.0037081 | 0.99654 | -0.024226 | 0.9965 | -0.024543 | 1.3734
33 | 0.0018836 | 0.00047094 | -0.0018834 | -0.00047124 | 1.383e-07 | -3.0288e-07 | 0.0028298 | 0.0028299 | 0.0028299 | 0.99031 | -0.068296 | 0.99024 | -0.068829 | 1.0481
34 | 0.0027679 | 0.00069037 | -0.0027669 | -0.00069121 | 1.0392e-06 | -8.3919e-07 | 0.0041578 | 0.0041583 | 0.0041583 | 0.99031 | -0.068296 | 0.98993 | -0.071031 | 1.5401
35 | 0.011462 | 0.0028686 | -0.011454 | -0.0028662 | 7.4781e-06 | 2.3547e-06 | 0.017205 | 0.017205 | 0.017205 | 0.99121 | -0.0619 | 0.99054 | -0.066629 | 6.3723
36 | 0.0010584 | 0.00026448 | -0.0010584 | -0.00026464 | 2.1289e-08 | -1.6537e-07 | 0.0015902 | 0.0015902 | 0.0015902 | 0.99024 | -0.068829 | 0.99022 | -0.068975 | 0.58897
37 | 0.0012401 | 0.00030856 | -0.0012398 | -0.0003102 | 2.9655e-07 | -1.6448e-06 | 0.0018633 | 0.0018639 | 0.0018639 | 0.98993 | -0.071031 | 0.98968 | -0.072773 | 0.69032
38 | 0.011219 | 0.0028072 | -0.011215 | -0.0028059 | 3.9025e-06 | 1.2176e-06 | 0.016851 | 0.016851 | 0.016851 | 0.99054 | -0.066629 | 0.99018 | -0.06915 | 6.2412
39 | 0.0006677 | 0.00016673 | -0.00066767 | -0.00016733 | 3.0051e-08 | -6.0391e-07 | 0.0010031 | 0.0010034 | 0.0010034 | 0.99022 | -0.068975 | 0.99017 | -0.069301 | 0.37162
40 | 0.0012398 | 0.0003102 | -0.0012397 | -0.0003107 | 8.8736e-08 | -4.9178e-07 | 0.0018639 | 0.0018641 | 0.0018641 | 0.98968 | -0.072773 | 0.98961 | -0.073291 | 0.69039

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.047245 | 0.011651

## res_load
| p_mw | q_mvar
0 | 0.00069646 | 0.00017455
1 | 0.00076384 | 0.00019144
2 | 0.00068058 | 0.00017057
3 | 0.0015273 | 0.00038279
4 | 0.001278 | 0.00032029
5 | 0.0015766 | 0.00039514
6 | 0.00034238 | 8.5808e-05
7 | 0.00040769 | 0.00010218
8 | 0.0005478 | 0.00013729
9 | 0.0025356 | 0.00063549
10 | 0.00068661 | 0.00017208
11 | 0.00090347 | 0.00022643
12 | 0.00089112 | 0.00022334
13 | 0.0010978 | 0.00027514
14 | 0.0033946 | 0.00085077
15 | 0.0017832 | 0.00044691
16 | 0.0021704 | 0.00054396
17 | 0.00196 | 0.00049123
18 | 0.0039037 | 0.00097836
19 | 0.0026355 | 0.00066052
20 | 0.0023961 | 0.00060052
21 | 0.00088759 | 0.00022245
22 | 0.0043406 | 0.0010879
23 | 0.00054205 | 0.00013585
24 | 0.0024833 | 0.00062237
25 | 0.00082502 | 0.00020677
26 | 0.0015268 | 0.00038265
27 | 0.00023563 | 5.9055e-05
28 | 0.00082631 | 0.00020709
29 | 0.00039068 | 9.7914e-05
30 | 0.0012397 | 0.0003107
31 | 0.00066767 | 0.00016733

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1