## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1364-39_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1364-39_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1364-39_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1364-39_0_3_node_11 | 0.4 | n |  | TRUE
4 | bus_LV_1364-39_0_3_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_1364-39_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1364-39_0_3_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1364-39_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1364-39_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1364-39_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1364-39_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1364-39_0_3_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_1364-39_0_3_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1364-39_0_3_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_1364-39_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1364-39_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1364-39_0_3_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_1364-39_0_3_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_1364-39_0_3_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1364-39_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1364-39_0_3_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1364-39_0_3_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1364-39_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1364-39_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1364-39_0_3_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1364-39_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_1364-39_0_3_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1364-39_0_3_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1364-39_0_3_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1364-39_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1364-39_0_3_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1364-39_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_MV_133_0_node_98 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1364-39_0_3_load_0 | 0 | 0.0047948 | 0.0012017 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1364-39_0_3_load_1 | 1 | 0.0045692 | 0.0011451 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1364-39_0_3_load_2 | 2 | 0.0039514 | 0.00099032 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1364-39_0_3_load_13 | 4 | 0.0048303 | 0.0012106 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1364-39_0_3_load_10 | 5 | 0.0059094 | 0.001481 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1364-39_0_3_load_3 | 6 | 0.0035371 | 0.00088649 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1364-39_0_3_load_4 | 7 | 0.086496 | 0.021678 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1364-39_0_3_load_6 | 9 | 0.0039566 | 0.00099161 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1364-39_0_3_load_20 | 11 | 0.011765 | 0.0029487 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1364-39_0_3_load_32 | 13 | 0.0023953 | 0.00060031 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1364-39_0_3_load_24 | 16 | 0.0071169 | 0.0017837 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1364-39_0_3_load_29 | 17 | 0.0040448 | 0.0010137 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1364-39_0_3_load_19 | 18 | 0.0033778 | 0.00084656 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1364-39_0_3_load_15 | 19 | 0.0010753 | 0.00026949 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1364-39_0_3_load_23 | 20 | 0.0041645 | 0.0010437 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1364-39_0_3_load_30 | 21 | 0.0024107 | 0.00060418 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1364-39_0_3_load_28 | 25 | 0.0041454 | 0.0010389 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1364-39_0_3_load_25 | 26 | 0.022668 | 0.0056812 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1364-39_0_3_load_16 | 27 | 0.0027455 | 0.00068808 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1364-39_0_3_load_31 | 30 | 0.053716 | 0.013463 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1364-39_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.006056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1364-39_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.023098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1364-39_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.014993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1364-39_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0046513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1364-39_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.037064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1364-39_0_3_line_5 | NAYY 4x150 SE | 4 | 21 | 0.0089273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1364-39_0_3_line_6 | NAYY 4x150 SE | 5 | 22 | 0.028508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1364-39_0_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.021145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1364-39_0_3_line_8 | NAYY 4x150 SE | 6 | 8 | 0.041135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1364-39_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.024204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1364-39_0_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.035854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1364-39_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.0059645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1364-39_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.016078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1364-39_0_3_line_13 | NAYY 4x150 SE | 10 | 13 | 0.0075486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1364-39_0_3_line_14 | NAYY 4x150 SE | 11 | 18 | 0.016768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1364-39_0_3_line_15 | NAYY 4x150 SE | 12 | 19 | 0.011898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1364-39_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.002665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1364-39_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.022142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1364-39_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.023836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1364-39_0_3_line_19 | NAYY 4x150 SE | 16 | 20 | 0.0019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1364-39_0_3_line_20 | NAYY 4x150 SE | 17 | 21 | 0.023702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1364-39_0_3_line_21 | NAYY 4x150 SE | 18 | 23 | 0.00501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1364-39_0_3_line_22 | NAYY 4x150 SE | 19 | 27 | 0.022228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1364-39_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.062176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1364-39_0_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.022319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1364-39_0_3_line_25 | NAYY 4x150 SE | 24 | 26 | 0.024382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1364-39_0_3_line_26 | NAYY 4x150 SE | 25 | 28 | 0.012531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1364-39_0_3_line_27 | NAYY 4x150 SE | 26 | 31 | 0.037013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1364-39_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.011374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1364-39_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.016291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1364-39_0_3_line_30 | NAYY 4x150 SE | 29 | 31 | 0.028779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1364-39_0_3_trafo_6 | 0.25 MVA 20/0.4 kV | 32 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2688116.5348 | 1205641.4131 | 2688122.5388 | 1205642.2056
1 | 2688145.5582 | 1205641.9477 | 2688128.2286 | 1205642.9565 | 2688122.5388 | 1205642.2056
2 | 2688160.5255 | 1205641.0765 | 2688145.5582 | 1205641.9477
3 | 2688160.5255 | 1205641.0765 | 2688160.1836 | 1205636.4377
4 | 2688160.5255 | 1205641.0765 | 2688162.3694 | 1205666.1089 | 2688162.9117 | 1205678.0602
5 | 2688160.1836 | 1205636.4377 | 2688159.5273 | 1205627.5346
6 | 2688164.9222 | 1205706.4841 | 2688163.6836 | 1205695.0695 | 2688162.9117 | 1205678.0602
7 | 2688210.7863 | 1205604.4597 | 2688210.7052 | 1205605.3274 | 2688212.584 | 1205609.9693 | 2688222.407 | 1205621.6554
8 | 2688221.3433 | 1205570.106 | 2688226.5723 | 1205578.144 | 2688215.6533 | 1205590.1684 | 2688211.2564 | 1205599.4317 | 2688210.7863 | 1205604.4597
9 | 2688222.407 | 1205621.6554 | 2688222.407 | 1205621.6554 | 2688211.3315 | 1205631.9207 | 2688209.5243 | 1205640.8419
10 | 2688254.7372 | 1205556.8352 | 2688231.9971 | 1205566.2497 | 2688221.3433 | 1205570.106
11 | 2688209.4334 | 1205646.7868 | 2688209.3375 | 1205641.7644 | 2688209.5243 | 1205640.8419
12 | 2688260.1898 | 1205571.87 | 2688258.6677 | 1205565.2321 | 2688254.7372 | 1205556.8352
13 | 2688254.7372 | 1205556.8352 | 2688261.4076 | 1205553.3015
14 | 2688209.4334 | 1205646.7868 | 2688209.7533 | 1205663.5514 | 2688209.7533 | 1205663.5514
15 | 2688260.1898 | 1205571.87 | 2688268.9472 | 1205579.9245
16 | 2688153.3611 | 1205580.2087 | 2688156.0324 | 1205580.1258
17 | 2688153.3611 | 1205580.2087 | 2688131.2191 | 1205580.2101
18 | 2688156.0324 | 1205580.1258 | 2688157.7848 | 1205603.8971
19 | 2688129.3191 | 1205580.2102 | 2688131.2191 | 1205580.2101
20 | 2688159.5273 | 1205627.5346 | 2688157.7848 | 1205603.8971
21 | 2688212.9984 | 1205667.3685 | 2688209.7533 | 1205663.5514
22 | 2688276.0215 | 1205599.6298 | 2688272.7031 | 1205595.5593 | 2688272.4231 | 1205584.1477 | 2688271.5299 | 1205582.3 | 2688268.9472 | 1205579.9245
23 | 2688164.9222 | 1205706.4841 | 2688188.3408 | 1205688.1735 | 2688207.7035 | 1205673.5721 | 2688210.2755 | 1205669.3963 | 2688212.9984 | 1205667.3685
24 | 2688260.7741 | 1205633.6968 | 2688260.9508 | 1205629.4634 | 2688274.0971 | 1205617.049
25 | 2688260.7741 | 1205633.6968 | 2688275.107 | 1205653.4208
26 | 2688283.2081 | 1205608.4453 | 2688274.0971 | 1205617.049
27 | 2688296.8651 | 1205683.3628 | 2688275.107 | 1205653.4208
28 | 2688283.2081 | 1205608.4453 | 2688276.0215 | 1205599.6298
29 | 2688274.7838 | 1205697.6346 | 2688273.1283 | 1205695.3865 | 2688268.7927 | 1205691.7644 | 2688264.161 | 1205690.1505 | 2688261.2629 | 1205689.6295
30 | 2688274.7838 | 1205697.6346 | 2688277.4936 | 1205697.0076 | 2688285.0726 | 1205695.2963 | 2688287.7814 | 1205694.736 | 2688287.6814 | 1205692.244 | 2688288.935 | 1205689.772 | 2688296.8651 | 1205683.3628

## bus_geodata
| x | y | coords
0 | 2688116.5348 | 1205641.4131
1 | 2688122.5388 | 1205642.2056
2 | 2688145.5582 | 1205641.9477
3 | 2688160.5255 | 1205641.0765
4 | 2688160.1836 | 1205636.4377
5 | 2688162.9117 | 1205678.0602
6 | 2688210.7863 | 1205604.4597
7 | 2688222.407 | 1205621.6554
8 | 2688221.3433 | 1205570.106
9 | 2688209.5243 | 1205640.8419
10 | 2688254.7372 | 1205556.8352
11 | 2688209.4334 | 1205646.7868
12 | 2688260.1898 | 1205571.87
13 | 2688261.4076 | 1205553.3015
14 | 2688153.3611 | 1205580.2087
15 | 2688156.0324 | 1205580.1258
16 | 2688131.2191 | 1205580.2101
17 | 2688157.7848 | 1205603.8971
18 | 2688209.7533 | 1205663.5514
19 | 2688268.9472 | 1205579.9245
20 | 2688129.3191 | 1205580.2102
21 | 2688159.5273 | 1205627.5346
22 | 2688164.9222 | 1205706.4841
23 | 2688212.9984 | 1205667.3685
24 | 2688260.7741 | 1205633.6969
25 | 2688274.0971 | 1205617.049
26 | 2688275.107 | 1205653.4208
27 | 2688276.0215 | 1205599.6298
28 | 2688283.2081 | 1205608.4453
29 | 2688274.7838 | 1205697.6346
30 | 2688261.2629 | 1205689.6295
31 | 2688296.8651 | 1205683.3628
32 | 2688212.9984 | 1205667.3685

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99011 | -0.069294 | 0.0047948 | 0.0012017
1 | 0.99015 | -0.068998 | 0.0045692 | 0.0011451
2 | 0.99046 | -0.066797 | 0.0039514 | 0.00099032
3 | 0.99075 | -0.064766 | 0 | 0
4 | 0.9906 | -0.065833 | 0.0048303 | 0.0012106
5 | 0.99267 | -0.051264 | 0.0059094 | 0.001481
6 | 0.99551 | -0.031026 | 0.0035371 | 0.00088649
7 | 0.99691 | -0.021423 | 0.086496 | 0.021678
8 | 0.9929 | -0.049047 | 0 | 0
9 | 1 | 0 | -0.23741 | -0.059678
10 | 0.99062 | -0.064831 | 0 | 0
11 | 0.99951 | -0.0033925 | 0.011765 | 0.0029487
12 | 0.98963 | -0.071736 | 0 | 0
13 | 0.9906 | -0.065015 | 0.0023953 | 0.00060031
14 | 0.98942 | -0.074192 | 0 | 0
15 | 0.98946 | -0.073886 | 0 | 0
16 | 0.98906 | -0.07674 | 0.0071169 | 0.0017837
17 | 0.98985 | -0.071145 | 0.0040448 | 0.0010137
18 | 0.99842 | -0.010972 | 0.0033778 | 0.00084656
19 | 0.98816 | -0.08198 | 0.0010753 | 0.00026949
20 | 0.98905 | -0.076821 | 0.0041645 | 0.0010437
21 | 0.99037 | -0.067445 | 0.0024107 | 0.00060418
22 | 0.99438 | -0.039213 | 0 | 0
23 | 0.99812 | -0.01307 | 0 | 0
24 | 0.98014 | -0.13847 | 0 | 0
25 | 0.98263 | -0.1208 | 0.0041454 | 0.0010389
26 | 0.97741 | -0.15787 | 0.022668 | 0.0056812
27 | 0.98545 | -0.10096 | 0.0027455 | 0.00068808
28 | 0.98411 | -0.11038 | 0 | 0
29 | 0.97222 | -0.19499 | 0 | 0
30 | 0.97093 | -0.20425 | 0.053716 | 0.013463
31 | 0.97449 | -0.17871 | 0 | 0
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0047948 | -0.0012017 | 0.004795 | 0.0012017 | 1.9623e-07 | -2.4173e-09 | 0.0072061 | 0.007206 | 0.0072061 | 0.99011 | -0.069294 | 0.99015 | -0.068998 | 2.6689
1 | -0.0093642 | -0.0023468 | 0.0093671 | 0.0023476 | 2.8544e-06 | 8.0064e-07 | 0.014073 | 0.014073 | 0.014073 | 0.99015 | -0.068998 | 0.99046 | -0.066797 | 5.2121
2 | -0.013318 | -0.003338 | 0.013322 | 0.0033392 | 3.7455e-06 | 1.2476e-06 | 0.020009 | 0.020009 | 0.020009 | 0.99046 | -0.066797 | 0.99075 | -0.064766 | 7.4107
3 | 0.022591 | 0.005664 | -0.022588 | -0.0056627 | 3.3415e-06 | 1.2253e-06 | 0.033931 | 0.033931 | 0.033931 | 0.99075 | -0.064766 | 0.9906 | -0.065833 | 12.5669
4 | -0.035913 | -0.0090032 | 0.035981 | 0.0090286 | 6.7289e-05 | 2.5402e-05 | 0.053939 | 0.053939 | 0.053939 | 0.99075 | -0.064766 | 0.99267 | -0.051264 | 19.9776
5 | 0.017757 | 0.0044521 | -0.017754 | -0.0044507 | 3.9637e-06 | 1.4096e-06 | 0.026675 | 0.026675 | 0.026675 | 0.9906 | -0.065833 | 0.99037 | -0.067445 | 9.8796
6 | -0.04189 | -0.01051 | 0.04196 | 0.010536 | 7.0152e-05 | 2.6612e-05 | 0.062798 | 0.062797 | 0.062798 | 0.99267 | -0.051264 | 0.99438 | -0.039213 | 23.2583
7 | -0.092107 | -0.023324 | 0.092232 | 0.023371 | 0.0001252 | 4.7604e-05 | 0.13776 | 0.13776 | 0.13776 | 0.99551 | -0.031026 | 0.99691 | -0.021423 | 25.5109
8 | 0.088569 | 0.022437 | -0.088344 | -0.022352 | 0.00022523 | 8.5558e-05 | 0.13247 | 0.13247 | 0.13247 | 0.99551 | -0.031026 | 0.9929 | -0.049047 | 24.5319
9 | -0.17873 | -0.045049 | 0.17927 | 0.045255 | 0.0005378 | 0.00020621 | 0.26687 | 0.26687 | 0.26687 | 0.99691 | -0.021423 | 1 | 0 | 49.4197
10 | 0.088344 | 0.022352 | -0.088148 | -0.022277 | 0.00019631 | 7.4579e-05 | 0.13247 | 0.13247 | 0.13247 | 0.9929 | -0.049047 | 0.99062 | -0.064831 | 24.532
11 | 0.057344 | 0.014423 | -0.057317 | -0.014412 | 2.711e-05 | 1.0349e-05 | 0.085347 | 0.085347 | 0.085347 | 1 | 0 | 0.99951 | -0.0033925 | 31.6099
12 | 0.085753 | 0.021677 | -0.085669 | -0.021645 | 8.3315e-05 | 3.1631e-05 | 0.12887 | 0.12887 | 0.12887 | 0.99062 | -0.064831 | 0.98963 | -0.071736 | 23.8657
13 | 0.0023953 | 0.00060024 | -0.0023953 | -0.00060031 | 6.0978e-08 | -7.3728e-08 | 0.003598 | 0.003598 | 0.003598 | 0.99062 | -0.064831 | 0.9906 | -0.065015 | 1.3326
14 | 0.045552 | 0.011464 | -0.045503 | -0.011445 | 4.8141e-05 | 1.8296e-05 | 0.067831 | 0.067831 | 0.067831 | 0.99951 | -0.0033925 | 0.99842 | -0.010972 | 25.1227
15 | 0.085669 | 0.021645 | -0.085546 | -0.021598 | 0.00012331 | 4.7275e-05 | 0.12887 | 0.12887 | 0.12887 | 0.98963 | -0.071736 | 0.98816 | -0.08198 | 47.7315
16 | -0.011285 | -0.0028286 | 0.011286 | 0.0028288 | 4.7904e-07 | 1.5002e-07 | 0.016973 | 0.016973 | 0.016973 | 0.98942 | -0.074192 | 0.98946 | -0.073886 | 6.2861
17 | 0.011285 | 0.0028286 | -0.011281 | -0.0028274 | 3.9801e-06 | 1.2466e-06 | 0.016973 | 0.016973 | 0.016973 | 0.98942 | -0.074192 | 0.98906 | -0.07674 | 6.2862
18 | -0.011286 | -0.0028288 | 0.01129 | 0.0028301 | 4.2845e-06 | 1.3416e-06 | 0.016973 | 0.016972 | 0.016973 | 0.98946 | -0.073886 | 0.98985 | -0.071145 | 6.2861
19 | 0.0041645 | 0.0010437 | -0.0041645 | -0.0010437 | 4.6543e-08 | -6.4835e-09 | 0.0062654 | 0.0062654 | 0.0062654 | 0.98906 | -0.07674 | 0.98905 | -0.076821 | 2.3205
20 | -0.015335 | -0.0038438 | 0.015343 | 0.0038465 | 7.8598e-06 | 2.7182e-06 | 0.023053 | 0.023053 | 0.023053 | 0.98985 | -0.071145 | 0.99037 | -0.067445 | 8.5381
21 | 0.042126 | 0.010599 | -0.042113 | -0.010594 | 1.2328e-05 | 4.6762e-06 | 0.062797 | 0.062797 | 0.062797 | 0.99842 | -0.010972 | 0.99812 | -0.01307 | 23.2582
22 | 0.084471 | 0.021328 | -0.084246 | -0.021242 | 0.00022462 | 8.6107e-05 | 0.12726 | 0.12726 | 0.12726 | 0.98816 | -0.08198 | 0.98545 | -0.10096 | 47.1318
23 | -0.04196 | -0.010536 | 0.042113 | 0.010594 | 0.000153 | 5.8036e-05 | 0.062797 | 0.062797 | 0.062797 | 0.99438 | -0.039213 | 0.99812 | -0.01307 | 23.2583
24 | -0.076939 | -0.019356 | 0.077129 | 0.019429 | 0.0001901 | 7.2834e-05 | 0.11683 | 0.11683 | 0.11683 | 0.98014 | -0.13847 | 0.98263 | -0.1208 | 43.2715
25 | 0.076939 | 0.019356 | -0.076731 | -0.019276 | 0.00020767 | 7.9568e-05 | 0.11683 | 0.11683 | 0.11683 | 0.98014 | -0.13847 | 0.97741 | -0.15787 | 43.2716
26 | -0.081275 | -0.020468 | 0.081393 | 0.020513 | 0.00011851 | 4.5424e-05 | 0.12311 | 0.12311 | 0.12311 | 0.98263 | -0.1208 | 0.98411 | -0.11038 | 45.5964
27 | 0.054063 | 0.013595 | -0.053907 | -0.013535 | 0.00015652 | 5.9739e-05 | 0.082323 | 0.082323 | 0.082323 | 0.97741 | -0.15787 | 0.97449 | -0.17871 | 30.4901
28 | 0.081501 | 0.020554 | -0.081393 | -0.020513 | 0.00010757 | 4.1227e-05 | 0.12311 | 0.12311 | 0.12311 | 0.98545 | -0.10096 | 0.98411 | -0.11038 | 45.5964
29 | 0.053785 | 0.013489 | -0.053716 | -0.013463 | 6.8893e-05 | 2.6296e-05 | 0.082323 | 0.082323 | 0.082323 | 0.97222 | -0.19499 | 0.97093 | -0.20425 | 30.4902
30 | -0.053785 | -0.013489 | 0.053907 | 0.013535 | 0.00012171 | 4.6452e-05 | 0.082323 | 0.082323 | 0.082323 | 0.97222 | -0.19499 | 0.97449 | -0.17871 | 30.4901

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24137 | 0.06067

## res_load
| p_mw | q_mvar
0 | 0.0047948 | 0.0012017
1 | 0.0045692 | 0.0011451
2 | 0.0039514 | 0.00099032
3 | 0.0048303 | 0.0012106
4 | 0.0059094 | 0.001481
5 | 0.0035371 | 0.00088649
6 | 0.086496 | 0.021678
7 | 0.0039566 | 0.00099161
8 | 0.011765 | 0.0029487
9 | 0.0023953 | 0.00060031
10 | 0.0071169 | 0.0017837
11 | 0.0040448 | 0.0010137
12 | 0.0033778 | 0.00084656
13 | 0.0010753 | 0.00026949
14 | 0.0041645 | 0.0010437
15 | 0.0024107 | 0.00060418
16 | 0.0041454 | 0.0010389
17 | 0.022668 | 0.0056812
18 | 0.0027455 | 0.00068808
19 | 0.053716 | 0.013463

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1