## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1364-44_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1364-44_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1364-44_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1364-44_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1364-44_0_2_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1364-44_0_2_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1364-44_0_2_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1364-44_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1364-44_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1364-44_0_2_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1364-44_0_2_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1364-44_0_2_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1364-44_0_2_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1364-44_0_2_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_1364-44_0_2_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1364-44_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1364-44_0_2_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1364-44_0_2_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1364-44_0_2_node_25 | 0.4 | n |  | TRUE
19 | bus_LV_1364-44_0_2_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1364-44_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1364-44_0_2_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1364-44_0_2_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_1364-44_0_2_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_1364-44_0_2_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1364-44_0_2_node_21 | 0.4 | n |  | TRUE
26 | bus_MV_133_0_node_46 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1364-44_0_2_load_0 | 0 | 0.0075721 | 0.0018977 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1364-44_0_2_load_3 | 2 | 0.0051181 | 0.0012827 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1364-44_0_2_load_4 | 3 | 0.0035106 | 0.00087984 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1364-44_0_2_load_5 | 4 | 0.0017483 | 0.00043816 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1364-44_0_2_load_18 | 5 | 0.0097649 | 0.0024473 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1364-44_0_2_load_22 | 6 | 0.0013353 | 0.00033465 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1364-44_0_2_load_6 | 7 | 0.0065088 | 0.0016313 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1364-44_0_2_load_7 | 8 | 0.0017005 | 0.00042618 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1364-44_0_2_load_9 | 10 | 0.0017425 | 0.00043671 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1364-44_0_2_load_10 | 11 | 0.0048945 | 0.0012267 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1364-44_0_2_load_19 | 13 | 0.0075143 | 0.0018833 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1364-44_0_2_load_17 | 14 | 0.0018425 | 0.00046178 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1364-44_0_2_load_12 | 15 | 0.001656 | 0.00041503 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1364-44_0_2_load_20 | 16 | 0.0064553 | 0.0016179 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1364-44_0_2_load_24 | 17 | 0.0071832 | 0.0018003 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1364-44_0_2_load_25 | 18 | 0.0022176 | 0.00055578 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1364-44_0_2_load_28 | 22 | 0.0063591 | 0.0015937 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1364-44_0_2_load_26 | 23 | 0.01304 | 0.0032682 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1364-44_0_2_load_27 | 24 | 0.0026548 | 0.00066536 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1364-44_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.03739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1364-44_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.018641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1364-44_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.021953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1364-44_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.00045591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1364-44_0_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0095593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1364-44_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.01943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1364-44_0_2_line_6 | NAYY 4x150 SE | 6 | 25 | 0.045798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1364-44_0_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.0050722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1364-44_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.017335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1364-44_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.017735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1364-44_0_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0053107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1364-44_0_2_line_11 | NAYY 4x150 SE | 10 | 12 | 0.011857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1364-44_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.0050337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1364-44_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.033992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1364-44_0_2_line_14 | NAYY 4x150 SE | 12 | 15 | 0.01185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1364-44_0_2_line_15 | NAYY 4x150 SE | 13 | 16 | 0.024743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1364-44_0_2_line_16 | NAYY 4x150 SE | 15 | 19 | 0.023464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1364-44_0_2_line_17 | NAYY 4x150 SE | 16 | 25 | 0.03585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1364-44_0_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.016429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1364-44_0_2_line_19 | NAYY 4x150 SE | 18 | 23 | 0.0066927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1364-44_0_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.01348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1364-44_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.032281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1364-44_0_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.009551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1364-44_0_2_line_23 | NAYY 4x150 SE | 20 | 23 | 0.020723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1364-44_0_2_line_24 | NAYY 4x150 SE | 21 | 24 | 0.039354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1364-44_0_2_trafo_8 | 0.25 MVA 20/0.4 kV | 26 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2688966.5814 | 1205689.3954 | 2688995.2435 | 1205683.8633 | 2689003.4393 | 1205684.0727
1 | 2688966.5814 | 1205689.3954 | 2688964.6189 | 1205670.8584
2 | 2688964.6189 | 1205670.8584 | 2688962.3078 | 1205649.0274
3 | 2688962.2598 | 1205648.5741 | 2688962.3078 | 1205649.0274
4 | 2688962.2598 | 1205648.5741 | 2688961.2535 | 1205639.0679
5 | 2688959.3605 | 1205619.7305 | 2688960.4334 | 1205631.3213 | 2688961.2535 | 1205639.0679
6 | 2688955.1393 | 1205574.1272 | 2688959.3605 | 1205619.7305
7 | 2689021.3881 | 1205605.7569 | 2689025.0612 | 1205602.2589
8 | 2689008.835 | 1205617.7114 | 2689021.3881 | 1205605.7569
9 | 2689035.9785 | 1205588.472 | 2689030.9975 | 1205596.6057 | 2689025.0612 | 1205602.2589
10 | 2689008.835 | 1205617.7114 | 2689004.4506 | 1205614.7146
11 | 2689042.1708 | 1205578.3603 | 2689035.9785 | 1205588.472
12 | 2689004.4506 | 1205614.7146 | 2689000.77 | 1205612.1987 | 2689000.3355 | 1205611.8216
13 | 2689042.1708 | 1205578.3603 | 2689040.7924 | 1205577.4392 | 2689027.0173 | 1205561.023 | 2689023.8639 | 1205557.7183 | 2689018.1319 | 1205555.0185
14 | 2689042.1708 | 1205578.3603 | 2689046.8706 | 1205581.5103 | 2689052.52 | 1205582.7175 | 2689052.9324 | 1205582.6728
15 | 2688981.6488 | 1205595.6029 | 2689000.3355 | 1205611.8216
16 | 2689073.709 | 1205573.8499 | 2689072.1157 | 1205576.1165 | 2689066.8517 | 1205579.6737 | 2689060.9929 | 1205581.7988 | 2689052.9324 | 1205582.6728
17 | 2688955.1393 | 1205574.1272 | 2688961.7265 | 1205574.1698 | 2688981.5445 | 1205595.5124 | 2688981.6488 | 1205595.6029
18 | 2689060.0793 | 1205623.0057 | 2689065.3926 | 1205612.1955 | 2689067.6563 | 1205608.4415
19 | 2689072.0248 | 1205603.611 | 2689069.6983 | 1205605.055 | 2689067.6563 | 1205608.4415
20 | 2689073.709 | 1205573.8499 | 2689076.1294 | 1205575.7984 | 2689080.837 | 1205585.0525
21 | 2689082.0065 | 1205543.3982 | 2689082.5003 | 1205550.5769 | 2689078.4214 | 1205564.9477 | 2689076.5927 | 1205569.7347 | 2689073.709 | 1205573.8499
22 | 2689087.9842 | 1205590.8963 | 2689082.1006 | 1205587.5508 | 2689080.837 | 1205585.0525
23 | 2689080.837 | 1205585.0525 | 2689079.1668 | 1205588.3964 | 2689074.9289 | 1205594.5595 | 2689072.0248 | 1205603.611
24 | 2689082.0065 | 1205543.3982 | 2689076.3281 | 1205537.5096 | 2689046.6807 | 1205527.8761

## bus_geodata
| x | y | coords
0 | 2689003.4393 | 1205684.0727
1 | 2688966.5814 | 1205689.3954
2 | 2688964.6189 | 1205670.8584
3 | 2688962.3078 | 1205649.0274
4 | 2688962.2598 | 1205648.5741
5 | 2688961.2535 | 1205639.0679
6 | 2688959.3605 | 1205619.7305
7 | 2689021.3881 | 1205605.7569
8 | 2689025.0612 | 1205602.2589
9 | 2689008.835 | 1205617.7114
10 | 2689035.9785 | 1205588.472
11 | 2689004.4506 | 1205614.7146
12 | 2689042.1708 | 1205578.3603
13 | 2689000.3355 | 1205611.8216
14 | 2689018.1319 | 1205555.0185
15 | 2689052.9324 | 1205582.6728
16 | 2688981.6488 | 1205595.6029
17 | 2689060.0793 | 1205623.0057
18 | 2689067.6563 | 1205608.4415
19 | 2689073.709 | 1205573.8499
20 | 2689080.837 | 1205585.0525
21 | 2689082.0065 | 1205543.3982
22 | 2689087.9842 | 1205590.8963
23 | 2689072.0248 | 1205603.611
24 | 2689046.6807 | 1205527.8761
25 | 2688955.1393 | 1205574.1272
26 | 2689053.5932 | 1205636.2019

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99262 | -0.051721 | 0.0075721 | 0.0018977
1 | 0.99303 | -0.048853 | 0 | 0
2 | 0.99323 | -0.047424 | 0.0051181 | 0.0012827
3 | 0.99363 | -0.044606 | 0.0035106 | 0.00087984
4 | 0.99364 | -0.044531 | 0.0017483 | 0.00043816
5 | 0.99389 | -0.042796 | 0.0097649 | 0.0024473
6 | 0.99466 | -0.037358 | 0.0013353 | 0.00033465
7 | 0.99889 | -0.0077817 | 0.0065088 | 0.0016313
8 | 0.99861 | -0.0097315 | 0.0017005 | 0.00042618
9 | 1 | 0 | -0.09402 | -0.023411
10 | 0.99767 | -0.016255 | 0.0017425 | 0.00043671
11 | 0.99964 | -0.0025416 | 0.0048945 | 0.0012267
12 | 0.99708 | -0.020415 | 0 | 0
13 | 0.99933 | -0.004706 | 0.0075143 | 0.0018833
14 | 0.99699 | -0.021045 | 0.0018425 | 0.00046178
15 | 0.99652 | -0.024358 | 0.001656 | 0.00041503
16 | 0.99807 | -0.013502 | 0.0064553 | 0.0016179
17 | 0.99398 | -0.042221 | 0.0071832 | 0.0018003
18 | 0.99415 | -0.041029 | 0.0022176 | 0.00055578
19 | 0.99546 | -0.031787 | 0 | 0
20 | 0.9949 | -0.0357 | 0 | 0
21 | 0.99534 | -0.032652 | 0 | 0
22 | 0.99482 | -0.036313 | 0.0063591 | 0.0015937
23 | 0.99424 | -0.040393 | 0.01304 | 0.0032682
24 | 0.99519 | -0.033706 | 0.0026548 | 0.00066536
25 | 0.99657 | -0.023957 | 0 | 0
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0075721 | -0.0018977 | 0.0075751 | 0.0018984 | 3.0061e-06 | 6.7268e-07 | 0.011351 | 0.011351 | 0.011351 | 0.99262 | -0.051721 | 0.99303 | -0.048853 | 4.2041
1 | -0.0075751 | -0.0018984 | 0.0075766 | 0.0018987 | 1.4987e-06 | 3.352e-07 | 0.011351 | 0.011351 | 0.011351 | 0.99303 | -0.048853 | 0.99323 | -0.047424 | 4.204
2 | -0.012695 | -0.0031815 | 0.0127 | 0.0031831 | 4.9548e-06 | 1.6215e-06 | 0.019018 | 0.019018 | 0.019018 | 0.99323 | -0.047424 | 0.99363 | -0.044606 | 7.0439
3 | -0.01621 | -0.0040629 | 0.01621 | 0.004063 | 1.6765e-07 | 5.8575e-08 | 0.024276 | 0.024276 | 0.024276 | 0.99363 | -0.044606 | 0.99364 | -0.044531 | 8.991
4 | -0.017959 | -0.0045011 | 0.017963 | 0.0045027 | 4.3143e-06 | 1.5355e-06 | 0.026894 | 0.026894 | 0.026894 | 0.99364 | -0.044531 | 0.99389 | -0.042796 | 9.9607
5 | -0.027728 | -0.00695 | 0.027749 | 0.0069578 | 2.0895e-05 | 7.7844e-06 | 0.041513 | 0.041513 | 0.041513 | 0.99389 | -0.042796 | 0.99466 | -0.037358 | 15.3753
6 | -0.029084 | -0.0072924 | 0.029138 | 0.0073126 | 5.4104e-05 | 2.0213e-05 | 0.043511 | 0.043511 | 0.043511 | 0.99466 | -0.037358 | 0.99657 | -0.023957 | 16.1151
7 | 0.038545 | 0.0096769 | -0.038534 | -0.0096729 | 1.0437e-05 | 3.9479e-06 | 0.057425 | 0.057425 | 0.057425 | 0.99889 | -0.0077817 | 0.99861 | -0.0097315 | 21.2685
8 | -0.045053 | -0.011308 | 0.045102 | 0.011327 | 4.8732e-05 | 1.8516e-05 | 0.067121 | 0.067121 | 0.067121 | 0.99889 | -0.0077817 | 1 | 0 | 24.8595
9 | 0.036834 | 0.0092467 | -0.0368 | -0.0092342 | 3.3344e-05 | 1.2593e-05 | 0.054891 | 0.054891 | 0.054891 | 0.99861 | -0.0097315 | 0.99767 | -0.016255 | 20.33
10 | 0.048118 | 0.012084 | -0.048101 | -0.012078 | 1.6993e-05 | 6.4661e-06 | 0.071609 | 0.071609 | 0.071609 | 1 | 0 | 0.99964 | -0.0025416 | 26.5219
11 | 0.035058 | 0.0087975 | -0.035038 | -0.0087898 | 2.0232e-05 | 7.6267e-06 | 0.052292 | 0.052292 | 0.052292 | 0.99767 | -0.016255 | 0.99708 | -0.020415 | 19.3675
12 | 0.043207 | 0.010851 | -0.043194 | -0.010846 | 1.2996e-05 | 4.9325e-06 | 0.064323 | 0.064323 | 0.064323 | 0.99964 | -0.0025416 | 0.99933 | -0.004706 | 23.8235
13 | 0.0018427 | 0.0004614 | -0.0018425 | -0.00046178 | 1.604e-07 | -3.8162e-07 | 0.0027498 | 0.00275 | 0.00275 | 0.99708 | -0.020415 | 0.99699 | -0.021045 | 1.0185
14 | 0.033195 | 0.0083284 | -0.033177 | -0.0083216 | 1.8148e-05 | 6.8257e-06 | 0.049542 | 0.049542 | 0.049542 | 0.99708 | -0.020415 | 0.99652 | -0.024358 | 18.349
15 | 0.035679 | 0.0089627 | -0.035636 | -0.0089463 | 4.3591e-05 | 1.6442e-05 | 0.053135 | 0.053135 | 0.053135 | 0.99933 | -0.004706 | 0.99807 | -0.013502 | 19.6795
16 | 0.031521 | 0.0079066 | -0.031488 | -0.0078944 | 3.2439e-05 | 1.2171e-05 | 0.04707 | 0.04707 | 0.04707 | 0.99652 | -0.024358 | 0.99546 | -0.031787 | 17.4333
17 | 0.02918 | 0.0073284 | -0.029138 | -0.0073126 | 4.2351e-05 | 1.5821e-05 | 0.04351 | 0.043511 | 0.043511 | 0.99807 | -0.013502 | 0.99657 | -0.023957 | 16.115
18 | -0.0071832 | -0.0018003 | 0.0071843 | 0.0018005 | 1.1855e-06 | 2.4296e-07 | 0.010753 | 0.010753 | 0.010753 | 0.99398 | -0.042221 | 0.99415 | -0.041029 | 3.9827
19 | -0.0094019 | -0.0023563 | 0.0094027 | 0.0023565 | 8.2705e-07 | 2.3131e-07 | 0.014073 | 0.014073 | 0.014073 | 0.99415 | -0.041029 | 0.99424 | -0.040393 | 5.2121
20 | 0.028833 | 0.0072297 | -0.028817 | -0.0072239 | 1.5626e-05 | 5.8348e-06 | 0.043101 | 0.043101 | 0.043101 | 0.99546 | -0.031787 | 0.9949 | -0.0357 | 15.9632
21 | 0.0026555 | 0.0006647 | -0.0026552 | -0.000665 | 3.1736e-07 | -2.9755e-07 | 0.0039692 | 0.0039693 | 0.0039693 | 0.99546 | -0.031787 | 0.99534 | -0.032652 | 1.4701
22 | 0.0063596 | 0.0015938 | -0.0063591 | -0.0015937 | 5.392e-07 | 8.3368e-08 | 0.0095117 | 0.0095118 | 0.0095118 | 0.9949 | -0.0357 | 0.99482 | -0.036313 | 3.5229
23 | 0.022458 | 0.00563 | -0.022443 | -0.0056247 | 1.4589e-05 | 5.3424e-06 | 0.033589 | 0.033589 | 0.033589 | 0.9949 | -0.0357 | 0.99424 | -0.040393 | 12.4404
24 | 0.0026552 | 0.000665 | -0.0026548 | -0.00066536 | 3.8692e-07 | -3.626e-07 | 0.0039693 | 0.0039695 | 0.0039695 | 0.99534 | -0.032652 | 0.99519 | -0.033706 | 1.4702

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.09402 | 0.023411

## res_load
| p_mw | q_mvar
0 | 0.0075721 | 0.0018977
1 | 0.0051181 | 0.0012827
2 | 0.0035106 | 0.00087984
3 | 0.0017483 | 0.00043816
4 | 0.0097649 | 0.0024473
5 | 0.0013353 | 0.00033465
6 | 0.0065088 | 0.0016313
7 | 0.0017005 | 0.00042618
8 | 0.0017425 | 0.00043671
9 | 0.0048945 | 0.0012267
10 | 0.0075143 | 0.0018833
11 | 0.0018425 | 0.00046178
12 | 0.001656 | 0.00041503
13 | 0.0064553 | 0.0016179
14 | 0.0071832 | 0.0018003
15 | 0.0022176 | 0.00055578
16 | 0.0063591 | 0.0015937
17 | 0.01304 | 0.0032682
18 | 0.0026548 | 0.00066536

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1