## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1364-50_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1364-50_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1364-50_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1364-50_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1364-50_0_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_1364-50_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1364-50_0_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1364-50_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1364-50_0_3_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_1364-50_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1364-50_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1364-50_0_3_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_1364-50_0_3_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_1364-50_0_3_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_1364-50_0_3_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1364-50_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1364-50_0_3_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_1364-50_0_3_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1364-50_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1364-50_0_3_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1364-50_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1364-50_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1364-50_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1364-50_0_3_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_1364-50_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1364-50_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_1364-50_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1364-50_0_3_node_22 | 0.4 | n |  | TRUE
28 | bus_MV_133_0_node_120 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1364-50_0_3_load_0 | 0 | 0.009888 | 0.0024782 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1364-50_0_3_load_3 | 3 | 0.018324 | 0.0045925 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1364-50_0_3_load_9 | 4 | 0.013135 | 0.0032918 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1364-50_0_3_load_12 | 6 | 0.0098065 | 0.0024578 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1364-50_0_3_load_21 | 8 | 0.0013764 | 0.00034496 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1364-50_0_3_load_23 | 11 | 0.033858 | 0.0084856 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1364-50_0_3_load_20 | 12 | 0.0039012 | 0.00097772 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1364-50_0_3_load_31 | 13 | 0.006342 | 0.0015895 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1364-50_0_3_load_11 | 15 | 0.008703 | 0.0021812 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1364-50_0_3_load_24 | 16 | 0.016298 | 0.0040847 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1364-50_0_3_load_25 | 17 | 0.0085118 | 0.0021333 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1364-50_0_3_load_14 | 20 | 0.033139 | 0.0083055 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1364-50_0_3_load_13 | 21 | 0.013223 | 0.003314 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1364-50_0_3_load_30 | 23 | 0.0093527 | 0.002344 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1364-50_0_3_load_26 | 24 | 0.0074484 | 0.0018668 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1364-50_0_3_load_28 | 25 | 0.031701 | 0.007945 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1364-50_0_3_load_27 | 26 | 0.0071525 | 0.0017926 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1364-50_0_3_load_22 | 27 | 0.00065335 | 0.00016375 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1364-50_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.016051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1364-50_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.02937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1364-50_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0070843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1364-50_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.011946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1364-50_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.03342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1364-50_0_3_line_5 | NAYY 4x150 SE | 4 | 10 | 0.011382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1364-50_0_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.011017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1364-50_0_3_line_7 | NAYY 4x150 SE | 5 | 7 | 0.055882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1364-50_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.024494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1364-50_0_3_line_9 | NAYY 4x150 SE | 8 | 12 | 0.0035791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1364-50_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.00273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1364-50_0_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.010758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1364-50_0_3_line_12 | NAYY 4x150 SE | 10 | 15 | 0.029201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1364-50_0_3_line_13 | NAYY 4x150 SE | 12 | 27 | 0.039684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1364-50_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.012098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1364-50_0_3_line_15 | NAYY 4x150 SE | 14 | 23 | 0.031259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1364-50_0_3_line_16 | NAYY 4x150 SE | 14 | 22 | 0.037791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1364-50_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.00073852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1364-50_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.017829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1364-50_0_3_line_19 | NAYY 4x150 SE | 17 | 24 | 0.012845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1364-50_0_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.016074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1364-50_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.007045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1364-50_0_3_line_22 | NAYY 4x150 SE | 19 | 24 | 0.0048177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1364-50_0_3_line_23 | NAYY 4x150 SE | 19 | 25 | 0.0084754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1364-50_0_3_line_24 | NAYY 4x150 SE | 20 | 21 | 0.016815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1364-50_0_3_line_25 | NAYY 4x150 SE | 21 | 22 | 0.022974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1364-50_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0019478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1364-50_0_3_trafo_26 | 0.25 MVA 20/0.4 kV | 28 | 24 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2688826.8701 | 1205436.4389 | 2688822.2371 | 1205439.005 | 2688817.1314 | 1205439.5961 | 2688811.5169 | 1205439.6126
1 | 2688788.5339 | 1205450.9449 | 2688800.0069 | 1205445.2451 | 2688807.1864 | 1205442.8058 | 2688811.7576 | 1205443.8856 | 2688811.5169 | 1205439.6126
2 | 2688826.8701 | 1205436.4389 | 2688830.341 | 1205432.2211 | 2688831.8289 | 1205431.5752
3 | 2688788.5339 | 1205450.9449 | 2688785.3537 | 1205439.4305
4 | 2688864.4369 | 1205431.2165 | 2688858.0885 | 1205431.9892 | 2688842.8252 | 1205434.2303 | 2688836.3055 | 1205431.6872 | 2688832.7682 | 1205431.1676 | 2688831.8289 | 1205431.5752
5 | 2688782.7689 | 1205428.3555 | 2688783.8563 | 1205434.0088 | 2688785.3537 | 1205439.4305
6 | 2688864.4369 | 1205431.2165 | 2688865.0422 | 1205429.391 | 2688868.5627 | 1205424.9071 | 2688870.5963 | 1205422.1912
7 | 2688864.4369 | 1205431.2165 | 2688865.5187 | 1205433.1561 | 2688885.1121 | 1205440.5192 | 2688899.923 | 1205429.3212 | 2688908.9857 | 1205418.4379
8 | 2688908.9857 | 1205418.4379 | 2688925.806 | 1205400.6327
9 | 2688925.806 | 1205400.6327 | 2688928.2638 | 1205398.0309
10 | 2688782.7689 | 1205428.3555 | 2688782.6344 | 1205425.6295
11 | 2688782.6344 | 1205425.6295 | 2688781.573 | 1205414.9245
12 | 2688782.7689 | 1205428.3555 | 2688804.3191 | 1205422.3165 | 2688810.8734 | 1205420.4293
13 | 2688951.0286 | 1205366.2508 | 2688948.2934 | 1205370.9477 | 2688944.5638 | 1205380.7763 | 2688928.2638 | 1205398.0309
14 | 2688873.2265 | 1205339.5651 | 2688864.2605 | 1205344.9685 | 2688862.7853 | 1205345.6612
15 | 2688873.2265 | 1205339.5651 | 2688898.5452 | 1205321.2328
16 | 2688873.2265 | 1205339.5651 | 2688877.823 | 1205349.6734 | 2688879.0213 | 1205354.5167 | 2688884.0904 | 1205354.859 | 2688884.8427 | 1205361.5524 | 2688875.1809 | 1205363.621
17 | 2688810.8734 | 1205420.4293 | 2688811.5831 | 1205420.225
18 | 2688811.5831 | 1205420.225 | 2688823.8166 | 1205416.7027 | 2688827.9875 | 1205413.7704
19 | 2688837.5151 | 1205405.2502 | 2688832.4116 | 1205410.66 | 2688827.9875 | 1205413.7704
20 | 2688840.8211 | 1205401.7459 | 2688846.5547 | 1205397.306 | 2688853.6774 | 1205392.053
21 | 2688853.6774 | 1205392.053 | 2688858.9729 | 1205387.4065
22 | 2688840.8211 | 1205401.7459 | 2688837.5151 | 1205405.2502
23 | 2688840.8211 | 1205401.7459 | 2688833.1541 | 1205398.1335
24 | 2688858.9729 | 1205387.4065 | 2688863.5953 | 1205386.5748 | 2688875.7137 | 1205386.5885
25 | 2688875.1809 | 1205363.621 | 2688875.7137 | 1205386.5885
26 | 2688831.3921 | 1205397.3033 | 2688833.1541 | 1205398.1335

## bus_geodata
| x | y | coords
0 | 2688811.5169 | 1205439.6126
1 | 2688826.8701 | 1205436.4389
2 | 2688788.5339 | 1205450.9449
3 | 2688831.8289 | 1205431.5753
4 | 2688785.3537 | 1205439.4305
5 | 2688864.4369 | 1205431.2165
6 | 2688870.5963 | 1205422.1912
7 | 2688908.9858 | 1205418.4379
8 | 2688925.806 | 1205400.6327
9 | 2688782.6344 | 1205425.6295
10 | 2688782.7689 | 1205428.3555
11 | 2688781.573 | 1205414.9245
12 | 2688928.2638 | 1205398.0309
13 | 2688862.7853 | 1205345.6612
14 | 2688873.2265 | 1205339.5651
15 | 2688810.8734 | 1205420.4293
16 | 2688811.5831 | 1205420.225
17 | 2688827.9875 | 1205413.7704
18 | 2688853.6774 | 1205392.053
19 | 2688840.8211 | 1205401.7459
20 | 2688858.9729 | 1205387.4065
21 | 2688875.7137 | 1205386.5885
22 | 2688875.1809 | 1205363.621
23 | 2688898.5452 | 1205321.2328
24 | 2688837.5151 | 1205405.2502
25 | 2688833.1541 | 1205398.1335
26 | 2688831.3921 | 1205397.3033
27 | 2688951.0286 | 1205366.2508
28 | 2688837.5151 | 1205405.2502

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98989 | -0.070878 | 0.009888 | 0.0024782
1 | 0.9891 | -0.076454 | 0 | 0
2 | 0.99175 | -0.057749 | 0 | 0
3 | 0.98875 | -0.078917 | 0.018324 | 0.0045925
4 | 0.9925 | -0.052423 | 0.013135 | 0.0032918
5 | 0.98799 | -0.084295 | 0 | 0
6 | 0.98784 | -0.0854 | 0.0098065 | 0.0024578
7 | 0.98751 | -0.087691 | 0 | 0
8 | 0.9873 | -0.089179 | 0.0013764 | 0.00034496
9 | 0.99331 | -0.046779 | 0 | 0
10 | 0.99344 | -0.045844 | 0 | 0
11 | 0.99278 | -0.050466 | 0.033858 | 0.0084856
12 | 0.98728 | -0.089347 | 0.0039012 | 0.00097772
13 | 0.99508 | -0.034487 | 0.006342 | 0.0015895
14 | 0.99519 | -0.033714 | 0 | 0
15 | 0.99726 | -0.019085 | 0.008703 | 0.0021812
16 | 0.99737 | -0.018346 | 0.016298 | 0.0040847
17 | 0.99885 | -0.0079888 | 0.0085118 | 0.0021333
18 | 0.99788 | -0.014842 | 0 | 0
19 | 0.99931 | -0.0048561 | 0 | 0
20 | 0.99725 | -0.019227 | 0.033139 | 0.0083055
21 | 0.99656 | -0.024112 | 0.013223 | 0.003314
22 | 0.99604 | -0.02774 | 0 | 0
23 | 0.99477 | -0.036661 | 0.0093527 | 0.002344
24 | 1 | 0 | -0.22732 | -0.05692
25 | 0.99884 | -0.0081488 | 0.031701 | 0.007945
26 | 0.99882 | -0.0082881 | 0.0071525 | 0.0017926
27 | 0.98724 | -0.089613 | 0.00065335 | 0.00016375
28 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.034117 | 0.0085555 | -0.034091 | -0.0085456 | 2.6345e-05 | 9.9265e-06 | 0.051287 | 0.051287 | 0.051287 | 0.98989 | -0.070878 | 0.9891 | -0.076454 | 18.9954
1 | -0.044005 | -0.011034 | 0.044085 | 0.011064 | 8.0199e-05 | 3.0467e-05 | 0.066151 | 0.066151 | 0.066151 | 0.98989 | -0.070878 | 0.99175 | -0.057749 | 24.5005
2 | 0.034091 | 0.0085456 | -0.034079 | -0.0085412 | 1.1628e-05 | 4.3814e-06 | 0.051287 | 0.051287 | 0.051287 | 0.9891 | -0.076454 | 0.98875 | -0.078917 | 18.9954
3 | -0.044085 | -0.011064 | 0.044118 | 0.011077 | 3.2619e-05 | 1.2391e-05 | 0.066151 | 0.066151 | 0.066151 | 0.99175 | -0.057749 | 0.9925 | -0.052423 | 24.5004
4 | 0.015755 | 0.0039487 | -0.015743 | -0.0039446 | 1.1724e-05 | 4.0808e-06 | 0.02371 | 0.02371 | 0.02371 | 0.98875 | -0.078917 | 0.98799 | -0.084295 | 8.7816
5 | -0.057253 | -0.014368 | 0.057305 | 0.014388 | 5.2335e-05 | 1.9982e-05 | 0.085843 | 0.085843 | 0.085843 | 0.9925 | -0.052423 | 0.99344 | -0.045844 | 31.7937
6 | 0.009808 | 0.0024582 | -0.0098065 | -0.0024578 | 1.5001e-06 | 4.359e-07 | 0.014772 | 0.014772 | 0.014772 | 0.98799 | -0.084295 | 0.98784 | -0.0854 | 5.4711
7 | 0.0059351 | 0.0014864 | -0.0059323 | -0.0014861 | 2.7861e-06 | 3.5629e-07 | 0.0089385 | 0.0089387 | 0.0089387 | 0.98799 | -0.084295 | 0.98751 | -0.087691 | 3.3106
8 | 0.0059323 | 0.0014861 | -0.0059311 | -0.0014859 | 1.2212e-06 | 1.564e-07 | 0.0089387 | 0.0089388 | 0.0089388 | 0.98751 | -0.087691 | 0.9873 | -0.089179 | 3.3107
9 | 0.0045546 | 0.001141 | -0.0045545 | -0.001141 | 1.0523e-07 | -5.2946e-09 | 0.0068643 | 0.0068644 | 0.0068644 | 0.9873 | -0.089179 | 0.98728 | -0.089347 | 2.5424
10 | -0.033875 | -0.0084921 | 0.03388 | 0.0084938 | 4.3871e-06 | 1.652e-06 | 0.050747 | 0.050747 | 0.050747 | 0.99331 | -0.046779 | 0.99344 | -0.045844 | 18.7954
11 | 0.033875 | 0.0084921 | -0.033858 | -0.0084856 | 1.7287e-05 | 6.5098e-06 | 0.050747 | 0.050748 | 0.050748 | 0.99331 | -0.046779 | 0.99278 | -0.050466 | 18.7954
12 | -0.091185 | -0.022882 | 0.091525 | 0.023013 | 0.00033996 | 0.00013037 | 0.13659 | 0.13659 | 0.13659 | 0.99344 | -0.045844 | 0.99726 | -0.019085 | 50.589
13 | 0.00065338 | 0.00016325 | -0.00065335 | -0.00016375 | 2.401e-08 | -4.9821e-07 | 0.00098459 | 0.00098477 | 0.00098477 | 0.98728 | -0.089347 | 0.98724 | -0.089613 | 0.36473
14 | -0.006342 | -0.0015895 | 0.0063427 | 0.0015896 | 6.7897e-07 | 1.0396e-07 | 0.0094837 | 0.0094836 | 0.0094837 | 0.99508 | -0.034487 | 0.99519 | -0.033714 | 3.5125
15 | 0.0093566 | 0.0023451 | -0.0093527 | -0.002344 | 3.8177e-06 | 1.0623e-06 | 0.01399 | 0.01399 | 0.01399 | 0.99519 | -0.033714 | 0.99477 | -0.036661 | 5.1815
16 | -0.015699 | -0.0039346 | 0.015712 | 0.0039391 | 1.2993e-05 | 4.506e-06 | 0.023474 | 0.023473 | 0.023474 | 0.99519 | -0.033714 | 0.99604 | -0.02774 | 8.6939
17 | -0.10023 | -0.025194 | 0.10024 | 0.025198 | 1.031e-05 | 3.9559e-06 | 0.14958 | 0.14958 | 0.14958 | 0.99726 | -0.019085 | 0.99737 | -0.018346 | 55.3986
18 | -0.11654 | -0.029282 | 0.1167 | 0.029347 | 0.00016821 | 6.4228e-05 | 0.17389 | 0.17389 | 0.17389 | 0.99737 | -0.018346 | 0.99885 | -0.0079888 | 32.2022
19 | -0.12522 | -0.03148 | 0.12536 | 0.031533 | 0.00013951 | 5.3319e-05 | 0.18657 | 0.18657 | 0.18657 | 0.99885 | -0.0079888 | 1 | 0 | 34.5504
20 | -0.06214 | -0.015583 | 0.062226 | 0.015616 | 8.6127e-05 | 3.2915e-05 | 0.092665 | 0.092665 | 0.092665 | 0.99788 | -0.014842 | 0.99931 | -0.0048561 | 34.3204
21 | 0.06214 | 0.015583 | -0.062102 | -0.015569 | 3.7748e-05 | 1.4427e-05 | 0.092665 | 0.092665 | 0.092665 | 0.99788 | -0.014842 | 0.99725 | -0.019227 | 34.3204
22 | -0.1011 | -0.02536 | 0.10117 | 0.025387 | 6.8135e-05 | 2.6142e-05 | 0.15055 | 0.15055 | 0.15055 | 0.99931 | -0.0048561 | 1 | 0 | 55.7582
23 | 0.038871 | 0.0097443 | -0.038854 | -0.0097376 | 1.7719e-05 | 6.704e-06 | 0.057882 | 0.057882 | 0.057882 | 0.99931 | -0.0048561 | 0.99884 | -0.0081488 | 21.4379
24 | 0.028963 | 0.0072632 | -0.028943 | -0.0072559 | 1.9597e-05 | 7.3182e-06 | 0.043217 | 0.043217 | 0.043217 | 0.99725 | -0.019227 | 0.99656 | -0.024112 | 16.0064
25 | 0.01572 | 0.0039419 | -0.015712 | -0.0039391 | 7.8989e-06 | 2.7389e-06 | 0.023473 | 0.023473 | 0.023473 | 0.99656 | -0.024112 | 0.99604 | -0.02774 | 8.6939
26 | 0.0071526 | 0.0017926 | -0.0071525 | -0.0017926 | 1.38e-07 | 2.7583e-08 | 0.010656 | 0.010656 | 0.010656 | 0.99884 | -0.0081488 | 0.99882 | -0.0082881 | 3.9465

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23477 | 0.058787

## res_load
| p_mw | q_mvar
0 | 0.009888 | 0.0024782
1 | 0.018324 | 0.0045925
2 | 0.013135 | 0.0032918
3 | 0.0098065 | 0.0024578
4 | 0.0013764 | 0.00034496
5 | 0.033858 | 0.0084856
6 | 0.0039012 | 0.00097772
7 | 0.006342 | 0.0015895
8 | 0.008703 | 0.0021812
9 | 0.016298 | 0.0040847
10 | 0.0085118 | 0.0021333
11 | 0.033139 | 0.0083055
12 | 0.013223 | 0.003314
13 | 0.0093527 | 0.002344
14 | 0.0074484 | 0.0018668
15 | 0.031701 | 0.007945
16 | 0.0071525 | 0.0017926
17 | 0.00065335 | 0.00016375

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1