## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1364-54_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1364-54_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1364-54_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1364-54_0_3_node_25 | 0.4 | n |  | TRUE
4 | bus_LV_1364-54_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1364-54_0_3_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_1364-54_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1364-54_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1364-54_0_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1364-54_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1364-54_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1364-54_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1364-54_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1364-54_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1364-54_0_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1364-54_0_3_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_1364-54_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1364-54_0_3_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1364-54_0_3_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1364-54_0_3_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1364-54_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1364-54_0_3_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1364-54_0_3_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1364-54_0_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1364-54_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1364-54_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1364-54_0_3_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1364-54_0_3_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1364-54_0_3_node_23 | 0.4 | n |  | TRUE
29 | bus_MV_133_0_node_122 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1364-54_0_3_load_0 | 0 | 0.0015782 | 0.00039552 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1364-54_0_3_load_25 | 3 | 0.00087888 | 0.00022027 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1364-54_0_3_load_3 | 4 | 0.0015544 | 0.00038957 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1364-54_0_3_load_9 | 8 | 0.00057468 | 0.00014403 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1364-54_0_3_load_6 | 9 | 0.0026101 | 0.00065416 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1364-54_0_3_load_10 | 10 | 0.0013232 | 0.00033163 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1364-54_0_3_load_7 | 12 | 0.0012392 | 0.00031057 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1364-54_0_3_load_13 | 13 | 0.0016784 | 0.00042064 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1364-54_0_3_load_30 | 14 | 0.081935 | 0.020535 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1364-54_0_3_load_26 | 15 | 0.0019773 | 0.00049555 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1364-54_0_3_load_19 | 18 | 0.0024789 | 0.00062127 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1364-54_0_3_load_29 | 19 | 0.052848 | 0.013245 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1364-54_0_3_load_27 | 21 | 0.0016413 | 0.00041135 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1364-54_0_3_load_21 | 22 | 0.0017408 | 0.0004363 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1364-54_0_3_load_18 | 23 | 0.0026522 | 0.00066471 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1364-54_0_3_load_15 | 24 | 0.061281 | 0.015358 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1364-54_0_3_load_28 | 26 | 0.0021533 | 0.00053967 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1364-54_0_3_load_22 | 27 | 0.0011658 | 0.00029218 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1364-54_0_3_load_23 | 28 | 0.0022773 | 0.00057074 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1364-54_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0079447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1364-54_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.064877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1364-54_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.13574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1364-54_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.044167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1364-54_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.016651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1364-54_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.020509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1364-54_0_3_line_6 | NAYY 4x150 SE | 5 | 28 | 0.051744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1364-54_0_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.006062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1364-54_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.068958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1364-54_0_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.039585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1364-54_0_3_line_10 | NAYY 4x150 SE | 9 | 12 | 0.0018306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1364-54_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.086651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1364-54_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.028492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1364-54_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.12486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1364-54_0_3_line_14 | NAYY 4x150 SE | 13 | 15 | 0.0074667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1364-54_0_3_line_15 | NAYY 4x150 SE | 14 | 19 | 0.036766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1364-54_0_3_line_16 | NAYY 4x150 SE | 14 | 20 | 0.043862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1364-54_0_3_line_17 | NAYY 4x150 SE | 15 | 21 | 0.020919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1364-54_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.00349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1364-54_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.034309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1364-54_0_3_line_20 | NAYY 4x150 SE | 16 | 19 | 0.10563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1364-54_0_3_line_21 | NAYY 4x150 SE | 17 | 22 | 0.021031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1364-54_0_3_line_22 | NAYY 4x150 SE | 18 | 23 | 0.018319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1364-54_0_3_line_23 | NAYY 4x150 SE | 20 | 25 | 0.012258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1364-54_0_3_line_24 | NAYY 4x150 SE | 21 | 26 | 0.0055542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1364-54_0_3_line_25 | NAYY 4x150 SE | 22 | 27 | 0.005807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1364-54_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.093306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1364-54_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.017414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1364-54_0_3_trafo_29 | 0.25 MVA 20/0.4 kV | 29 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2687571.3609 | 1206469.8156 | 2687578.4322 | 1206473.437
1 | 2687622.7348 | 1206517.2559 | 2687619.0433 | 1206505.0048 | 2687609.9028 | 1206497.11 | 2687604.6496 | 1206489.6836 | 2687588.9732 | 1206478.8354 | 2687578.4322 | 1206473.437
2 | 2687618.3571 | 1206342.4663 | 2687571.3609 | 1206469.8156
3 | 2687622.7348 | 1206517.2559 | 2687594.9375 | 1206513.4678 | 2687583.6552 | 1206516.2485 | 2687579.6195 | 1206518.2237
4 | 2687611.445 | 1206327.3105 | 2687618.3571 | 1206342.4663
5 | 2687560.4621 | 1206525.2365 | 2687570.5319 | 1206522.6713 | 2687579.6195 | 1206518.2237
6 | 2687611.445 | 1206327.3105 | 2687577.6094 | 1206297.4835 | 2687571.382 | 1206295.1833
7 | 2687560.4621 | 1206525.2365 | 2687562.0982 | 1206527.2507 | 2687565.3744 | 1206528.4217
8 | 2687565.3744 | 1206528.4217 | 2687580.6207 | 1206530.7357 | 2687603.3071 | 1206540.1969 | 2687610.5773 | 1206545.4515 | 2687614.5913 | 1206553.3488 | 2687617.3512 | 1206561.7059 | 2687617.6197 | 1206564.1448
9 | 2687565.3744 | 1206528.4217 | 2687569.175 | 1206532.2132 | 2687573.7984 | 1206533.3151 | 2687577.6502 | 1206534.6502 | 2687582.1189 | 1206537.4843 | 2687585.2788 | 1206539.8433 | 2687588.356 | 1206543.1684 | 2687591.3984 | 1206546.2706 | 2687594.322 | 1206552.9343
10 | 2687594.322 | 1206552.9343 | 2687595.0575 | 1206554.6107
11 | 2687486.2523 | 1206308.307 | 2687492.3637 | 1206309.097 | 2687489.3749 | 1206340.7183 | 2687483.8284 | 1206347.0523 | 2687470.5269 | 1206357.3197 | 2687457.0912 | 1206366.8847 | 2687450.9543 | 1206370.2747
12 | 2687486.2523 | 1206308.307 | 2687486.5547 | 1206310.5128 | 2687486.1942 | 1206313.3094 | 2687485.0385 | 1206315.8719 | 2687483.1894 | 1206318.0018 | 2687480.8018 | 1206319.5122 | 2687471.3709 | 1206322.576 | 2687466.3461 | 1206323.2755
13 | 2687486.2523 | 1206308.307 | 2687431.3476 | 1206196.1673
14 | 2687458.9507 | 1206324.3049 | 2687466.3461 | 1206323.2755
15 | 2687467.8118 | 1206191.464 | 2687465.9034 | 1206191.7105 | 2687431.3476 | 1206196.1673
16 | 2687387.8445 | 1206201.7631 | 2687429.1334 | 1206196.4529 | 2687431.3476 | 1206196.1673
17 | 2687458.9507 | 1206324.3049 | 2687440.2971 | 1206326.9015 | 2687438.2228 | 1206326.6898
18 | 2687528.5862 | 1206277.863 | 2687528.6441 | 1206279.6206 | 2687529.6886 | 1206281.0035
19 | 2687528.5862 | 1206277.863 | 2687529.2571 | 1206276.7166 | 2687531.4826 | 1206275.8931 | 2687535.3555 | 1206275.2828 | 2687545.3457 | 1206272.9944 | 2687557.0316 | 1206271.2535 | 2687561.6366 | 1206271.6642
20 | 2687528.5862 | 1206277.863 | 2687467.8118 | 1206191.464
21 | 2687529.6886 | 1206281.0035 | 2687531.6133 | 1206282.0212 | 2687545.2133 | 1206284.6112 | 2687549.8257 | 1206286.5657
22 | 2687579.8476 | 1206272.8355 | 2687578.5215 | 1206273.1699 | 2687561.6366 | 1206271.6642
23 | 2687384.6024 | 1206191.4978 | 2687386.226 | 1206191.2659 | 2687387.8445 | 1206201.7631
24 | 2687432.6973 | 1206326.1257 | 2687438.2228 | 1206326.6898
25 | 2687555.1725 | 1206288.8315 | 2687549.8257 | 1206286.5657
26 | 2687384.6024 | 1206191.4978 | 2687383.9045 | 1206184.6165 | 2687381.4717 | 1206182.4572 | 2687377.9677 | 1206180.727 | 2687375.0746 | 1206177.2713 | 2687375.4361 | 1206173.363 | 2687378.5426 | 1206170.551 | 2687384.8733 | 1206168.8426 | 2687389.8842 | 1206167.4038 | 2687393.0509 | 1206166.7164 | 2687396.479 | 1206165.3212 | 2687400.15 | 1206162.9178 | 2687402.7099 | 1206159.5197 | 2687404.7425 | 1206156.8033 | 2687408.595 | 1206154.4804 | 2687414.0914 | 1206152.6041 | 2687420.7107 | 1206151.9672 | 2687425.3425 | 1206153.0357 | 2687430.5073 | 1206156.1467 | 2687433.7257 | 1206158.1618 | 2687437.9327 | 1206159.1574
27 | 2687555.1725 | 1206288.8315 | 2687561.8738 | 1206291.6712 | 2687571.382 | 1206295.1833

## bus_geodata
| x | y | coords
0 | 2687578.4322 | 1206473.437
1 | 2687571.3609 | 1206469.8156
2 | 2687622.7348 | 1206517.2559
3 | 2687618.3571 | 1206342.4663
4 | 2687579.6195 | 1206518.2237
5 | 2687611.445 | 1206327.3105
6 | 2687560.4621 | 1206525.2365
7 | 2687565.3744 | 1206528.4217
8 | 2687617.6197 | 1206564.1448
9 | 2687594.322 | 1206552.9344
10 | 2687450.9543 | 1206370.2747
11 | 2687486.2523 | 1206308.307
12 | 2687595.0575 | 1206554.6107
13 | 2687466.3461 | 1206323.2755
14 | 2687431.3476 | 1206196.1673
15 | 2687458.9507 | 1206324.3049
16 | 2687528.5862 | 1206277.863
17 | 2687529.6886 | 1206281.0035
18 | 2687561.6366 | 1206271.6642
19 | 2687467.8118 | 1206191.464
20 | 2687387.8445 | 1206201.7631
21 | 2687438.2227 | 1206326.6898
22 | 2687549.8257 | 1206286.5657
23 | 2687579.8476 | 1206272.8355
24 | 2687437.9327 | 1206159.1574
25 | 2687384.6024 | 1206191.4978
26 | 2687432.6973 | 1206326.1257
27 | 2687555.1725 | 1206288.8315
28 | 2687571.382 | 1206295.1833
29 | 2687387.8445 | 1206201.7631

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99393 | -0.042661 | 0.0015782 | 0.00039552
1 | 0.99402 | -0.042053 | 0 | 0
2 | 0.99338 | -0.046595 | 0 | 0
3 | 0.99549 | -0.031665 | 0.00087888 | 0.00022027
4 | 0.993 | -0.049274 | 0.0015544 | 0.00038957
5 | 0.99569 | -0.030244 | 0 | 0
6 | 0.99287 | -0.050195 | 0 | 0
7 | 0.99283 | -0.050467 | 0 | 0
8 | 0.99277 | -0.05087 | 0.00057468 | 0.00014403
9 | 0.99261 | -0.052011 | 0.0026101 | 0.00065416
10 | 0.99424 | -0.040232 | 0.0013232 | 0.00033163
11 | 0.99441 | -0.039071 | 0 | 0
12 | 0.99261 | -0.052034 | 0.0012392 | 0.00031057
13 | 0.9941 | -0.041215 | 0.0016784 | 0.00042064
14 | 0.99598 | -0.028006 | 0.081935 | 0.020535
15 | 0.99404 | -0.041651 | 0.0019773 | 0.00049555
16 | 0.99716 | -0.019887 | 0 | 0
17 | 0.9971 | -0.020365 | 0 | 0
18 | 0.99691 | -0.021655 | 0.0024789 | 0.00062127
19 | 1 | 0 | -0.17305 | -0.043356
20 | 0.99208 | -0.055161 | 0 | 0
21 | 0.99393 | -0.042453 | 0.0016413 | 0.00041135
22 | 0.99668 | -0.023252 | 0.0017408 | 0.0004363
23 | 0.99684 | -0.022143 | 0.0026522 | 0.00066471
24 | 0.9827 | -0.12139 | 0.061281 | 0.015358
25 | 0.99099 | -0.062787 | 0 | 0
26 | 0.99391 | -0.042574 | 0.0021533 | 0.00053967
27 | 0.99659 | -0.023948 | 0.0011658 | 0.00029218
28 | 0.99632 | -0.025831 | 0.0022773 | 0.00057074
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0075636 | -0.0018934 | 0.0075642 | 0.0018935 | 6.3556e-07 | 1.4147e-07 | 0.011323 | 0.011323 | 0.011323 | 0.99393 | -0.042661 | 0.99402 | -0.042053 | 4.1936
1 | 0.0059854 | 0.0014979 | -0.0059822 | -0.0014974 | 3.2502e-06 | 4.097e-07 | 0.00896 | 0.0089603 | 0.0089603 | 0.99393 | -0.042661 | 0.99338 | -0.046595 | 3.3186
2 | -0.0075642 | -0.0018935 | 0.0075751 | 0.0018959 | 1.0859e-05 | 2.4142e-06 | 0.011323 | 0.011322 | 0.011323 | 0.99402 | -0.042053 | 0.99549 | -0.031665 | 4.1936
3 | 0.0059822 | 0.0014974 | -0.00598 | -0.0014972 | 2.2128e-06 | 2.795e-07 | 0.0089603 | 0.0089605 | 0.0089605 | 0.99338 | -0.046595 | 0.993 | -0.049274 | 3.3187
4 | -0.008454 | -0.0021162 | 0.0084556 | 0.0021166 | 1.6589e-06 | 4.2152e-07 | 0.012636 | 0.012636 | 0.012636 | 0.99549 | -0.031665 | 0.99569 | -0.030244 | 4.6799
5 | 0.0044256 | 0.0011076 | -0.004425 | -0.0011076 | 5.6276e-07 | -4.8829e-08 | 0.0066312 | 0.0066313 | 0.0066313 | 0.993 | -0.049274 | 0.99287 | -0.050195 | 2.456
6 | -0.0084556 | -0.0021166 | 0.0084608 | 0.0021179 | 5.155e-06 | 1.3093e-06 | 0.012636 | 0.012635 | 0.012636 | 0.99569 | -0.030244 | 0.99632 | -0.025831 | 4.6799
7 | 0.004425 | 0.0011076 | -0.0044248 | -0.0011077 | 1.6634e-07 | -1.4418e-08 | 0.0066313 | 0.0066313 | 0.0066313 | 0.99287 | -0.050195 | 0.99283 | -0.050467 | 2.456
8 | 0.00057472 | 0.00014315 | -0.00057468 | -0.00014403 | 3.1914e-08 | -8.7942e-07 | 0.00086105 | 0.00086137 | 0.00086137 | 0.99283 | -0.050467 | 0.99277 | -0.05087 | 0.31902
9 | 0.0038501 | 0.00096451 | -0.0038493 | -0.0009647 | 8.2248e-07 | -1.9546e-07 | 0.0057703 | 0.0057705 | 0.0057705 | 0.99283 | -0.050467 | 0.99261 | -0.052011 | 2.1372
10 | 0.0012392 | 0.00031055 | -0.0012392 | -0.00031057 | 3.942e-09 | -2.2147e-08 | 0.0018577 | 0.0018577 | 0.0018577 | 0.99261 | -0.052011 | 0.99261 | -0.052034 | 0.68802
11 | -0.0013232 | -0.00033163 | 0.0013234 | 0.00033059 | 2.1201e-07 | -1.0424e-06 | 0.0019804 | 0.00198 | 0.0019804 | 0.99424 | -0.040232 | 0.99441 | -0.039071 | 0.73347
12 | 0.0074533 | 0.0018676 | -0.0074511 | -0.0018671 | 2.2115e-06 | 4.8106e-07 | 0.011153 | 0.011153 | 0.011153 | 0.99441 | -0.039071 | 0.9941 | -0.041215 | 4.1307
13 | -0.0087767 | -0.0021981 | 0.0087901 | 0.0022017 | 1.3437e-05 | 3.5457e-06 | 0.013133 | 0.013132 | 0.013133 | 0.99441 | -0.039071 | 0.99598 | -0.028006 | 4.864
14 | 0.0057727 | 0.0014464 | -0.0057723 | -0.0014464 | 3.4786e-07 | 3.6993e-08 | 0.0086406 | 0.0086407 | 0.0086407 | 0.9941 | -0.041215 | 0.99404 | -0.041651 | 3.2003
15 | -0.15281 | -0.038402 | 0.15341 | 0.038631 | 0.00059807 | 0.00022907 | 0.22834 | 0.22834 | 0.22834 | 0.99598 | -0.028006 | 1 | 0 | 42.2846
16 | 0.062084 | 0.015665 | -0.061848 | -0.015575 | 0.00023566 | 9.0071e-05 | 0.092792 | 0.092792 | 0.092792 | 0.99598 | -0.028006 | 0.99208 | -0.055161 | 34.3675
17 | 0.003795 | 0.00095085 | -0.0037946 | -0.00095096 | 4.2126e-07 | -1.0912e-07 | 0.0056808 | 0.0056809 | 0.0056809 | 0.99404 | -0.041651 | 0.99393 | -0.042453 | 2.104
18 | 0.013655 | 0.0034205 | -0.013654 | -0.0034202 | 9.0417e-07 | 3.0223e-07 | 0.020376 | 0.020376 | 0.020376 | 0.99716 | -0.019887 | 0.9971 | -0.020365 | 7.5467
19 | 0.0051326 | 0.0012858 | -0.0051313 | -0.0012858 | 1.2558e-06 | 3.5566e-08 | 0.0076589 | 0.007659 | 0.007659 | 0.99716 | -0.019887 | 0.99691 | -0.021655 | 2.8367
20 | -0.018788 | -0.0047063 | 0.018839 | 0.0047249 | 5.1805e-05 | 1.8543e-05 | 0.028035 | 0.028034 | 0.028035 | 0.99716 | -0.019887 | 1 | 0 | 10.3833
21 | 0.013654 | 0.0034202 | -0.013649 | -0.0034184 | 5.4487e-06 | 1.8214e-06 | 0.020376 | 0.020376 | 0.020376 | 0.9971 | -0.020365 | 0.99668 | -0.023252 | 7.5467
22 | 0.0026524 | 0.00066454 | -0.0026522 | -0.00066471 | 1.7917e-07 | -1.6993e-07 | 0.003959 | 0.0039591 | 0.0039591 | 0.99691 | -0.021655 | 0.99684 | -0.022143 | 1.4663
23 | 0.061848 | 0.015575 | -0.061782 | -0.01555 | 6.5861e-05 | 2.5173e-05 | 0.092792 | 0.092792 | 0.092792 | 0.99208 | -0.055161 | 0.99099 | -0.062787 | 34.3675
24 | 0.0021533 | 0.00053961 | -0.0021533 | -0.00053967 | 3.6019e-08 | -5.813e-08 | 0.0032237 | 0.0032238 | 0.0032238 | 0.99393 | -0.042453 | 0.99391 | -0.042574 | 1.194
25 | 0.011908 | 0.0029821 | -0.011907 | -0.0029817 | 1.1451e-06 | 3.6477e-07 | 0.017777 | 0.017777 | 0.017777 | 0.99668 | -0.023252 | 0.99659 | -0.023948 | 6.5841
26 | -0.061281 | -0.015358 | 0.061782 | 0.01555 | 0.00050132 | 0.00019162 | 0.092793 | 0.092792 | 0.092793 | 0.9827 | -0.12139 | 0.99099 | -0.062787 | 34.3676
27 | 0.010741 | 0.0026895 | -0.010738 | -0.0026887 | 2.7945e-06 | 8.4798e-07 | 0.016036 | 0.016037 | 0.016037 | 0.99659 | -0.023948 | 0.99632 | -0.025831 | 5.9395

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22589 | 0.056601

## res_load
| p_mw | q_mvar
0 | 0.0015782 | 0.00039552
1 | 0.00087888 | 0.00022027
2 | 0.0015544 | 0.00038957
3 | 0.00057468 | 0.00014403
4 | 0.0026101 | 0.00065416
5 | 0.0013232 | 0.00033163
6 | 0.0012392 | 0.00031057
7 | 0.0016784 | 0.00042064
8 | 0.081935 | 0.020535
9 | 0.0019773 | 0.00049555
10 | 0.0024789 | 0.00062127
11 | 0.052848 | 0.013245
12 | 0.0016413 | 0.00041135
13 | 0.0017408 | 0.0004363
14 | 0.0026522 | 0.00066471
15 | 0.061281 | 0.015358
16 | 0.0021533 | 0.00053967
17 | 0.0011658 | 0.00029218
18 | 0.0022773 | 0.00057074

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1