## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1365-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1365-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1365-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1365-5_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1365-5_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1365-5_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1365-5_0_3_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_1365-5_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1365-5_0_3_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_1365-5_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1365-5_0_3_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1365-5_0_3_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1365-5_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1365-5_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1365-5_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1365-5_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1365-5_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1365-5_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1365-5_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1365-5_0_3_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1365-5_0_3_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1365-5_0_3_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1365-5_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1365-5_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1365-5_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1365-5_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1365-5_0_3_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_1365-5_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1365-5_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1365-5_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1365-5_0_3_node_32 | 0.4 | n |  | TRUE
31 | bus_MV_127_0_node_52 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1365-5_0_3_load_0 | 0 | 0.022785 | 0.0057103 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1365-5_0_3_load_1 | 1 | 0.001863 | 0.0004669 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1365-5_0_3_load_4 | 4 | 0.0037705 | 0.00094498 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1365-5_0_3_load_6 | 5 | 0.0008127 | 0.00020368 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1365-5_0_3_load_31 | 6 | 0.027343 | 0.0068529 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1365-5_0_3_load_5 | 7 | 0.069366 | 0.017385 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1365-5_0_3_load_30 | 10 | 0.030804 | 0.0077202 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1365-5_0_3_load_33 | 11 | 0.015986 | 0.0040065 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1365-5_0_3_load_8 | 12 | 0.0029129 | 0.00073003 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1365-5_0_3_load_9 | 13 | 0.00078393 | 0.00019647 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1365-5_0_3_load_11 | 14 | 0.00099523 | 0.00024943 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1365-5_0_3_load_12 | 15 | 0.0022183 | 0.00055595 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1365-5_0_3_load_13 | 16 | 0.0023513 | 0.00058928 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1365-5_0_3_load_14 | 17 | 0.0022921 | 0.00057446 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1365-5_0_3_load_15 | 18 | 0.0018913 | 0.000474 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1365-5_0_3_load_29 | 19 | 0.002829 | 0.00070902 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1365-5_0_3_load_28 | 20 | 0.0016735 | 0.00041941 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1365-5_0_3_load_20 | 21 | 0.0030919 | 0.00077491 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1365-5_0_3_load_18 | 22 | 0.0029958 | 0.00075083 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1365-5_0_3_load_21 | 23 | 0.0020802 | 0.00052135 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1365-5_0_3_load_16 | 24 | 0.0065865 | 0.0016507 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1365-5_0_3_load_22 | 25 | 0.0018474 | 0.000463 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1365-5_0_3_load_24 | 26 | 0.0024722 | 0.00061959 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1365-5_0_3_load_26 | 28 | 0.0025554 | 0.00064043 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1365-5_0_3_load_27 | 29 | 0.002451 | 0.00061429 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1365-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.073057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1365-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.083205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1365-5_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.019824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1365-5_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.017036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1365-5_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.1159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1365-5_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.012262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1365-5_0_3_line_6 | NAYY 4x150 SE | 5 | 9 | 0.1267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1365-5_0_3_line_7 | NAYY 4x150 SE | 6 | 10 | 0.01463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1365-5_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.021944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1365-5_0_3_line_9 | NAYY 4x150 SE | 8 | 11 | 0.022241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1365-5_0_3_line_10 | NAYY 4x150 SE | 9 | 12 | 0.064647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1365-5_0_3_line_11 | NAYY 4x150 SE | 10 | 30 | 0.017621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1365-5_0_3_line_12 | NAYY 4x150 SE | 11 | 30 | 0.0068578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1365-5_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.018728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1365-5_0_3_line_14 | NAYY 4x150 SE | 14 | 15 | 0.015382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1365-5_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.022838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1365-5_0_3_line_16 | NAYY 4x150 SE | 15 | 17 | 0.032182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1365-5_0_3_line_17 | NAYY 4x150 SE | 16 | 18 | 0.0075858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1365-5_0_3_line_18 | NAYY 4x150 SE | 16 | 19 | 0.071524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1365-5_0_3_line_19 | NAYY 4x150 SE | 17 | 21 | 0.017944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1365-5_0_3_line_20 | NAYY 4x150 SE | 17 | 22 | 0.089801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1365-5_0_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.083013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1365-5_0_3_line_22 | NAYY 4x150 SE | 20 | 28 | 0.0022148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1365-5_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.0050257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1365-5_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.02316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1365-5_0_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.014138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1365-5_0_3_line_26 | NAYY 4x150 SE | 26 | 27 | 0.026053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1365-5_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.016518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1365-5_0_3_line_28 | NAYY 4x150 SE | 27 | 29 | 0.017178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1365-5_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.025695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1365-5_0_3_trafo_4 | 0.25 MVA 20/0.4 kV | 31 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2687656.5249 | 1209401.8635 | 2687658.7146 | 1209398.9536 | 2687664.3726 | 1209385.8947 | 2687666.8149 | 1209374.9011 | 2687671.3097 | 1209368.563 | 2687676.3391 | 1209365.168 | 2687682.8276 | 1209363.3621 | 2687687.3194 | 1209362.9278 | 2687697.0047 | 1209364.4823 | 2687704.172 | 1209369.9693
1 | 2687641.731 | 1209478.123 | 2687641.0831 | 1209475.1337 | 2687639.5784 | 1209470.4419 | 2687639.3642 | 1209467.4256 | 2687638.7852 | 1209463.8926 | 2687637.5489 | 1209460.5945 | 2687634.7329 | 1209454.0822 | 2687634.2135 | 1209446.4918 | 2687635.7518 | 1209440.099 | 2687645.5874 | 1209423.1434 | 2687649.9762 | 1209410.5662 | 2687656.5249 | 1209401.8635
2 | 2687719.1991 | 1209382.865 | 2687710.6868 | 1209374.9569 | 2687704.172 | 1209369.9693
3 | 2687641.731 | 1209478.123 | 2687636.3712 | 1209478.6558 | 2687633.4234 | 1209479.0461 | 2687630.0568 | 1209480.0084 | 2687628.14 | 1209481.1143 | 2687625.8321 | 1209482.9705
4 | 2687719.1991 | 1209382.865 | 2687723.2191 | 1209381.4231 | 2687735.4204 | 1209380.4129 | 2687749.239 | 1209370.7542 | 2687753.0765 | 1209367.2527 | 2687757.6487 | 1209360.3154 | 2687757.5577 | 1209353.0648 | 2687753.2654 | 1209345.1076 | 2687726.8232 | 1209319.3574 | 2687716.5842 | 1209307.2922
5 | 2687625.8321 | 1209482.9705 | 2687624.2898 | 1209484.9714 | 2687623.502 | 1209486.85 | 2687622.8045 | 1209491.376 | 2687622.7587 | 1209494.4945
6 | 2687728.6643 | 1209208.1445 | 2687722.4927 | 1209210.0995 | 2687719.082 | 1209211.9729 | 2687711.2438 | 1209218.6954 | 2687699.7365 | 1209231.9462 | 2687692.2299 | 1209240.4192 | 2687687.4561 | 1209245.041 | 2687686.6897 | 1209247.0088 | 2687687.7501 | 1209249.8596 | 2687693.4764 | 1209256.4703 | 2687700.1869 | 1209265.4304 | 2687702.5355 | 1209270.635 | 2687706.6564 | 1209285.0829 | 2687710.3254 | 1209297.6895 | 2687713.2077 | 1209303.3134 | 2687716.5842 | 1209307.2922
7 | 2687623.3645 | 1209509.1036 | 2687622.7007 | 1209498.4459 | 2687622.7587 | 1209494.4945
8 | 2687653.5214 | 1209525.2272 | 2687654.7077 | 1209513.3034 | 2687653.196 | 1209503.4576
9 | 2687653.5214 | 1209525.2272 | 2687634.876 | 1209526.0873 | 2687631.3062 | 1209526.294
10 | 2687728.6643 | 1209208.1445 | 2687729.2255 | 1209210.8212 | 2687729.9236 | 1209212.9773 | 2687731.5065 | 1209216.4918 | 2687733.386 | 1209219.4769 | 2687736.4507 | 1209223.0354 | 2687739.9227 | 1209226.2886 | 2687756.1752 | 1209234.6664 | 2687759.1644 | 1209237.1565 | 2687766.4362 | 1209243.0895 | 2687774.3887 | 1209247.7207 | 2687776.1984 | 1209248.6754
11 | 2687624.4599 | 1209526.6903 | 2687623.3645 | 1209509.1036
12 | 2687624.4599 | 1209526.6903 | 2687631.3062 | 1209526.294
13 | 2687792.7623 | 1209257.4141 | 2687776.1984 | 1209248.6754
14 | 2687506.7984 | 1209419.1315 | 2687508.9119 | 1209419.1907 | 2687512.3867 | 1209419.6642 | 2687516.5353 | 1209421.3706 | 2687519.4323 | 1209423.4033 | 2687520.5341 | 1209424.7449
15 | 2687512.2577 | 1209443.1042 | 2687521.1533 | 1209434.6026 | 2687522.103 | 1209432.5708 | 2687522.4808 | 1209430.1414 | 2687522.0189 | 1209427.4217 | 2687520.9112 | 1209425.204 | 2687520.5341 | 1209424.7449
16 | 2687506.7984 | 1209419.1315 | 2687505.5835 | 1209419.0974 | 2687501.9131 | 1209419.5106 | 2687498.2269 | 1209420.4905 | 2687494.8935 | 1209421.7758 | 2687491.6018 | 1209423.84 | 2687489.6871 | 1209425.324 | 2687486.9334 | 1209428.5525 | 2687482.4764 | 1209436.4701 | 2687482.3059 | 1209436.6515
17 | 2687506.7736 | 1209448.3453 | 2687512.2577 | 1209443.1042
18 | 2687567.3325 | 1209488.7379 | 2687512.2577 | 1209443.1042
19 | 2687482.3059 | 1209436.6515 | 2687479.7657 | 1209439.3545 | 2687477.8075 | 1209440.6934 | 2687476.4626 | 1209441.1628 | 2687473.1704 | 1209441.1924 | 2687466.7247 | 1209441.1312 | 2687466.0256 | 1209441.1535
20 | 2687502.354 | 1209524.186 | 2687482.3059 | 1209436.6515
21 | 2687567.3325 | 1209488.7379 | 2687595.6372 | 1209474.6329 | 2687600.1872 | 1209472.8096 | 2687602.3119 | 1209473.5968 | 2687601.3019 | 1209476.6284 | 2687599.3089 | 1209479.301 | 2687581.2477 | 1209502.4956 | 2687580.4133 | 1209504.4402 | 2687580.7243 | 1209510.6107
22 | 2687580.8357 | 1209512.8227 | 2687580.7243 | 1209510.6107
23 | 2687461.0024 | 1209441.3135 | 2687466.0256 | 1209441.1535
24 | 2687502.354 | 1209524.186 | 2687492.2846 | 1209527.0625 | 2687480.2446 | 1209531.0639
25 | 2687461.0024 | 1209441.3135 | 2687458.8375 | 1209441.3825 | 2687448.6988 | 1209442.2456 | 2687446.9099 | 1209442.4114
26 | 2687581.6672 | 1209529.3194 | 2687559.4129 | 1209531.5944 | 2687555.7589 | 1209532.0566
27 | 2687581.6672 | 1209529.3194 | 2687580.8357 | 1209512.8227
28 | 2687581.6672 | 1209529.3194 | 2687598.8105 | 1209528.2243
29 | 2687624.4599 | 1209526.6903 | 2687614.4547 | 1209527.266 | 2687608.4136 | 1209527.6109 | 2687598.8105 | 1209528.2243

## bus_geodata
| x | y | coords
0 | 2687656.5249 | 1209401.8635
1 | 2687704.172 | 1209369.9693
2 | 2687641.731 | 1209478.123
3 | 2687719.1991 | 1209382.865
4 | 2687625.8321 | 1209482.9705
5 | 2687716.5842 | 1209307.2922
6 | 2687622.7587 | 1209494.4945
7 | 2687653.196 | 1209503.4576
8 | 2687653.5214 | 1209525.2272
9 | 2687728.6643 | 1209208.1445
10 | 2687623.3645 | 1209509.1036
11 | 2687631.3062 | 1209526.294
12 | 2687776.1984 | 1209248.6754
13 | 2687792.7623 | 1209257.4141
14 | 2687520.5341 | 1209424.7449
15 | 2687506.7984 | 1209419.1315
16 | 2687512.2577 | 1209443.1042
17 | 2687482.3059 | 1209436.6515
18 | 2687506.7736 | 1209448.3453
19 | 2687567.3325 | 1209488.7379
20 | 2687580.7243 | 1209510.6107
21 | 2687466.0256 | 1209441.1535
22 | 2687502.354 | 1209524.186
23 | 2687461.0024 | 1209441.3135
24 | 2687480.2446 | 1209531.0639
25 | 2687446.9099 | 1209442.4114
26 | 2687555.7589 | 1209532.0566
27 | 2687581.6672 | 1209529.3194
28 | 2687580.8357 | 1209512.8227
29 | 2687598.8105 | 1209528.2243
30 | 2687624.4599 | 1209526.6903
31 | 2687641.731 | 1209478.123

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99582 | -0.029338 | 0.022785 | 0.0057103
1 | 0.99515 | -0.034054 | 0.001863 | 0.0004669
2 | 0.99929 | -0.0049693 | 0 | 0
3 | 0.99502 | -0.034961 | 0 | 0
4 | 1 | 0 | -0.21335 | -0.053466
5 | 0.99427 | -0.040264 | 0.0008127 | 0.00020368
6 | 0.9984 | -0.011147 | 0.027343 | 0.0068529
7 | 0.98995 | -0.070431 | 0.069366 | 0.017385
8 | 0.99214 | -0.054964 | 0 | 0
9 | 0.9936 | -0.045014 | 0 | 0
10 | 0.99677 | -0.022484 | 0.030804 | 0.0077202
11 | 0.99436 | -0.039356 | 0.015986 | 0.0040065
12 | 0.99325 | -0.047434 | 0.0029129 | 0.00073003
13 | 0.99323 | -0.047583 | 0.00078393 | 0.00019647
14 | 0.98502 | -0.10513 | 0.00099523 | 0.00024943
15 | 0.98455 | -0.10848 | 0.0022183 | 0.00055595
16 | 0.98575 | -0.099939 | 0.0023513 | 0.00058928
17 | 0.98367 | -0.11475 | 0.0022921 | 0.00057446
18 | 0.98573 | -0.10009 | 0.0018913 | 0.000474
19 | 0.98848 | -0.080617 | 0.002829 | 0.00070902
20 | 0.99199 | -0.055935 | 0.0016735 | 0.00041941
21 | 0.98348 | -0.11605 | 0.0030919 | 0.00077491
22 | 0.98242 | -0.12364 | 0.0029958 | 0.00075083
23 | 0.98345 | -0.11625 | 0.0020802 | 0.00052135
24 | 0.9822 | -0.12522 | 0.0065865 | 0.0016507
25 | 0.98342 | -0.11652 | 0.0018474 | 0.000463
26 | 0.99279 | -0.050297 | 0.0024722 | 0.00061959
27 | 0.99289 | -0.049644 | 0 | 0
28 | 0.99209 | -0.055242 | 0.0025554 | 0.00064043
29 | 0.99378 | -0.043403 | 0.002451 | 0.00061429
30 | 0.9952 | -0.033452 | 0 | 0
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0063841 | 0.0015962 | -0.00638 | -0.0015955 | 4.1476e-06 | 6.4543e-07 | 0.0095383 | 0.0095386 | 0.0095386 | 0.99582 | -0.029338 | 0.99515 | -0.034054 | 3.5328
1 | -0.029169 | -0.0073065 | 0.029267 | 0.0073433 | 9.8626e-05 | 3.6847e-05 | 0.043584 | 0.043584 | 0.043584 | 0.99582 | -0.029338 | 0.99929 | -0.0049693 | 16.1424
2 | 0.004517 | 0.0011286 | -0.0045165 | -0.0011286 | 5.6411e-07 | -4.0556e-08 | 0.006753 | 0.0067531 | 0.0067531 | 0.99515 | -0.034054 | 0.99502 | -0.034961 | 2.5011
3 | -0.029267 | -0.0073433 | 0.029287 | 0.0073509 | 2.0193e-05 | 7.5433e-06 | 0.043584 | 0.043584 | 0.043584 | 0.99929 | -0.0049693 | 1 | 0 | 16.1423
4 | 0.0045165 | 0.0011286 | -0.0045132 | -0.0011289 | 3.2985e-06 | -2.3567e-07 | 0.0067531 | 0.0067536 | 0.0067536 | 0.99502 | -0.034961 | 0.99427 | -0.040264 | 2.5013
5 | 0.18326 | 0.046115 | -0.18298 | -0.046005 | 0.00028463 | 0.00010915 | 0.27276 | 0.27276 | 0.27276 | 1 | 0 | 0.9984 | -0.011147 | 50.512
6 | 0.0037005 | 0.00092519 | -0.003698 | -0.0009259 | 2.4244e-06 | -7.0966e-07 | 0.0055373 | 0.0055379 | 0.0055379 | 0.99427 | -0.040264 | 0.9936 | -0.045014 | 2.0511
7 | 0.15564 | 0.039153 | -0.15539 | -0.039058 | 0.00024571 | 9.4123e-05 | 0.23201 | 0.23201 | 0.23201 | 0.9984 | -0.011147 | 0.99677 | -0.022484 | 42.9652
8 | -0.069366 | -0.017385 | 0.069514 | 0.017442 | 0.00014886 | 5.6971e-05 | 0.10427 | 0.10427 | 0.10427 | 0.98995 | -0.070431 | 0.99214 | -0.054964 | 38.6168
9 | -0.069514 | -0.017442 | 0.069665 | 0.017499 | 0.00015087 | 5.7741e-05 | 0.10427 | 0.10427 | 0.10427 | 0.99214 | -0.054964 | 0.99436 | -0.039356 | 38.6167
10 | 0.003698 | 0.0009259 | -0.0036968 | -0.00092627 | 1.2372e-06 | -3.6116e-07 | 0.0055379 | 0.0055382 | 0.0055382 | 0.9936 | -0.045014 | 0.99325 | -0.047434 | 2.0512
11 | 0.12459 | 0.031338 | -0.1244 | -0.031266 | 0.00019025 | 7.2716e-05 | 0.18603 | 0.18603 | 0.18603 | 0.99677 | -0.022484 | 0.9952 | -0.033452 | 34.4495
12 | -0.085652 | -0.021506 | 0.085722 | 0.021533 | 7.0317e-05 | 2.6956e-05 | 0.12819 | 0.12819 | 0.12819 | 0.99436 | -0.039356 | 0.9952 | -0.033452 | 47.477
13 | 0.00078395 | 0.00019624 | -0.00078393 | -0.00019647 | 1.6118e-08 | -2.3619e-07 | 0.0011744 | 0.0011745 | 0.0011745 | 0.99325 | -0.047434 | 0.99323 | -0.047583 | 0.43498
14 | 0.021153 | 0.0053045 | -0.021143 | -0.0053009 | 9.8019e-06 | 3.5742e-06 | 0.031956 | 0.031956 | 0.031956 | 0.98502 | -0.10513 | 0.98455 | -0.10848 | 11.8356
15 | -0.022148 | -0.0055539 | 0.022164 | 0.0055597 | 1.5954e-05 | 5.8454e-06 | 0.03346 | 0.033459 | 0.03346 | 0.98502 | -0.10513 | 0.98575 | -0.099939 | 12.3924
16 | 0.018925 | 0.0047449 | -0.018909 | -0.004739 | 1.643e-05 | 5.9103e-06 | 0.028604 | 0.028604 | 0.028604 | 0.98455 | -0.10848 | 0.98367 | -0.11475 | 10.5939
17 | 0.0018913 | 0.00047391 | -0.0018913 | -0.000474 | 3.8582e-08 | -8.1862e-08 | 0.0028549 | 0.002855 | 0.002855 | 0.98575 | -0.099939 | 0.98573 | -0.10009 | 1.0574
18 | -0.026407 | -0.0066229 | 0.026478 | 0.0066493 | 7.0923e-05 | 2.6364e-05 | 0.039864 | 0.039863 | 0.039864 | 0.98575 | -0.099939 | 0.98848 | -0.080617 | 14.7643
19 | 0.007021 | 0.0017593 | -0.0070197 | -0.0017591 | 1.263e-06 | 2.5803e-07 | 0.010621 | 0.010621 | 0.010621 | 0.98367 | -0.11475 | 0.98348 | -0.11605 | 3.9336
20 | 0.0095956 | 0.0024052 | -0.0095838 | -0.0024018 | 1.1807e-05 | 3.4027e-06 | 0.014516 | 0.014516 | 0.014516 | 0.98367 | -0.11475 | 0.98242 | -0.12364 | 5.3763
21 | -0.029307 | -0.0073583 | 0.029408 | 0.007396 | 0.00010084 | 3.7717e-05 | 0.044122 | 0.044122 | 0.044122 | 0.98848 | -0.080617 | 0.99199 | -0.055935 | 16.3415
22 | -0.031081 | -0.0078154 | 0.031084 | 0.0078166 | 3.0053e-06 | 1.1273e-06 | 0.046632 | 0.046632 | 0.046632 | 0.99199 | -0.055935 | 0.99209 | -0.055242 | 17.2711
23 | 0.0039278 | 0.00098417 | -0.0039277 | -0.0009842 | 1.1075e-07 | -2.1175e-08 | 0.0059427 | 0.0059427 | 0.0059427 | 0.98348 | -0.11605 | 0.98345 | -0.11625 | 2.201
24 | 0.0065879 | 0.001651 | -0.0065865 | -0.0016507 | 1.4389e-06 | 2.6025e-07 | 0.0099783 | 0.0099785 | 0.0099785 | 0.98242 | -0.12364 | 0.9822 | -0.12522 | 3.6957
25 | 0.0018474 | 0.00046284 | -0.0018474 | -0.000463 | 6.8931e-08 | -1.5287e-07 | 0.0027952 | 0.0027953 | 0.0027953 | 0.98345 | -0.11625 | 0.98342 | -0.11652 | 1.0353
26 | -0.0024722 | -0.00061959 | 0.0024724 | 0.00061934 | 2.232e-07 | -2.5108e-07 | 0.0037054 | 0.0037052 | 0.0037054 | 0.99279 | -0.050297 | 0.99289 | -0.049644 | 1.3724
27 | 0.033666 | 0.0084669 | -0.03364 | -0.008457 | 2.6249e-05 | 9.8822e-06 | 0.050465 | 0.050465 | 0.050465 | 0.99289 | -0.049644 | 0.99209 | -0.055242 | 18.6906
28 | -0.036138 | -0.0090862 | 0.03617 | 0.0090981 | 3.1454e-05 | 1.1875e-05 | 0.05417 | 0.05417 | 0.05417 | 0.99289 | -0.049644 | 0.99378 | -0.043403 | 20.0629
29 | -0.038621 | -0.0097124 | 0.038674 | 0.0097327 | 5.364e-05 | 2.0297e-05 | 0.05784 | 0.05784 | 0.05784 | 0.99378 | -0.043403 | 0.9952 | -0.033452 | 21.4221

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21712 | 0.05441

## res_load
| p_mw | q_mvar
0 | 0.022785 | 0.0057103
1 | 0.001863 | 0.0004669
2 | 0.0037705 | 0.00094498
3 | 0.0008127 | 0.00020368
4 | 0.027343 | 0.0068529
5 | 0.069366 | 0.017385
6 | 0.030804 | 0.0077202
7 | 0.015986 | 0.0040065
8 | 0.0029129 | 0.00073003
9 | 0.00078393 | 0.00019647
10 | 0.00099523 | 0.00024943
11 | 0.0022183 | 0.00055595
12 | 0.0023513 | 0.00058928
13 | 0.0022921 | 0.00057446
14 | 0.0018913 | 0.000474
15 | 0.002829 | 0.00070902
16 | 0.0016735 | 0.00041941
17 | 0.0030919 | 0.00077491
18 | 0.0029958 | 0.00075083
19 | 0.0020802 | 0.00052135
20 | 0.0065865 | 0.0016507
21 | 0.0018474 | 0.000463
22 | 0.0024722 | 0.00061959
23 | 0.0025554 | 0.00064043
24 | 0.002451 | 0.00061429

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1