## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1366-10_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1366-10_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1366-10_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1366-10_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1366-10_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1366-10_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1366-10_0_2_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_1366-10_0_2_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1366-10_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1366-10_0_2_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_1366-10_0_2_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_1366-10_0_2_node_35 | 0.4 | n |  | TRUE
12 | bus_LV_1366-10_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1366-10_0_2_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1366-10_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1366-10_0_2_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1366-10_0_2_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_1366-10_0_2_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1366-10_0_2_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1366-10_0_2_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_1366-10_0_2_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1366-10_0_2_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_1366-10_0_2_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_1366-10_0_2_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1366-10_0_2_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1366-10_0_2_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1366-10_0_2_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1366-10_0_2_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1366-10_0_2_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1366-10_0_2_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1366-10_0_2_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1366-10_0_2_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1366-10_0_2_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1366-10_0_2_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_1366-10_0_2_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_1366-10_0_2_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1366-10_0_2_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1366-10_0_2_node_38 | 0.4 | n |  | TRUE
38 | bus_MV_133_0_node_153 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1366-10_0_2_load_0 | 0 | 0.005124 | 0.0012842 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1366-10_0_2_load_1 | 1 | 0.00443 | 0.0011103 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1366-10_0_2_load_5 | 5 | 0.0033228 | 0.00083277 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1366-10_0_2_load_6 | 8 | 0.020748 | 0.0052 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1366-10_0_2_load_28 | 9 | 0.0032224 | 0.00080761 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1366-10_0_2_load_25 | 10 | 0.0046952 | 0.0011767 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1366-10_0_2_load_35 | 11 | 0.0032135 | 0.00080537 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1366-10_0_2_load_9 | 15 | 0.00085894 | 0.00021527 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1366-10_0_2_load_39 | 16 | 0.002405 | 0.00060276 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1366-10_0_2_load_41 | 19 | 0.0074101 | 0.0018571 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1366-10_0_2_load_40 | 21 | 0.00053098 | 0.00013308 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1366-10_0_2_load_34 | 22 | 0.007994 | 0.0020035 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1366-10_0_2_load_11 | 23 | 0.0040817 | 0.001023 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1366-10_0_2_load_12 | 24 | 0.0012139 | 0.00030424 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1366-10_0_2_load_21 | 27 | 0.00075912 | 0.00019025 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1366-10_0_2_load_22 | 28 | 0.0017748 | 0.0004448 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1366-10_0_2_load_17 | 29 | 0.0023875 | 0.00059837 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1366-10_0_2_load_18 | 30 | 0.0041077 | 0.0010295 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1366-10_0_2_load_20 | 31 | 0.00086581 | 0.00021699 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1366-10_0_2_load_33 | 32 | 0.0010258 | 0.00025708 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1366-10_0_2_load_26 | 33 | 0.0082478 | 0.0020671 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1366-10_0_2_load_30 | 35 | 0.015417 | 0.0038638 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1366-10_0_2_load_31 | 36 | 0.0033489 | 0.00083931 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1366-10_0_2_load_38 | 37 | 0.0019727 | 0.00049442 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1366-10_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0025747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1366-10_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.042728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1366-10_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.022223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1366-10_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.023198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1366-10_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.013161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1366-10_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.020282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1366-10_0_2_line_6 | NAYY 4x150 SE | 3 | 7 | 0.027049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1366-10_0_2_line_7 | NAYY 4x150 SE | 4 | 8 | 0.017889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1366-10_0_2_line_8 | NAYY 4x150 SE | 5 | 9 | 0.04347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1366-10_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.053099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1366-10_0_2_line_10 | NAYY 4x150 SE | 7 | 11 | 0.015067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1366-10_0_2_line_11 | NAYY 4x150 SE | 8 | 12 | 0.046144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1366-10_0_2_line_12 | NAYY 4x150 SE | 9 | 13 | 0.019221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1366-10_0_2_line_13 | NAYY 4x150 SE | 11 | 22 | 0.010448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1366-10_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.016006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1366-10_0_2_line_15 | NAYY 4x150 SE | 12 | 15 | 0.014212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1366-10_0_2_line_16 | NAYY 4x150 SE | 13 | 34 | 0.030758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1366-10_0_2_line_17 | NAYY 4x150 SE | 14 | 16 | 0.051478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1366-10_0_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.004667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1366-10_0_2_line_19 | NAYY 4x150 SE | 16 | 21 | 0.013912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1366-10_0_2_line_20 | NAYY 4x150 SE | 17 | 20 | 0.009425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1366-10_0_2_line_21 | NAYY 4x150 SE | 18 | 19 | 0.044494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1366-10_0_2_line_22 | NAYY 4x150 SE | 18 | 20 | 0.0161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1366-10_0_2_line_23 | NAYY 4x150 SE | 20 | 23 | 0.04439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1366-10_0_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.017897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1366-10_0_2_line_25 | NAYY 4x150 SE | 24 | 25 | 0.012591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1366-10_0_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1366-10_0_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.017915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1366-10_0_2_line_28 | NAYY 4x150 SE | 26 | 28 | 0.0095247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1366-10_0_2_line_29 | NAYY 4x150 SE | 26 | 29 | 0.013404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1366-10_0_2_line_30 | NAYY 4x150 SE | 29 | 30 | 0.025312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1366-10_0_2_line_31 | NAYY 4x150 SE | 30 | 31 | 0.0020363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1366-10_0_2_line_32 | NAYY 4x150 SE | 31 | 32 | 0.00085637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1366-10_0_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.0073907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1366-10_0_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.012783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1366-10_0_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.027653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1366-10_0_2_line_36 | NAYY 4x150 SE | 36 | 37 | 0.089746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1366-10_0_2_trafo_5 | 0.25 MVA 20/0.4 kV | 38 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2693389.2675 | 1203663.4409 | 2693388.7668 | 1203660.9153
1 | 2693416.2015 | 1203693.0603 | 2693391.837 | 1203676.4016 | 2693389.2675 | 1203663.4409
2 | 2693384.4452 | 1203639.1169 | 2693388.7668 | 1203660.9153
3 | 2693437.5067 | 1203683.9541 | 2693420.1342 | 1203692.1879 | 2693416.2015 | 1203693.0603
4 | 2693416.2015 | 1203693.0603 | 2693408.662 | 1203703.8479
5 | 2693384.4452 | 1203639.1169 | 2693364.1449 | 1203640.4004
6 | 2693410.9774 | 1203633.4835 | 2693384.4452 | 1203639.1169
7 | 2693437.5067 | 1203683.9541 | 2693440.2728 | 1203701.6275
8 | 2693408.662 | 1203703.8479 | 2693395.3092 | 1203722.9534 | 2693391.9975 | 1203725.9703 | 2693386.073 | 1203728.6684 | 2693377.0218 | 1203730.1473
9 | 2693364.1449 | 1203640.4004 | 2693360.1943 | 1203644.8527 | 2693360.2085 | 1203691.9989
10 | 2693410.9774 | 1203633.4835 | 2693405.8577 | 1203619.3134
11 | 2693450.3764 | 1203746.5637 | 2693443.894 | 1203724.1362 | 2693440.3362 | 1203702.0326 | 2693440.2728 | 1203701.6275
12 | 2693358.9427 | 1203735.1041 | 2693361.6672 | 1203732.6562 | 2693377.0218 | 1203730.1473
13 | 2693402.3075 | 1203609.4875 | 2693405.8577 | 1203619.3134
14 | 2693450.3764 | 1203746.5637 | 2693458.2229 | 1203746.0194 | 2693466.3955 | 1203745.5469
15 | 2693450.3764 | 1203746.5637 | 2693451.1567 | 1203760.7546
16 | 2693328.1069 | 1203734.6998 | 2693351.5805 | 1203735.3337 | 2693358.9427 | 1203735.1041
17 | 2693466.3955 | 1203745.5469 | 2693469.9156 | 1203742.3443 | 2693474.2944 | 1203736.3088 | 2693482.58 | 1203725.22 | 2693490.7913 | 1203721.3015 | 2693506.4626 | 1203716.7406
18 | 2693451.413 | 1203765.4146 | 2693451.1567 | 1203760.7546
19 | 2693506.4626 | 1203716.7406 | 2693517.5091 | 1203713.5257 | 2693519.9115 | 1203713.6745
20 | 2693451.844 | 1203774.8276 | 2693451.413 | 1203765.4146
21 | 2693510.6649 | 1203759.8715 | 2693496.6889 | 1203764.0555 | 2693467.5307 | 1203771.2151
22 | 2693451.844 | 1203774.8276 | 2693458.9672 | 1203773.8161 | 2693467.5307 | 1203771.2151
23 | 2693451.844 | 1203774.8276 | 2693452.3748 | 1203786.6104 | 2693449.9825 | 1203819.1181
24 | 2693448.669 | 1203836.9672 | 2693449.9825 | 1203819.1181
25 | 2693447.7449 | 1203849.5242 | 2693448.669 | 1203836.9672
26 | 2693447.7449 | 1203849.5242 | 2693467.3727 | 1203851.7772
27 | 2693469.6674 | 1203834.0124 | 2693467.3727 | 1203851.7772
28 | 2693467.3727 | 1203851.7772 | 2693464.9223 | 1203860.9813
29 | 2693467.3727 | 1203851.7772 | 2693480.6888 | 1203853.3059
30 | 2693505.8359 | 1203856.1929 | 2693480.6888 | 1203853.3059
31 | 2693505.8359 | 1203856.1929 | 2693507.8589 | 1203856.4252
32 | 2693507.8589 | 1203856.4252 | 2693508.7097 | 1203856.5229
33 | 2693328.1069 | 1203734.6998 | 2693333.4504 | 1203729.7356 | 2693333.5473 | 1203729.7307
34 | 2693328.1069 | 1203734.6998 | 2693322.7062 | 1203734.5598 | 2693315.5396 | 1203732.7956
35 | 2693288.1746 | 1203730.6341 | 2693305.9229 | 1203730.4282 | 2693315.5396 | 1203732.7956
36 | 2693288.1746 | 1203730.6341 | 2693260.5616 | 1203645.2418

## bus_geodata
| x | y | coords
0 | 2693389.2675 | 1203663.4409
1 | 2693388.7668 | 1203660.9153
2 | 2693416.2015 | 1203693.0603
3 | 2693384.4452 | 1203639.1169
4 | 2693437.5067 | 1203683.9541
5 | 2693408.662 | 1203703.8479
6 | 2693364.1449 | 1203640.4004
7 | 2693410.9774 | 1203633.4835
8 | 2693440.2728 | 1203701.6275
9 | 2693377.0218 | 1203730.1473
10 | 2693360.2085 | 1203691.9989
11 | 2693405.8577 | 1203619.3134
12 | 2693450.3764 | 1203746.5637
13 | 2693358.9427 | 1203735.1041
14 | 2693466.3955 | 1203745.5469
15 | 2693451.1567 | 1203760.7546
16 | 2693506.4626 | 1203716.7406
17 | 2693451.413 | 1203765.4146
18 | 2693467.5307 | 1203771.2151
19 | 2693510.6649 | 1203759.8715
20 | 2693451.844 | 1203774.8276
21 | 2693519.9115 | 1203713.6745
22 | 2693402.3075 | 1203609.4875
23 | 2693449.9825 | 1203819.1181
24 | 2693448.669 | 1203836.9672
25 | 2693447.7449 | 1203849.5242
26 | 2693467.3727 | 1203851.7772
27 | 2693469.6674 | 1203834.0124
28 | 2693464.9223 | 1203860.9813
29 | 2693480.6888 | 1203853.3059
30 | 2693505.8359 | 1203856.1929
31 | 2693507.8589 | 1203856.4252
32 | 2693508.7097 | 1203856.5229
33 | 2693333.5473 | 1203729.7307
34 | 2693328.1069 | 1203734.6998
35 | 2693315.5396 | 1203732.7956
36 | 2693288.1746 | 1203730.6341
37 | 2693260.5616 | 1203645.2418
38 | 2693416.2015 | 1203693.0603

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99705 | -0.020602 | 0.005124 | 0.0012842
1 | 0.99698 | -0.021128 | 0.00443 | 0.0011103
2 | 0.99861 | -0.0096924 | 0 | 0
3 | 0.99647 | -0.024682 | 0 | 0
4 | 0.99701 | -0.020903 | 0 | 0
5 | 1 | 0 | -0.10716 | -0.026717
6 | 0.99634 | -0.02564 | 0 | 0
7 | 0.99604 | -0.027731 | 0 | 0
8 | 0.99577 | -0.029572 | 0.020748 | 0.0052
9 | 0.998 | -0.014011 | 0.0032224 | 0.00080761
10 | 0.99598 | -0.028149 | 0.0046952 | 0.0011767
11 | 0.9958 | -0.02943 | 0.0032135 | 0.00080537
12 | 0.99395 | -0.042347 | 0 | 0
13 | 0.9972 | -0.019601 | 0 | 0
14 | 0.99389 | -0.042823 | 0 | 0
15 | 0.99345 | -0.045868 | 0.00085894 | 0.00021527
16 | 0.99367 | -0.044353 | 0.002405 | 0.00060276
17 | 0.99329 | -0.046984 | 0 | 0
18 | 0.9928 | -0.050448 | 0 | 0
19 | 0.99233 | -0.053789 | 0.0074101 | 0.0018571
20 | 0.99297 | -0.04924 | 0 | 0
21 | 0.99366 | -0.044427 | 0.00053098 | 0.00013308
22 | 0.99568 | -0.030271 | 0.007994 | 0.0020035
23 | 0.99194 | -0.05654 | 0.0040817 | 0.001023
24 | 0.99163 | -0.058745 | 0.0012139 | 0.00030424
25 | 0.99143 | -0.060142 | 0 | 0
26 | 0.99112 | -0.062329 | 0 | 0
27 | 0.9911 | -0.062467 | 0.00075912 | 0.00019025
28 | 0.9911 | -0.062501 | 0.0017748 | 0.0004448
29 | 0.99096 | -0.063472 | 0.0023875 | 0.00059837
30 | 0.99074 | -0.065016 | 0.0041077 | 0.0010295
31 | 0.99073 | -0.065055 | 0.00086581 | 0.00021699
32 | 0.99073 | -0.065064 | 0.0010258 | 0.00025708
33 | 0.99583 | -0.029179 | 0.0082478 | 0.0020671
34 | 0.99592 | -0.028565 | 0 | 0
35 | 0.99554 | -0.031235 | 0.015417 | 0.0038638
36 | 0.99533 | -0.03272 | 0.0033489 | 0.00083931
37 | 0.99508 | -0.034508 | 0.0019727 | 0.00049442
38 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.020353 | 0.0051015 | -0.020351 | -0.005101 | 1.4823e-06 | 5.3654e-07 | 0.030375 | 0.030375 | 0.030375 | 0.99705 | -0.020602 | 0.99698 | -0.021128 | 11.2498
1 | -0.025476 | -0.0063857 | 0.025515 | 0.0064 | 3.8544e-05 | 1.4267e-05 | 0.038022 | 0.038021 | 0.038022 | 0.99705 | -0.020602 | 0.99861 | -0.0096924 | 14.0821
2 | 0.015921 | 0.0039907 | -0.015913 | -0.003988 | 7.8302e-06 | 2.722e-06 | 0.023763 | 0.023763 | 0.023763 | 0.99698 | -0.021128 | 0.99647 | -0.024682 | 8.801
3 | 0.048409 | 0.012159 | -0.048333 | -0.01213 | 7.5339e-05 | 2.8673e-05 | 0.072142 | 0.072143 | 0.072143 | 0.99861 | -0.0096924 | 0.99701 | -0.020903 | 26.7195
4 | -0.073924 | -0.018559 | 0.074023 | 0.018597 | 9.9669e-05 | 3.8162e-05 | 0.11016 | 0.11016 | 0.11016 | 0.99861 | -0.0096924 | 1 | 0 | 40.8014
5 | 0.0046974 | 0.0011766 | -0.0046968 | -0.0011767 | 6.2269e-07 | -2.468e-08 | 0.0070143 | 0.0070144 | 0.0070144 | 0.99647 | -0.024682 | 0.99634 | -0.02564 | 2.5979
6 | 0.011216 | 0.0028114 | -0.011211 | -0.0028099 | 4.7346e-06 | 1.4688e-06 | 0.016748 | 0.016749 | 0.016749 | 0.99647 | -0.024682 | 0.99604 | -0.027731 | 6.2032
7 | 0.048333 | 0.01213 | -0.048275 | -0.012108 | 5.8096e-05 | 2.2111e-05 | 0.072143 | 0.072143 | 0.072143 | 0.99701 | -0.020903 | 0.99577 | -0.029572 | 26.7195
8 | 0.03234 | 0.0081198 | -0.032277 | -0.0080962 | 6.283e-05 | 2.3596e-05 | 0.048128 | 0.048128 | 0.048128 | 1 | 0 | 0.998 | -0.014011 | 17.8251
9 | 0.0046968 | 0.0011767 | -0.0046952 | -0.0011767 | 1.6303e-06 | -6.4241e-08 | 0.0070144 | 0.0070147 | 0.0070147 | 0.99634 | -0.02564 | 0.99598 | -0.028149 | 2.598
10 | 0.011211 | 0.0028099 | -0.011208 | -0.0028091 | 2.6373e-06 | 8.1829e-07 | 0.016749 | 0.016749 | 0.016749 | 0.99604 | -0.027731 | 0.9958 | -0.02943 | 6.2032
11 | 0.027527 | 0.0069081 | -0.027478 | -0.0068899 | 4.8728e-05 | 1.8142e-05 | 0.041138 | 0.041138 | 0.041138 | 0.99577 | -0.029572 | 0.99395 | -0.042347 | 15.2362
12 | 0.029055 | 0.0072886 | -0.029032 | -0.0072801 | 2.2511e-05 | 8.4072e-06 | 0.043323 | 0.043323 | 0.043323 | 0.998 | -0.014011 | 0.9972 | -0.019601 | 16.0457
13 | 0.0079949 | 0.0020037 | -0.007994 | -0.0020035 | 9.3047e-07 | 2.2197e-07 | 0.011947 | 0.011947 | 0.011947 | 0.9958 | -0.02943 | 0.99568 | -0.030271 | 4.4247
14 | 0.0029368 | 0.00073509 | -0.0029366 | -0.00073523 | 1.9304e-07 | -1.3319e-07 | 0.0043963 | 0.0043964 | 0.0043964 | 0.99395 | -0.042347 | 0.99389 | -0.042823 | 1.6283
15 | 0.024541 | 0.0061548 | -0.024529 | -0.0061504 | 1.1972e-05 | 4.4205e-06 | 0.036741 | 0.036741 | 0.036741 | 0.99395 | -0.042347 | 0.99345 | -0.045868 | 13.608
16 | 0.029032 | 0.0072801 | -0.028996 | -0.0072667 | 3.6024e-05 | 1.3454e-05 | 0.043323 | 0.043323 | 0.043323 | 0.9972 | -0.019601 | 0.99592 | -0.028565 | 16.0457
17 | 0.0029366 | 0.00073523 | -0.002936 | -0.00073566 | 6.209e-07 | -4.2817e-07 | 0.0043964 | 0.0043966 | 0.0043966 | 0.99389 | -0.042823 | 0.99367 | -0.044353 | 1.6284
18 | 0.02367 | 0.0059352 | -0.023667 | -0.0059338 | 3.6608e-06 | 1.3476e-06 | 0.035455 | 0.035455 | 0.035455 | 0.99345 | -0.045868 | 0.99329 | -0.046984 | 13.1315
19 | 0.00053099 | 0.0001329 | -0.00053098 | -0.00013308 | 5.4883e-09 | -1.781e-07 | 0.00079509 | 0.00079515 | 0.00079515 | 0.99367 | -0.044353 | 0.99366 | -0.044427 | 0.2945
20 | 0.023667 | 0.0059338 | -0.023659 | -0.0059311 | 7.393e-06 | 2.7215e-06 | 0.035455 | 0.035455 | 0.035455 | 0.99329 | -0.046984 | 0.99297 | -0.04924 | 13.1315
21 | 0.0074135 | 0.0018579 | -0.0074101 | -0.0018571 | 3.4279e-06 | 7.4333e-07 | 0.011111 | 0.011112 | 0.011112 | 0.9928 | -0.050448 | 0.99233 | -0.053789 | 4.1154
22 | -0.0074135 | -0.0018579 | 0.0074147 | 0.0018581 | 1.2403e-06 | 2.6882e-07 | 0.011111 | 0.011111 | 0.011111 | 0.9928 | -0.050448 | 0.99297 | -0.04924 | 4.1153
23 | 0.016245 | 0.0040729 | -0.016228 | -0.0040672 | 1.6415e-05 | 5.74e-06 | 0.024344 | 0.024344 | 0.024344 | 0.99297 | -0.04924 | 0.99194 | -0.05654 | 9.0163
24 | 0.012146 | 0.0030442 | -0.012143 | -0.003043 | 3.7078e-06 | 1.1951e-06 | 0.018221 | 0.018221 | 0.018221 | 0.99194 | -0.05654 | 0.99163 | -0.058745 | 6.7485
25 | 0.010929 | 0.0027388 | -0.010927 | -0.0027381 | 2.113e-06 | 6.503e-07 | 0.016399 | 0.016399 | 0.016399 | 0.99163 | -0.058745 | 0.99143 | -0.060142 | 6.0739
26 | 0.010927 | 0.0027381 | -0.010923 | -0.0027371 | 3.3061e-06 | 1.0176e-06 | 0.016399 | 0.0164 | 0.0164 | 0.99143 | -0.060142 | 0.99112 | -0.062329 | 6.0739
27 | 0.00075914 | 0.00019003 | -0.00075912 | -0.00019025 | 1.452e-08 | -2.2529e-07 | 0.0011396 | 0.0011397 | 0.0011397 | 0.99112 | -0.062329 | 0.9911 | -0.062467 | 0.42212
28 | 0.0017748 | 0.00044469 | -0.0017748 | -0.0004448 | 4.2199e-08 | -1.0652e-07 | 0.0026646 | 0.0026646 | 0.0026646 | 0.99112 | -0.062329 | 0.9911 | -0.062501 | 0.9869
29 | 0.0083894 | 0.0021024 | -0.0083881 | -0.0021021 | 1.3269e-06 | 3.3763e-07 | 0.012595 | 0.012595 | 0.012595 | 0.99112 | -0.062329 | 0.99096 | -0.063472 | 4.665
30 | 0.0060006 | 0.0015037 | -0.0059993 | -0.0015035 | 1.2823e-06 | 1.6718e-07 | 0.0090104 | 0.0090105 | 0.0090105 | 0.99096 | -0.063472 | 0.99074 | -0.065016 | 3.3372
31 | 0.0018916 | 0.00047404 | -0.0018916 | -0.00047406 | 1.0256e-08 | -2.2278e-08 | 0.002841 | 0.002841 | 0.002841 | 0.99074 | -0.065016 | 0.99073 | -0.065055 | 1.0522
32 | 0.0010258 | 0.00025707 | -0.0010258 | -0.00025708 | 1.2683e-09 | -1.054e-08 | 0.0015406 | 0.0015406 | 0.0015406 | 0.99073 | -0.065055 | 0.99073 | -0.065064 | 0.5706
33 | -0.0082478 | -0.0020671 | 0.0082485 | 0.0020673 | 7.0047e-07 | 1.7325e-07 | 0.012324 | 0.012324 | 0.012324 | 0.99583 | -0.029179 | 0.99592 | -0.028565 | 4.5645
34 | 0.020748 | 0.0051994 | -0.02074 | -0.0051966 | 7.6651e-06 | 2.7818e-06 | 0.030999 | 0.030999 | 0.030999 | 0.99592 | -0.028565 | 0.99554 | -0.031235 | 11.4812
35 | 0.0053232 | 0.0013328 | -0.0053221 | -0.0013327 | 1.0923e-06 | 6.0618e-08 | 0.007956 | 0.0079562 | 0.0079562 | 0.99554 | -0.031235 | 0.99533 | -0.03272 | 2.9467
36 | 0.0019732 | 0.00049344 | -0.0019727 | -0.00049442 | 4.8728e-07 | -9.7872e-07 | 0.0029496 | 0.00295 | 0.00295 | 0.99533 | -0.03272 | 0.99508 | -0.034508 | 1.0926

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11049 | 0.02755

## res_load
| p_mw | q_mvar
0 | 0.005124 | 0.0012842
1 | 0.00443 | 0.0011103
2 | 0.0033228 | 0.00083277
3 | 0.020748 | 0.0052
4 | 0.0032224 | 0.00080761
5 | 0.0046952 | 0.0011767
6 | 0.0032135 | 0.00080537
7 | 0.00085894 | 0.00021527
8 | 0.002405 | 0.00060276
9 | 0.0074101 | 0.0018571
10 | 0.00053098 | 0.00013308
11 | 0.007994 | 0.0020035
12 | 0.0040817 | 0.001023
13 | 0.0012139 | 0.00030424
14 | 0.00075912 | 0.00019025
15 | 0.0017748 | 0.0004448
16 | 0.0023875 | 0.00059837
17 | 0.0041077 | 0.0010295
18 | 0.00086581 | 0.00021699
19 | 0.0010258 | 0.00025708
20 | 0.0082478 | 0.0020671
21 | 0.015417 | 0.0038638
22 | 0.0033489 | 0.00083931
23 | 0.0019727 | 0.00049442

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1