## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1366-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1366-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1366-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1366-4_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1366-4_0_4_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_1366-4_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_1366-4_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1366-4_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1366-4_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1366-4_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1366-4_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1366-4_0_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1366-4_0_4_node_37 | 0.4 | n |  | TRUE
13 | bus_LV_1366-4_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1366-4_0_4_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_1366-4_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1366-4_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1366-4_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1366-4_0_4_node_46 | 0.4 | n |  | TRUE
19 | bus_LV_1366-4_0_4_node_50 | 0.4 | n |  | TRUE
20 | bus_LV_1366-4_0_4_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_1366-4_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1366-4_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1366-4_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1366-4_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1366-4_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1366-4_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1366-4_0_4_node_39 | 0.4 | n |  | TRUE
28 | bus_LV_1366-4_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1366-4_0_4_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_1366-4_0_4_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_1366-4_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1366-4_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_1366-4_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_1366-4_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1366-4_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_1366-4_0_4_node_52 | 0.4 | n |  | TRUE
37 | bus_LV_1366-4_0_4_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_1366-4_0_4_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_1366-4_0_4_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_1366-4_0_4_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_1366-4_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_1366-4_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_1366-4_0_4_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_1366-4_0_4_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_1366-4_0_4_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_1366-4_0_4_node_49 | 0.4 | n |  | TRUE
47 | bus_MV_133_0_node_231 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1366-4_0_4_load_0 | 0 | 0.055883 | 0.014006 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1366-4_0_4_load_9 | 4 | 0.0030024 | 0.00075247 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1366-4_0_4_load_11 | 5 | 0.0026037 | 0.00065255 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1366-4_0_4_load_5 | 7 | 0.0053013 | 0.0013286 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1366-4_0_4_load_6 | 8 | 0.0015843 | 0.00039707 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1366-4_0_4_load_8 | 9 | 0.00083326 | 0.00020883 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1366-4_0_4_load_10 | 10 | 0.0030728 | 0.00077013 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1366-4_0_4_load_37 | 12 | 0.0024164 | 0.0006056 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1366-4_0_4_load_36 | 14 | 0.0032083 | 0.00080407 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1366-4_0_4_load_12 | 15 | 0.0053326 | 0.0013365 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1366-4_0_4_load_50 | 19 | 0.00149 | 0.00037343 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1366-4_0_4_load_45 | 20 | 0.00087047 | 0.00021816 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1366-4_0_4_load_17 | 21 | 0.00026377 | 6.6107e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1366-4_0_4_load_18 | 22 | 0.00056806 | 0.00014237 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1366-4_0_4_load_20 | 24 | 0.00029567 | 7.4101e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1366-4_0_4_load_21 | 25 | 0.00054581 | 0.00013679 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1366-4_0_4_load_22 | 26 | 0.0020978 | 0.00052576 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1366-4_0_4_load_39 | 27 | 0.00059984 | 0.00015033 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1366-4_0_4_load_27 | 28 | 0.00048947 | 0.00012267 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1366-4_0_4_load_41 | 29 | 0.0015833 | 0.00039681 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1366-4_0_4_load_40 | 30 | 0.00072382 | 0.00018141 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1366-4_0_4_load_28 | 31 | 0.0020991 | 0.00052607 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1366-4_0_4_load_23 | 32 | 0.0022208 | 0.00055658 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1366-4_0_4_load_25 | 34 | 0.001743 | 0.00043683 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1366-4_0_4_load_26 | 35 | 0.00054378 | 0.00013628 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1366-4_0_4_load_52 | 36 | 0.0010699 | 0.00026815 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1366-4_0_4_load_38 | 37 | 0.0031019 | 0.0007774 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1366-4_0_4_load_48 | 39 | 0.0028175 | 0.00070614 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1366-4_0_4_load_44 | 40 | 0.00095965 | 0.00024051 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1366-4_0_4_load_29 | 41 | 0.0075346 | 0.0018884 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1366-4_0_4_load_30 | 42 | 0.017572 | 0.0044039 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1366-4_0_4_load_32 | 43 | 0.004769 | 0.0011952 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1366-4_0_4_load_35 | 44 | 0.0053263 | 0.0013349 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1366-4_0_4_load_49 | 46 | 0.00067379 | 0.00016887 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1366-4_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.057958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1366-4_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.10629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1366-4_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.044551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1366-4_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.018773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1366-4_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.037595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1366-4_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.12491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1366-4_0_4_line_6 | NAYY 4x150 SE | 6 | 10 | 0.034182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1366-4_0_4_line_7 | NAYY 4x150 SE | 6 | 7 | 0.01378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1366-4_0_4_line_8 | NAYY 4x150 SE | 7 | 8 | 0.016653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1366-4_0_4_line_9 | NAYY 4x150 SE | 8 | 9 | 0.031992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1366-4_0_4_line_10 | NAYY 4x150 SE | 9 | 11 | 0.010141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1366-4_0_4_line_11 | NAYY 4x150 SE | 10 | 12 | 0.049239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1366-4_0_4_line_12 | NAYY 4x150 SE | 11 | 13 | 0.010611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1366-4_0_4_line_13 | NAYY 4x150 SE | 12 | 14 | 0.020268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1366-4_0_4_line_14 | NAYY 4x150 SE | 13 | 18 | 0.21271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1366-4_0_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.012566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1366-4_0_4_line_16 | NAYY 4x150 SE | 14 | 44 | 0.021126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1366-4_0_4_line_17 | NAYY 4x150 SE | 15 | 16 | 0.01861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1366-4_0_4_line_18 | NAYY 4x150 SE | 16 | 17 | 0.003165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1366-4_0_4_line_19 | NAYY 4x150 SE | 17 | 19 | 0.027939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1366-4_0_4_line_20 | NAYY 4x150 SE | 18 | 20 | 0.033117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1366-4_0_4_line_21 | NAYY 4x150 SE | 20 | 45 | 0.18781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1366-4_0_4_line_22 | NAYY 4x150 SE | 21 | 22 | 0.026995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1366-4_0_4_line_23 | NAYY 4x150 SE | 21 | 23 | 0.0053495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1366-4_0_4_line_24 | NAYY 4x150 SE | 22 | 24 | 0.018872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1366-4_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.05986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1366-4_0_4_line_26 | NAYY 4x150 SE | 23 | 26 | 0.1316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1366-4_0_4_line_27 | NAYY 4x150 SE | 24 | 27 | 0.0083421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1366-4_0_4_line_28 | NAYY 4x150 SE | 25 | 28 | 0.011347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1366-4_0_4_line_29 | NAYY 4x150 SE | 26 | 29 | 0.047711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1366-4_0_4_line_30 | NAYY 4x150 SE | 27 | 30 | 0.038017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1366-4_0_4_line_31 | NAYY 4x150 SE | 28 | 31 | 0.029076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1366-4_0_4_line_32 | NAYY 4x150 SE | 30 | 38 | 0.020865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1366-4_0_4_line_33 | NAYY 4x150 SE | 31 | 40 | 0.018434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1366-4_0_4_line_34 | NAYY 4x150 SE | 32 | 33 | 0.029507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1366-4_0_4_line_35 | NAYY 4x150 SE | 33 | 34 | 0.030151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1366-4_0_4_line_36 | NAYY 4x150 SE | 33 | 35 | 0.15481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1366-4_0_4_line_37 | NAYY 4x150 SE | 33 | 36 | 0.087657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1366-4_0_4_line_38 | NAYY 4x150 SE | 34 | 37 | 0.025187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1366-4_0_4_line_39 | NAYY 4x150 SE | 35 | 38 | 0.010513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1366-4_0_4_line_40 | NAYY 4x150 SE | 38 | 39 | 0.016683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1366-4_0_4_line_41 | NAYY 4x150 SE | 39 | 45 | 0.10131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1366-4_0_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.029442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1366-4_0_4_line_43 | NAYY 4x150 SE | 42 | 43 | 0.026502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1366-4_0_4_line_44 | NAYY 4x150 SE | 43 | 44 | 0.028747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1366-4_0_4_line_45 | NAYY 4x150 SE | 45 | 46 | 0.055998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1366-4_0_4_trafo_4 | 0.25 MVA 20/0.4 kV | 47 | 3 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2689459.7375 | 1203519.7528 | 2689456.351 | 1203524.3273 | 2689445.2516 | 1203533.7561 | 2689438.0486 | 1203538.607 | 2689436.8492 | 1203548.0619 | 2689439.9416 | 1203567.3027
1 | 2689459.7375 | 1203519.7528 | 2689472.3293 | 1203520.931 | 2689481.4514 | 1203521.0677 | 2689490.9208 | 1203542.7126 | 2689506.3684 | 1203552.3725 | 2689519.4591 | 1203567.9789 | 2689524.7237 | 1203577.7086 | 2689529.2801 | 1203587.9836
2 | 2689550.8476 | 1203626.9434 | 2689533.012 | 1203596.4006 | 2689529.2801 | 1203587.9836
3 | 2689550.8476 | 1203626.9434 | 2689557.9551 | 1203639.1135 | 2689558.3266 | 1203643.7782
4 | 2689550.8476 | 1203626.9434 | 2689560.2991 | 1203607.6503 | 2689562.1597 | 1203594.2027 | 2689562.9589 | 1203591.7963
5 | 2689568.6961 | 1203768.1922 | 2689567.2393 | 1203760.81 | 2689567.1118 | 1203754.0926 | 2689558.3266 | 1203643.7782
6 | 2689568.6961 | 1203768.1922 | 2689535.4183 | 1203760.3809
7 | 2689568.6961 | 1203768.1922 | 2689569.8397 | 1203781.9248
8 | 2689569.8397 | 1203781.9248 | 2689571.2217 | 1203798.5199
9 | 2689571.2217 | 1203798.5199 | 2689573.8767 | 1203830.4019
10 | 2689574.7183 | 1203840.5076 | 2689573.8767 | 1203830.4019
11 | 2689535.4183 | 1203760.3809 | 2689520.424 | 1203756.8612 | 2689494.384 | 1203760.429 | 2689487.6511 | 1203763.8539
12 | 2689574.7183 | 1203840.5076 | 2689585.359 | 1203840.3226
13 | 2689487.6511 | 1203763.8539 | 2689469.5858 | 1203773.0435
14 | 2689585.359 | 1203840.3226 | 2689784.8393 | 1203766.4914
15 | 2689585.359 | 1203840.3226 | 2689586.8453 | 1203852.8007
16 | 2689464.8691 | 1203792.6098 | 2689464.1974 | 1203789.3513 | 2689464.3131 | 1203781.6257 | 2689469.5858 | 1203773.0435 | 2689469.5858 | 1203773.0435
17 | 2689576.7475 | 1203861.9743 | 2689587.7311 | 1203860.2379 | 2689586.8453 | 1203852.8007
18 | 2689576.7475 | 1203861.9743 | 2689577.0426 | 1203865.1252
19 | 2689577.0426 | 1203865.1252 | 2689579.5617 | 1203892.9499
20 | 2689784.8393 | 1203766.4914 | 2689771.4849 | 1203736.1863
21 | 2689721.0424 | 1203555.2725 | 2689771.4849 | 1203736.1863
22 | 2689737.8362 | 1203353.1972 | 2689742.2693 | 1203339.3947 | 2689746.6022 | 1203327.6722
23 | 2689748.4568 | 1203322.6545 | 2689746.6022 | 1203327.6722
24 | 2689732.0654 | 1203371.1647 | 2689737.8362 | 1203353.1972
25 | 2689748.4568 | 1203322.6545 | 2689755.0993 | 1203317.1618 | 2689764.486 | 1203303.7719 | 2689783.892 | 1203274.7792
26 | 2689748.4568 | 1203322.6545 | 2689690.5272 | 1203219.4282 | 2689680.0059 | 1203211.4059
27 | 2689732.0654 | 1203371.1647 | 2689730.9644 | 1203374.5923 | 2689730.5093 | 1203379.3124
28 | 2689789.6617 | 1203265.0579 | 2689788.4093 | 1203268.0302 | 2689783.892 | 1203274.7792
29 | 2689680.0059 | 1203211.4059 | 2689669.8511 | 1203203.6631 | 2689648.8763 | 1203189.539 | 2689639.8098 | 1203186.2234
30 | 2689730.5093 | 1203379.3124 | 2689729.0352 | 1203394.5987 | 2689726.1788 | 1203417.078
31 | 2689789.6617 | 1203265.0579 | 2689792.6315 | 1203258.0094 | 2689792.8988 | 1203246.8172 | 2689791.186 | 1203236.7293
32 | 2689721.5362 | 1203437.3473 | 2689725.0996 | 1203425.5709 | 2689726.1788 | 1203417.078
33 | 2689783.7351 | 1203220.0253 | 2689788.2895 | 1203227.4241 | 2689791.186 | 1203236.7293 | 2689791.186 | 1203236.7293
34 | 2689624.4671 | 1203323.5826 | 2689622.4282 | 1203317.9705 | 2689625.1628 | 1203307.149 | 2689629.3344 | 1203300.4738 | 2689629.686 | 1203295.9845
35 | 2689624.4671 | 1203323.5826 | 2689647.0944 | 1203310.2356 | 2689649.6254 | 1203307.2941
36 | 2689624.4671 | 1203323.5826 | 2689626.2961 | 1203333.5499 | 2689624.2029 | 1203351.8304 | 2689626.7063 | 1203360.9739 | 2689630.9457 | 1203366.5078 | 2689637.8333 | 1203368.5014 | 2689649.8082 | 1203367.7027 | 2689657.9736 | 1203370.2492 | 2689666.1995 | 1203376.3655 | 2689699.0054 | 1203411.3698 | 2689714.6481 | 1203429.4056
37 | 2689624.4671 | 1203323.5826 | 2689543.2744 | 1203356.62
38 | 2689669.1407 | 1203291.4987 | 2689652.3457 | 1203304.1326 | 2689649.6254 | 1203307.2941
39 | 2689721.5362 | 1203437.3473 | 2689714.6481 | 1203429.4056
40 | 2689721.5362 | 1203437.3473 | 2689721.2468 | 1203454.0281
41 | 2689721.0424 | 1203555.2725 | 2689719.7734 | 1203538.9428 | 2689721.2468 | 1203454.0281
42 | 2689481.8039 | 1203875.5874 | 2689480.981 | 1203870.767 | 2689476.024 | 1203846.721
43 | 2689476.024 | 1203846.721 | 2689470.6732 | 1203820.7649
44 | 2689464.8691 | 1203792.6098 | 2689470.6732 | 1203820.7649
45 | 2689676.8545 | 1203521.6982 | 2689693.9006 | 1203529.7927 | 2689721.0424 | 1203555.2725

## bus_geodata
| x | y | coords
0 | 2689439.9416 | 1203567.3027
1 | 2689459.7375 | 1203519.7528
2 | 2689529.2801 | 1203587.9836
3 | 2689550.8476 | 1203626.9434
4 | 2689558.3266 | 1203643.7782
5 | 2689562.9589 | 1203591.7963
6 | 2689568.6961 | 1203768.1922
7 | 2689569.8397 | 1203781.9248
8 | 2689571.2217 | 1203798.5199
9 | 2689573.8767 | 1203830.4019
10 | 2689535.4183 | 1203760.3809
11 | 2689574.7183 | 1203840.5076
12 | 2689487.6511 | 1203763.8539
13 | 2689585.359 | 1203840.3226
14 | 2689469.5858 | 1203773.0435
15 | 2689586.8453 | 1203852.8007
16 | 2689576.7475 | 1203861.9743
17 | 2689577.0426 | 1203865.1252
18 | 2689784.8393 | 1203766.4914
19 | 2689579.5617 | 1203892.9499
20 | 2689771.4849 | 1203736.1863
21 | 2689746.6022 | 1203327.6722
22 | 2689737.8362 | 1203353.1972
23 | 2689748.4568 | 1203322.6545
24 | 2689732.0654 | 1203371.1647
25 | 2689783.8919 | 1203274.7792
26 | 2689680.0059 | 1203211.4059
27 | 2689730.5093 | 1203379.3124
28 | 2689789.6617 | 1203265.0579
29 | 2689639.8098 | 1203186.2234
30 | 2689726.1788 | 1203417.078
31 | 2689791.186 | 1203236.7293
32 | 2689629.686 | 1203295.9845
33 | 2689624.4671 | 1203323.5826
34 | 2689649.6254 | 1203307.2941
35 | 2689714.6481 | 1203429.4056
36 | 2689543.2744 | 1203356.62
37 | 2689669.1407 | 1203291.4987
38 | 2689721.5362 | 1203437.3473
39 | 2689721.2468 | 1203454.0281
40 | 2689783.7351 | 1203220.0253
41 | 2689481.8039 | 1203875.5874
42 | 2689476.024 | 1203846.721
43 | 2689470.6732 | 1203820.7649
44 | 2689464.8691 | 1203792.6098
45 | 2689721.0424 | 1203555.2725
46 | 2689676.8545 | 1203521.6982
47 | 2689529.2801 | 1203587.9836

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98308 | -0.11848 | 0.055883 | 0.014006
1 | 0.98778 | -0.085187 | 0 | 0
2 | 0.99639 | -0.024945 | 0 | 0
3 | 1 | 0 | -0.14641 | -0.036782
4 | 0.99885 | -0.0079651 | 0.0030024 | 0.00075247
5 | 0.99986 | -0.00097777 | 0.0026037 | 0.00065255
6 | 0.99144 | -0.05952 | 0 | 0
7 | 0.99106 | -0.062178 | 0.0053013 | 0.0013286
8 | 0.99066 | -0.064944 | 0.0015843 | 0.00039707
9 | 0.98994 | -0.070004 | 0.00083326 | 0.00020883
10 | 0.98926 | -0.074796 | 0.0030728 | 0.00077013
11 | 0.98972 | -0.071566 | 0 | 0
12 | 0.98635 | -0.095365 | 0.0024164 | 0.0006056
13 | 0.98949 | -0.073201 | 0 | 0
14 | 0.98522 | -0.10336 | 0.0032083 | 0.00080407
15 | 0.98936 | -0.074076 | 0.0053326 | 0.0013365
16 | 0.98932 | -0.074359 | 0 | 0
17 | 0.98932 | -0.074408 | 0 | 0
18 | 0.98587 | -0.098657 | 0 | 0
19 | 0.98926 | -0.074833 | 0.00149 | 0.00037343
20 | 0.98474 | -0.10661 | 0.00087047 | 0.00021816
21 | 0.97339 | -0.18763 | 0.00026377 | 6.6107e-05
22 | 0.97371 | -0.18534 | 0.00056806 | 0.00014237
23 | 0.97333 | -0.18807 | 0 | 0
24 | 0.97394 | -0.18363 | 0.00029567 | 7.4101e-05
25 | 0.97297 | -0.19066 | 0.00054581 | 0.00013679
26 | 0.97262 | -0.1932 | 0.0020978 | 0.00052576
27 | 0.97405 | -0.18284 | 0.00059984 | 0.00015033
28 | 0.97291 | -0.19109 | 0.00048947 | 0.00012267
29 | 0.97251 | -0.19399 | 0.0015833 | 0.00039681
30 | 0.97458 | -0.17903 | 0.00072382 | 0.00018141
31 | 0.97278 | -0.19203 | 0.0020991 | 0.00052607
32 | 0.97282 | -0.19172 | 0.0022208 | 0.00055658
33 | 0.97292 | -0.19103 | 0 | 0
34 | 0.9727 | -0.19258 | 0.001743 | 0.00043683
35 | 0.97476 | -0.17774 | 0.00054378 | 0.00013628
36 | 0.97278 | -0.19203 | 0.0010699 | 0.00026815
37 | 0.97259 | -0.1934 | 0.0031019 | 0.0007774
38 | 0.97489 | -0.17678 | 0 | 0
39 | 0.97536 | -0.17346 | 0.0028175 | 0.00070614
40 | 0.97275 | -0.19221 | 0.00095965 | 0.00024051
41 | 0.9816 | -0.12906 | 0.0075346 | 0.0018884
42 | 0.98193 | -0.12676 | 0.017572 | 0.0044039
43 | 0.98289 | -0.11988 | 0.004769 | 0.0011952
44 | 0.98414 | -0.11102 | 0.0053263 | 0.0013349
45 | 0.97858 | -0.15036 | 0 | 0
46 | 0.97852 | -0.15076 | 0.00067379 | 0.00016887
47 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.055883 | -0.014006 | 0.056142 | 0.014104 | 0.00025876 | 9.8783e-05 | 0.084586 | 0.084586 | 0.084586 | 0.98308 | -0.11848 | 0.98778 | -0.085187 | 31.3281
1 | -0.056142 | -0.014104 | 0.056616 | 0.014286 | 0.00047452 | 0.00018114 | 0.084586 | 0.084585 | 0.084586 | 0.98778 | -0.085187 | 0.99639 | -0.024945 | 31.328
2 | -0.056616 | -0.014286 | 0.056815 | 0.014361 | 0.0001989 | 7.5917e-05 | 0.084585 | 0.084585 | 0.084585 | 0.99639 | -0.024945 | 1 | 0 | 31.3279
3 | 0.086186 | 0.021769 | -0.086089 | -0.021732 | 9.6422e-05 | 3.6593e-05 | 0.12831 | 0.12831 | 0.12831 | 1 | 0 | 0.99885 | -0.0079651 | 23.7603
4 | 0.0026041 | 0.0006522 | -0.0026037 | -0.00065255 | 3.5223e-07 | -3.5768e-07 | 0.0038747 | 0.0038749 | 0.0038749 | 1 | 0 | 0.99986 | -0.00097777 | 1.4352
5 | 0.083087 | 0.02098 | -0.082489 | -0.020753 | 0.00059761 | 0.0002266 | 0.12383 | 0.12383 | 0.12383 | 0.99885 | -0.0079651 | 0.99144 | -0.05952 | 22.9322
6 | 0.044254 | 0.011136 | -0.04416 | -0.0111 | 9.4143e-05 | 3.5769e-05 | 0.066436 | 0.066436 | 0.066436 | 0.99144 | -0.05952 | 0.98926 | -0.074796 | 24.6059
7 | 0.038235 | 0.009617 | -0.038221 | -0.0096119 | 1.4165e-05 | 5.0926e-06 | 0.057398 | 0.057398 | 0.057398 | 0.99144 | -0.05952 | 0.99106 | -0.062178 | 10.6293
8 | 0.03292 | 0.0082833 | -0.032907 | -0.0082788 | 1.2699e-05 | 4.4553e-06 | 0.049439 | 0.049439 | 0.049439 | 0.99106 | -0.062178 | 0.99066 | -0.064944 | 9.1553
9 | 0.031323 | 0.0078818 | -0.031301 | -0.0078741 | 2.2105e-05 | 7.6787e-06 | 0.047059 | 0.047059 | 0.047059 | 0.99066 | -0.064944 | 0.98994 | -0.070004 | 8.7147
10 | 0.030467 | 0.0076653 | -0.030461 | -0.007663 | 6.6388e-06 | 2.2927e-06 | 0.045807 | 0.045807 | 0.045807 | 0.98994 | -0.070004 | 0.98972 | -0.071566 | 8.4828
11 | 0.041087 | 0.01033 | -0.04097 | -0.010286 | 0.0001174 | 4.4523e-05 | 0.061814 | 0.061814 | 0.061814 | 0.98926 | -0.074796 | 0.98635 | -0.095365 | 22.8941
12 | 0.030461 | 0.007663 | -0.030454 | -0.0076606 | 6.9466e-06 | 2.3991e-06 | 0.045807 | 0.045807 | 0.045807 | 0.98972 | -0.071566 | 0.98949 | -0.073201 | 8.4828
13 | 0.038553 | 0.00968 | -0.038511 | -0.0096638 | 4.2794e-05 | 1.6201e-05 | 0.058169 | 0.058169 | 0.058169 | 0.98635 | -0.095365 | 0.98522 | -0.10336 | 21.5439
14 | 0.02363 | 0.0059511 | -0.023546 | -0.0059243 | 8.3856e-05 | 2.6808e-05 | 0.035546 | 0.035548 | 0.035548 | 0.98949 | -0.073201 | 0.98587 | -0.098657 | 6.5829
15 | 0.0068236 | 0.0017095 | -0.0068228 | -0.0017093 | 8.2566e-07 | 1.5617e-07 | 0.010261 | 0.010261 | 0.010261 | 0.98949 | -0.073201 | 0.98936 | -0.074076 | 3.8005
16 | 0.035302 | 0.0088597 | -0.035265 | -0.0088456 | 3.7483e-05 | 1.4148e-05 | 0.053323 | 0.053323 | 0.053323 | 0.98522 | -0.10336 | 0.98414 | -0.11102 | 19.7493
17 | 0.0014902 | 0.00037285 | -0.0014901 | -0.00037307 | 5.8321e-08 | -2.1654e-07 | 0.002241 | 0.0022411 | 0.0022411 | 0.98936 | -0.074076 | 0.98932 | -0.074359 | 0.83003
18 | 0.0014901 | 0.00037307 | -0.0014901 | -0.00037311 | 9.9193e-09 | -3.6825e-08 | 0.0022411 | 0.0022411 | 0.0022411 | 0.98932 | -0.074359 | 0.98932 | -0.074408 | 0.83004
19 | 0.0014901 | 0.00037311 | -0.00149 | -0.00037343 | 8.7566e-08 | -3.2504e-07 | 0.0022411 | 0.0022412 | 0.0022412 | 0.98932 | -0.074408 | 0.98926 | -0.074833 | 0.83009
20 | 0.023546 | 0.0059243 | -0.02352 | -0.0059146 | 2.6113e-05 | 9.6218e-06 | 0.035548 | 0.035548 | 0.035548 | 0.98587 | -0.098657 | 0.98474 | -0.10661 | 13.1659
21 | 0.02265 | 0.0056965 | -0.022512 | -0.005646 | 0.00013734 | 5.0449e-05 | 0.034232 | 0.034233 | 0.034233 | 0.98474 | -0.10661 | 0.97858 | -0.15036 | 12.679
22 | -0.0080442 | -0.002013 | 0.0080467 | 0.0020137 | 2.5467e-06 | 6.4386e-07 | 0.012296 | 0.012296 | 0.012296 | 0.97339 | -0.18763 | 0.97371 | -0.18534 | 4.5541
23 | 0.0077804 | 0.0019469 | -0.0077799 | -0.0019468 | 4.7214e-07 | 1.151e-07 | 0.011893 | 0.011893 | 0.011893 | 0.97339 | -0.18763 | 0.97333 | -0.18807 | 4.4048
24 | -0.0086148 | -0.002156 | 0.0086168 | 0.0021566 | 2.0406e-06 | 5.5007e-07 | 0.013164 | 0.013164 | 0.013164 | 0.97371 | -0.18534 | 0.97394 | -0.18363 | 4.8756
25 | 0.0040961 | 0.0010254 | -0.0040946 | -0.0010256 | 1.4646e-06 | -1.8041e-07 | 0.0062616 | 0.0062619 | 0.0062619 | 0.97333 | -0.18807 | 0.97297 | -0.19066 | 2.3192
26 | 0.0036839 | 0.00092141 | -0.0036813 | -0.00092204 | 2.6043e-06 | -6.3279e-07 | 0.0056312 | 0.0056318 | 0.0056318 | 0.97333 | -0.18807 | 0.97262 | -0.1932 | 2.0858
27 | -0.0089125 | -0.0022307 | 0.0089135 | 0.0022309 | 9.6502e-07 | 2.6734e-07 | 0.013616 | 0.013616 | 0.013616 | 0.97394 | -0.18363 | 0.97405 | -0.18284 | 5.0428
28 | 0.0035488 | 0.00088877 | -0.0035486 | -0.00088883 | 2.0855e-07 | -6.0703e-08 | 0.0054272 | 0.0054272 | 0.0054272 | 0.97297 | -0.19066 | 0.97291 | -0.19109 | 2.0101
29 | 0.0015834 | 0.00039628 | -0.0015833 | -0.00039681 | 1.747e-07 | -5.2486e-07 | 0.0024223 | 0.0024225 | 0.0024225 | 0.97262 | -0.1932 | 0.97251 | -0.19399 | 0.89724
30 | -0.0095133 | -0.0023813 | 0.0095183 | 0.0023827 | 5.0097e-06 | 1.4533e-06 | 0.014532 | 0.014532 | 0.014532 | 0.97405 | -0.18284 | 0.97458 | -0.17903 | 5.3822
31 | 0.0030591 | 0.00076616 | -0.0030587 | -0.00076636 | 3.9716e-07 | -2.0827e-07 | 0.0046786 | 0.0046787 | 0.0046787 | 0.97291 | -0.19109 | 0.97278 | -0.19203 | 1.7329
32 | -0.010242 | -0.0025641 | 0.010245 | 0.0025651 | 3.1835e-06 | 9.6434e-07 | 0.015637 | 0.015637 | 0.015637 | 0.97458 | -0.17903 | 0.97489 | -0.17678 | 5.7915
33 | 0.00095967 | 0.00024029 | -0.00095965 | -0.00024051 | 2.4786e-08 | -2.1931e-07 | 0.0014679 | 0.001468 | 0.001468 | 0.97278 | -0.19203 | 0.97275 | -0.19221 | 0.54369
34 | -0.0022208 | -0.00055658 | 0.002221 | 0.0005563 | 2.1245e-07 | -2.8468e-07 | 0.0033969 | 0.0033968 | 0.0033969 | 0.97282 | -0.19172 | 0.97292 | -0.19103 | 1.2581
35 | 0.0048462 | 0.0012141 | -0.0048452 | -0.0012141 | 1.0336e-06 | 2.319e-08 | 0.0074118 | 0.007412 | 0.007412 | 0.97292 | -0.19103 | 0.9727 | -0.19258 | 2.7452
36 | -0.0081373 | -0.0020375 | 0.0081523 | 0.0020413 | 1.496e-05 | 3.8278e-06 | 0.012445 | 0.012444 | 0.012445 | 0.97292 | -0.19103 | 0.97476 | -0.17774 | 4.6092
37 | 0.0010701 | 0.00026712 | -0.0010699 | -0.00026815 | 1.4648e-07 | -1.0321e-06 | 0.0016363 | 0.0016366 | 0.0016366 | 0.97292 | -0.19103 | 0.97278 | -0.19203 | 0.60616
38 | 0.0031022 | 0.00077722 | -0.0031019 | -0.0007774 | 3.5396e-07 | -1.7647e-07 | 0.0047456 | 0.0047457 | 0.0047457 | 0.9727 | -0.19258 | 0.97259 | -0.1934 | 1.7577
39 | -0.008696 | -0.0021776 | 0.0086972 | 0.0021779 | 1.1559e-06 | 3.1351e-07 | 0.013274 | 0.013274 | 0.013274 | 0.97476 | -0.17774 | 0.97489 | -0.17678 | 4.9164
40 | -0.018943 | -0.004743 | 0.018951 | 0.0047462 | 8.7015e-06 | 3.1386e-06 | 0.028911 | 0.028911 | 0.028911 | 0.97489 | -0.17678 | 0.97536 | -0.17346 | 10.7078
41 | -0.021769 | -0.0054523 | 0.021838 | 0.0054778 | 6.9717e-05 | 2.5546e-05 | 0.033209 | 0.033209 | 0.033209 | 0.97536 | -0.17346 | 0.97858 | -0.15036 | 12.2998
42 | -0.0075346 | -0.0018884 | 0.007537 | 0.0018889 | 2.3967e-06 | 5.495e-07 | 0.011422 | 0.011422 | 0.011422 | 0.9816 | -0.12906 | 0.98193 | -0.12676 | 4.2303
43 | -0.025109 | -0.0062928 | 0.025133 | 0.0063017 | 2.3943e-05 | 8.8732e-06 | 0.03805 | 0.03805 | 0.03805 | 0.98193 | -0.12676 | 0.98289 | -0.11988 | 14.0926
44 | -0.029902 | -0.0074969 | 0.029939 | 0.0075107 | 3.6762e-05 | 1.3774e-05 | 0.04527 | 0.04527 | 0.04527 | 0.98289 | -0.11988 | 0.98414 | -0.11102 | 16.7666
45 | 0.00067382 | 0.00016818 | -0.00067379 | -0.00016887 | 3.6675e-08 | -6.8937e-07 | 0.0010244 | 0.0010246 | 0.0010246 | 0.97858 | -0.15036 | 0.97852 | -0.15076 | 0.37948

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.14641 | 0.036782

## res_load
| p_mw | q_mvar
0 | 0.055883 | 0.014006
1 | 0.0030024 | 0.00075247
2 | 0.0026037 | 0.00065255
3 | 0.0053013 | 0.0013286
4 | 0.0015843 | 0.00039707
5 | 0.00083326 | 0.00020883
6 | 0.0030728 | 0.00077013
7 | 0.0024164 | 0.0006056
8 | 0.0032083 | 0.00080407
9 | 0.0053326 | 0.0013365
10 | 0.00149 | 0.00037343
11 | 0.00087047 | 0.00021816
12 | 0.00026377 | 6.6107e-05
13 | 0.00056806 | 0.00014237
14 | 0.00029567 | 7.4101e-05
15 | 0.00054581 | 0.00013679
16 | 0.0020978 | 0.00052576
17 | 0.00059984 | 0.00015033
18 | 0.00048947 | 0.00012267
19 | 0.0015833 | 0.00039681
20 | 0.00072382 | 0.00018141
21 | 0.0020991 | 0.00052607
22 | 0.0022208 | 0.00055658
23 | 0.001743 | 0.00043683
24 | 0.00054378 | 0.00013628
25 | 0.0010699 | 0.00026815
26 | 0.0031019 | 0.0007774
27 | 0.0028175 | 0.00070614
28 | 0.00095965 | 0.00024051
29 | 0.0075346 | 0.0018884
30 | 0.017572 | 0.0044039
31 | 0.004769 | 0.0011952
32 | 0.0053263 | 0.0013349
33 | 0.00067379 | 0.00016887

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1