## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1367-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1367-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1367-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1367-1_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1367-1_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1367-1_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1367-1_0_2_node_98 | 0.4 | n |  | TRUE
7 | bus_LV_1367-1_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1367-1_0_2_node_99 | 0.4 | n |  | TRUE
9 | bus_LV_1367-1_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1367-1_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1367-1_0_2_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1367-1_0_2_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1367-1_0_2_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_1367-1_0_2_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_1367-1_0_2_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1367-1_0_2_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_1367-1_0_2_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1367-1_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1367-1_0_2_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1367-1_0_2_node_58 | 0.4 | n |  | TRUE
21 | bus_LV_1367-1_0_2_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_1367-1_0_2_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1367-1_0_2_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1367-1_0_2_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1367-1_0_2_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1367-1_0_2_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1367-1_0_2_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_1367-1_0_2_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_1367-1_0_2_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1367-1_0_2_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1367-1_0_2_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1367-1_0_2_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1367-1_0_2_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1367-1_0_2_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_1367-1_0_2_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1367-1_0_2_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1367-1_0_2_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_1367-1_0_2_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_1367-1_0_2_node_89 | 0.4 | n |  | TRUE
40 | bus_LV_1367-1_0_2_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_1367-1_0_2_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1367-1_0_2_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_1367-1_0_2_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_1367-1_0_2_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_1367-1_0_2_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_1367-1_0_2_node_71 | 0.4 | n |  | TRUE
47 | bus_LV_1367-1_0_2_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_1367-1_0_2_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_1367-1_0_2_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_1367-1_0_2_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_1367-1_0_2_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_1367-1_0_2_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1367-1_0_2_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_1367-1_0_2_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_1367-1_0_2_node_64 | 0.4 | n |  | TRUE
56 | bus_LV_1367-1_0_2_node_84 | 0.4 | n |  | TRUE
57 | bus_LV_1367-1_0_2_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_1367-1_0_2_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_1367-1_0_2_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_1367-1_0_2_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_1367-1_0_2_node_95 | 0.4 | n |  | TRUE
62 | bus_LV_1367-1_0_2_node_96 | 0.4 | n |  | TRUE
63 | bus_LV_1367-1_0_2_node_97 | 0.4 | n |  | TRUE
64 | bus_LV_1367-1_0_2_node_100 | 0.4 | n |  | TRUE
65 | bus_MV_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1367-1_0_2_load_0 | 0 | 0.0028974 | 0.00072615 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1367-1_0_2_load_1 | 1 | 0.0019011 | 0.00047646 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1367-1_0_2_load_2 | 2 | 0.0011504 | 0.00028831 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1367-1_0_2_load_3 | 3 | 0.0017075 | 0.00042795 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1367-1_0_2_load_5 | 5 | 0.0013511 | 0.00033862 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1367-1_0_2_load_98 | 6 | 0.00096059 | 0.00024075 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1367-1_0_2_load_12 | 12 | 0.00065633 | 0.00016449 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1367-1_0_2_load_22 | 13 | 0.00037938 | 9.5083e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1367-1_0_2_load_19 | 14 | 0.0013439 | 0.00033682 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1367-1_0_2_load_20 | 15 | 0.00068343 | 0.00017128 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1367-1_0_2_load_16 | 16 | 0.00066247 | 0.00016603 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1367-1_0_2_load_23 | 17 | 0.0016707 | 0.00041871 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1367-1_0_2_load_9 | 18 | 8.9039e-05 | 2.2315e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1367-1_0_2_load_58 | 20 | 0.00026398 | 6.616e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1367-1_0_2_load_57 | 21 | 6.8259e-05 | 1.7107e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1367-1_0_2_load_21 | 22 | 0.001873 | 0.00046941 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1367-1_0_2_load_14 | 23 | 0.00079803 | 0.0002 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1367-1_0_2_load_13 | 24 | 0.00089328 | 0.00022388 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1367-1_0_2_load_17 | 26 | 0.00054986 | 0.00013781 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1367-1_0_2_load_38 | 27 | 9.3181e-05 | 2.3353e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1367-1_0_2_load_37 | 28 | 8.9682e-05 | 2.2476e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1367-1_0_2_load_24 | 29 | 0.0026457 | 0.00066307 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1367-1_0_2_load_27 | 32 | 0.00056816 | 0.0001424 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1367-1_0_2_load_28 | 33 | 0.00058287 | 0.00014608 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1367-1_0_2_load_31 | 36 | 0.00046063 | 0.00011545 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1367-1_0_2_load_34 | 37 | 0.00047071 | 0.00011797 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1367-1_0_2_load_89 | 39 | 0.00023947 | 6.0018e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1367-1_0_2_load_30 | 40 | 0.0003421 | 8.5739e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1367-1_0_2_load_36 | 41 | 0.0016573 | 0.00041537 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1367-1_0_2_load_32 | 42 | 0.0024101 | 0.00060402 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1367-1_0_2_load_41 | 43 | 0.00013885 | 3.4799e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1367-1_0_2_load_43 | 45 | 0.00037533 | 9.4066e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1367-1_0_2_load_71 | 46 | 0.00054993 | 0.00013783 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1367-1_0_2_load_45 | 47 | 0.00026807 | 6.7186e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1367-1_0_2_load_44 | 48 | 9.714e-05 | 2.4346e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1367-1_0_2_load_46 | 49 | 0.00013386 | 3.3548e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1367-1_0_2_load_49 | 50 | 0.00012421 | 3.1129e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1367-1_0_2_load_50 | 51 | 0.00020821 | 5.2182e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1367-1_0_2_load_47 | 52 | 0.00028237 | 7.0768e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1367-1_0_2_load_51 | 53 | 0.00025225 | 6.322e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1367-1_0_2_load_52 | 54 | 0.00022314 | 5.5925e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1367-1_0_2_load_64 | 55 | 0.00048074 | 0.00012048 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1367-1_0_2_load_84 | 56 | 0.00021433 | 5.3716e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1367-1_0_2_load_53 | 57 | 0.0001167 | 2.9248e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1367-1_0_2_load_54 | 58 | 0.00024626 | 6.1719e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1367-1_0_2_load_55 | 59 | 8.895e-05 | 2.2293e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1367-1_0_2_load_95 | 61 | 0.00019323 | 4.8429e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1367-1_0_2_load_97 | 63 | 0.00051679 | 0.00012952 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1367-1_0_2_load_100 | 64 | 0.0020749 | 0.00052002 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1367-1_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0020813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1367-1_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.020993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1367-1_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.01668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1367-1_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.12921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1367-1_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0077644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1367-1_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.67863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1367-1_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.033101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1367-1_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.5253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1367-1_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.038509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1367-1_0_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.11812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1367-1_0_2_line_10 | NAYY 4x150 SE | 8 | 64 | 0.018475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1367-1_0_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.031711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1367-1_0_2_line_12 | NAYY 4x150 SE | 9 | 12 | 0.079835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1367-1_0_2_line_13 | NAYY 4x150 SE | 10 | 13 | 0.20984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1367-1_0_2_line_14 | NAYY 4x150 SE | 11 | 14 | 0.064293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1367-1_0_2_line_15 | NAYY 4x150 SE | 11 | 15 | 0.046578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1367-1_0_2_line_16 | NAYY 4x150 SE | 12 | 16 | 0.033856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1367-1_0_2_line_17 | NAYY 4x150 SE | 13 | 17 | 0.10033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1367-1_0_2_line_18 | NAYY 4x150 SE | 15 | 22 | 0.010202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1367-1_0_2_line_19 | NAYY 4x150 SE | 16 | 23 | 0.010232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1367-1_0_2_line_20 | NAYY 4x150 SE | 17 | 29 | 0.033247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1367-1_0_2_line_21 | NAYY 4x150 SE | 18 | 19 | 0.012848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1367-1_0_2_line_22 | NAYY 4x150 SE | 19 | 20 | 0.0039634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1367-1_0_2_line_23 | NAYY 4x150 SE | 20 | 21 | 0.0078284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1367-1_0_2_line_24 | NAYY 4x150 SE | 21 | 60 | 0.027892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1367-1_0_2_line_25 | NAYY 4x150 SE | 23 | 24 | 0.014973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1367-1_0_2_line_26 | NAYY 4x150 SE | 24 | 25 | 0.0067683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1367-1_0_2_line_27 | NAYY 4x150 SE | 25 | 26 | 0.10351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1367-1_0_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.24186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1367-1_0_2_line_29 | NAYY 4x150 SE | 27 | 28 | 0.20612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1367-1_0_2_line_30 | NAYY 4x150 SE | 28 | 43 | 0.17708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1367-1_0_2_line_31 | NAYY 4x150 SE | 29 | 30 | 0.089303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1367-1_0_2_line_32 | NAYY 4x150 SE | 30 | 31 | 0.094074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1367-1_0_2_line_33 | NAYY 4x150 SE | 30 | 32 | 0.037448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1367-1_0_2_line_34 | NAYY 4x150 SE | 31 | 33 | 0.094549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1367-1_0_2_line_35 | NAYY 4x150 SE | 31 | 34 | 0.35028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1367-1_0_2_line_36 | NAYY 4x150 SE | 32 | 35 | 0.23702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1367-1_0_2_line_37 | NAYY 4x150 SE | 33 | 36 | 0.025516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1367-1_0_2_line_38 | NAYY 4x150 SE | 34 | 37 | 0.068992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1367-1_0_2_line_39 | NAYY 4x150 SE | 35 | 39 | 0.046151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1367-1_0_2_line_40 | NAYY 4x150 SE | 36 | 40 | 0.0039368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1367-1_0_2_line_41 | NAYY 4x150 SE | 37 | 38 | 0.054502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1367-1_0_2_line_42 | NAYY 4x150 SE | 38 | 41 | 0.00663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1367-1_0_2_line_43 | NAYY 4x150 SE | 40 | 42 | 0.017544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1367-1_0_2_line_44 | NAYY 4x150 SE | 43 | 44 | 0.10223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1367-1_0_2_line_45 | NAYY 4x150 SE | 43 | 45 | 0.41833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1367-1_0_2_line_46 | NAYY 4x150 SE | 43 | 46 | 0.37657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1367-1_0_2_line_47 | NAYY 4x150 SE | 44 | 47 | 0.021976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1367-1_0_2_line_48 | NAYY 4x150 SE | 45 | 48 | 0.086275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1367-1_0_2_line_49 | NAYY 4x150 SE | 47 | 49 | 0.022607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1367-1_0_2_line_50 | NAYY 4x150 SE | 49 | 50 | 0.017476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1367-1_0_2_line_51 | NAYY 4x150 SE | 50 | 51 | 0.016296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1367-1_0_2_line_52 | NAYY 4x150 SE | 51 | 53 | 0.029881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1367-1_0_2_line_53 | NAYY 4x150 SE | 52 | 53 | 0.23833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1367-1_0_2_line_54 | NAYY 4x150 SE | 53 | 54 | 0.08459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1367-1_0_2_line_55 | NAYY 4x150 SE | 53 | 55 | 0.40031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1367-1_0_2_line_56 | NAYY 4x150 SE | 53 | 56 | 0.44735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1367-1_0_2_line_57 | NAYY 4x150 SE | 54 | 57 | 0.024828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1367-1_0_2_line_58 | NAYY 4x150 SE | 57 | 58 | 0.11388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1367-1_0_2_line_59 | NAYY 4x150 SE | 58 | 59 | 0.011903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1367-1_0_2_line_60 | NAYY 4x150 SE | 59 | 60 | 0.026783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1367-1_0_2_line_61 | NAYY 4x150 SE | 61 | 62 | 0.30918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1367-1_0_2_line_62 | NAYY 4x150 SE | 62 | 63 | 0.01345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1367-1_0_2_line_63 | NAYY 4x150 SE | 62 | 64 | 0.63884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1367-1_0_2_trafo_8 | 0.25 MVA 20/0.4 kV | 65 | 10 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2705971.6552 | 1199953.8023 | 2705970.9914 | 1199955.7749
1 | 2705971.6552 | 1199953.8023 | 2705972.7515 | 1199950.5449 | 2705977.1353 | 1199942.9619 | 2705982.3165 | 1199935.852
2 | 2705967.78 | 1199972.0944 | 2705967.8563 | 1199971.506 | 2705969.6566 | 1199959.7409 | 2705970.9914 | 1199955.7749
3 | 2706020.858 | 1199866.7623 | 2706032.2143 | 1199861.9271 | 2706038.4142 | 1199861.4367 | 2706042.9852 | 1199863.0412 | 2706044.7433 | 1199864.818 | 2706046.0044 | 1199867.987 | 2706047.2806 | 1199872.0236 | 2706047.4327 | 1199875.0395 | 2706046.3958 | 1199878.9682 | 2706043.9081 | 1199882.6933 | 2706037.7394 | 1199886.5755 | 2706023.9088 | 1199891.3779 | 2706015.8834 | 1199894.7601 | 2706010.4689 | 1199898.1998 | 2705996.4313 | 1199915.5295 | 2705987.4302 | 1199928.8346 | 2705982.3165 | 1199935.852
4 | 2705967.78 | 1199972.0944 | 2705966.7814 | 1199979.7943
5 | 2706020.858 | 1199866.7623 | 2705486.324 | 1199448.6582
6 | 2705959.7902 | 1200011.9577 | 2705964.8627 | 1199996.8816 | 2705966.7183 | 1199980.2808 | 2705966.7814 | 1199979.7943
7 | 2705154.9799 | 1199856.2702 | 2705486.324 | 1199448.6582
8 | 2705959.7902 | 1200011.9577 | 2705963.5555 | 1200015.1933 | 2705969.709 | 1200020.7396 | 2705976.3697 | 1200029.8862 | 2705980.6186 | 1200043.2041
9 | 2705891.2382 | 1200097.1128 | 2705921.7137 | 1200089.3363 | 2705942.0977 | 1200052.9057 | 2705950.7606 | 1200026.4521 | 2705955.557 | 1200019.2099 | 2705959.7902 | 1200011.9577
10 | 2705153.2325 | 1199874.641 | 2705154.4585 | 1199865.9899 | 2705154.9799 | 1199856.2702
11 | 2705980.6186 | 1200043.2041 | 2705988.7404 | 1200073.8582
12 | 2705980.6186 | 1200043.2041 | 2705991.9429 | 1200036.289 | 2706000.2707 | 1200025.7294 | 2706013.6991 | 1200010.9574 | 2706036.5311 | 1199992.3828 | 2706039.955 | 1199990.9237
13 | 2705891.2382 | 1200097.1128 | 2705893.1775 | 1200117.439 | 2705887.2836 | 1200127.3192 | 2705879.0322 | 1200147.7649 | 2705855.4873 | 1200157.6436 | 2705849.1079 | 1200163.5569 | 2705844.9687 | 1200175.8366 | 2705835.6746 | 1200196.6975 | 2705826.8805 | 1200213.8315 | 2705800.5636 | 1200274.9961
14 | 2705988.7404 | 1200073.8582 | 2705997.3429 | 1200080.4265 | 2706009.619 | 1200085.5255 | 2706021.907 | 1200085.2321 | 2706034.2359 | 1200081.3482 | 2706045.4869 | 1200071.2741
15 | 2705988.7404 | 1200073.8582 | 2706001.9347 | 1200111.3182 | 2706007.7906 | 1200114.8963
16 | 2706039.955 | 1199990.9237 | 2706042.2169 | 1199989.9598 | 2706049.4083 | 1199987.6525 | 2706057.1656 | 1199987.7902 | 2706066.9491 | 1199989.1759 | 2706072.0206 | 1199990.9004 | 2706072.7726 | 1199991.2924
17 | 2705800.5636 | 1200274.9961 | 2705800.5539 | 1200275.0188 | 2705792.3982 | 1200290.0849 | 2705777.2542 | 1200308.0626 | 2705770.9349 | 1200319.6254 | 2705758.7992 | 1200364.4991
18 | 2706016.4963 | 1200120.2159 | 2706007.7906 | 1200114.8963
19 | 2706082.3053 | 1199993.6604 | 2706078.0944 | 1199994.066 | 2706072.7726 | 1199991.2924
20 | 2705758.7992 | 1200364.4991 | 2705758.4765 | 1200365.6924 | 2705737.5392 | 1200389.9069
21 | 2706308.2094 | 1199544.1094 | 2706306.4476 | 1199549.3928 | 2706303.1023 | 1199552.5022 | 2706300.5983 | 1199553.5418
22 | 2706308.2094 | 1199544.1094 | 2706311.1097 | 1199542.0373 | 2706311.4111 | 1199541.776
23 | 2706317.3257 | 1199536.6475 | 2706311.4111 | 1199541.776
24 | 2706330.8144 | 1199513.6237 | 2706331.0384 | 1199519.0092 | 2706328.5554 | 1199523.735 | 2706323.8452 | 1199529.9332 | 2706319.9431 | 1199534.378 | 2706317.3257 | 1199536.6475
25 | 2706082.3053 | 1199993.6604 | 2706085.1122 | 1199993.39 | 2706089.0061 | 1199988.9561 | 2706092.3081 | 1199983.647
26 | 2706096.6084 | 1199978.5283 | 2706094.266 | 1199980.4992 | 2706092.3081 | 1199983.647
27 | 2706096.6084 | 1199978.5283 | 2706099.2146 | 1199981.421 | 2706102.1745 | 1199983.6973 | 2706109.3183 | 1199987.5045 | 2706114.3328 | 1199989.0057 | 2706119.8049 | 1199991.7492 | 2706125.9028 | 1199996.5608 | 2706127.4067 | 1200000.6348 | 2706128.7691 | 1200004.5283 | 2706130.6276 | 1200006.2181 | 2706134.3556 | 1200003.8382 | 2706138.1012 | 1200000.0354 | 2706142.0122 | 1199998.0701 | 2706144.9396 | 1200002.1694 | 2706145.6895 | 1200006.2522 | 2706149.9716 | 1200006.5396 | 2706159.6245 | 1200007.1337 | 2706171.9556 | 1200009.5655 | 2706176.6723 | 1200015.8122
28 | 2706176.6723 | 1200015.8122 | 2706366.2864 | 1199865.6765
29 | 2706514.8767 | 1199724.5914 | 2706493.4054 | 1199749.9931 | 2706475.3583 | 1199764.4483 | 2706429.7649 | 1199796.9588 | 2706400.7163 | 1199824.116 | 2706366.2864 | 1199865.6765
30 | 2706578.9046 | 1199559.4878 | 2706514.8767 | 1199724.5914
31 | 2705698.3458 | 1200458.9932 | 2705691.9931 | 1200452.6654 | 2705692.8181 | 1200440.4716 | 2705700.6214 | 1200426.3553 | 2705714.911 | 1200410.1635 | 2705736.0727 | 1200391.6028 | 2705737.5392 | 1200389.9069
32 | 2705693.5304 | 1200547.3692 | 2705697.581 | 1200540.9253 | 2705699.568 | 1200531.9098 | 2705699.5486 | 1200521.8247 | 2705690.9286 | 1200499.479 | 2705688.1341 | 1200486.1425 | 2705688.5928 | 1200477.4335 | 2705698.3458 | 1200458.9932
33 | 2705698.3458 | 1200458.9932 | 2705721.9552 | 1200439.7975 | 2705728.8679 | 1200438.5745
34 | 2705693.5304 | 1200547.3692 | 2705707.0193 | 1200547.5746 | 2705726.4259 | 1200551.9987 | 2705774.8405 | 1200569.4564 | 2705783.9494 | 1200568.4725 | 2705784.4123 | 1200568.223
35 | 2705693.5304 | 1200547.3692 | 2705576.7371 | 1200877.6001
36 | 2705954.9056 | 1200425.5018 | 2705921.3025 | 1200428.108 | 2705883.4293 | 1200432.7735 | 2705865.8467 | 1200433.6849 | 2705859.6797 | 1200430.2065 | 2705847.2597 | 1200425.5278 | 2705838.8301 | 1200422.9767 | 2705829.1798 | 1200423.5618 | 2705813.4456 | 1200426.2962 | 2705791.7709 | 1200430.3931 | 2705779.0471 | 1200445.445 | 2705773.6312 | 1200446.4165 | 2705756.4373 | 1200444.2996 | 2705728.8679 | 1200438.5745
37 | 2705784.4123 | 1200568.223 | 2705800.7084 | 1200559.4407 | 2705804.9839 | 1200553.8925
38 | 2705576.7371 | 1200877.6001 | 2705593.1437 | 1200885.8512 | 2705608.6094 | 1200896.0761 | 2705635.8234 | 1200913.0765
39 | 2705954.9056 | 1200425.5018 | 2705999.0876 | 1200412.1644
40 | 2705807.3869 | 1200550.7741 | 2705804.9839 | 1200553.8925
41 | 2705679.7981 | 1200944.3013 | 2705675.2852 | 1200937.728 | 2705635.8234 | 1200913.0765
42 | 2705683.5538 | 1200949.7715 | 2705679.7981 | 1200944.3013
43 | 2705818.0957 | 1200536.8773 | 2705807.3869 | 1200550.7741
44 | 2706513.191 | 1199494.1239 | 2706523.0252 | 1199526.0212 | 2706526.54 | 1199535.1902 | 2706530.1876 | 1199540.7591 | 2706535.5988 | 1199544.3691 | 2706561.0362 | 1199553.262 | 2706578.9046 | 1199559.4878
45 | 2706578.9046 | 1199559.4878 | 2706956.0709 | 1199740.4406
46 | 2706578.9046 | 1199559.4878 | 2706879.8939 | 1199333.1911
47 | 2706513.191 | 1199494.1239 | 2706503.9831 | 1199475.7915 | 2706503.6949 | 1199474.3588
48 | 2706956.0709 | 1199740.4406 | 2706957.2183 | 1199738.9225 | 2706960.752 | 1199736.3617 | 2706965.373 | 1199734.7433 | 2706970.0698 | 1199734.8497 | 2706977.9073 | 1199736.4799 | 2707021.0329 | 1199751.3734 | 2707037.1222 | 1199756.1521
49 | 2706503.6949 | 1199474.3588 | 2706499.2367 | 1199452.1956
50 | 2706499.2367 | 1199452.1956 | 2706496.064 | 1199436.4232 | 2706495.983 | 1199435.0376
51 | 2706495.983 | 1199435.0376 | 2706495.0317 | 1199418.7694
52 | 2706495.0317 | 1199418.7694 | 2706493.2874 | 1199388.9396
53 | 2706493.2874 | 1199388.9396 | 2706586.5846 | 1199169.6288
54 | 2706493.2874 | 1199388.9396 | 2706492.8482 | 1199381.4278 | 2706481.2819 | 1199362.5086 | 2706467.1817 | 1199353.7181 | 2706454.3366 | 1199355.7018 | 2706443.5712 | 1199364.4828 | 2706438.2313 | 1199374.5381
55 | 2706493.2874 | 1199388.9396 | 2706819.0831 | 1199156.3259
56 | 2706493.2874 | 1199388.9396 | 2706590.8882 | 1198952.367
57 | 2706438.2313 | 1199374.5381 | 2706434.8557 | 1199380.8945 | 2706426.7681 | 1199396.5614
58 | 2706426.7681 | 1199396.5614 | 2706422.1954 | 1199405.4194 | 2706408.9773 | 1199425.3535 | 2706398.9494 | 1199440.63 | 2706375.117 | 1199471.1492 | 2706362.1632 | 1199484.3834 | 2706358.8795 | 1199487.4288
59 | 2706358.8795 | 1199487.4288 | 2706350.7415 | 1199494.9764 | 2706350.2059 | 1199495.5758
60 | 2706330.8144 | 1199513.6237 | 2706337.384 | 1199509.9269 | 2706342.0385 | 1199504.7172 | 2706350.2059 | 1199495.5758
61 | 2704710.6379 | 1200335.3215 | 2704643.0725 | 1200289.7957 | 2704604.8933 | 1200212.8299 | 2704570.3825 | 1200167.2279 | 2704513.4749 | 1200104.6252
62 | 2704710.6379 | 1200335.3215 | 2704707.8491 | 1200348.4797
63 | 2704710.6379 | 1200335.3215 | 2705153.2325 | 1199874.641

## bus_geodata
| x | y | coords
0 | 2705971.6552 | 1199953.8023
1 | 2705970.9914 | 1199955.7749
2 | 2705982.3165 | 1199935.852
3 | 2705967.78 | 1199972.0944
4 | 2706020.858 | 1199866.7623
5 | 2705966.7814 | 1199979.7943
6 | 2705486.324 | 1199448.6582
7 | 2705959.7902 | 1200011.9577
8 | 2705154.9799 | 1199856.2702
9 | 2705980.6186 | 1200043.2041
10 | 2705891.2382 | 1200097.1128
11 | 2705988.7404 | 1200073.8582
12 | 2706039.955 | 1199990.9237
13 | 2705800.5637 | 1200274.9961
14 | 2706045.4869 | 1200071.2741
15 | 2706007.7906 | 1200114.8963
16 | 2706072.7726 | 1199991.2924
17 | 2705758.7992 | 1200364.4991
18 | 2706300.5983 | 1199553.5418
19 | 2706308.2094 | 1199544.1094
20 | 2706311.4111 | 1199541.776
21 | 2706317.3257 | 1199536.6475
22 | 2706016.4963 | 1200120.2159
23 | 2706082.3053 | 1199993.6604
24 | 2706092.3081 | 1199983.647
25 | 2706096.6084 | 1199978.5283
26 | 2706176.6723 | 1200015.8122
27 | 2706366.2864 | 1199865.6765
28 | 2706514.8767 | 1199724.5914
29 | 2705737.5392 | 1200389.9069
30 | 2705698.3458 | 1200458.9932
31 | 2705693.5304 | 1200547.3692
32 | 2705728.8679 | 1200438.5745
33 | 2705784.4123 | 1200568.223
34 | 2705576.7371 | 1200877.6001
35 | 2705954.9056 | 1200425.5018
36 | 2705804.9839 | 1200553.8925
37 | 2705635.8233 | 1200913.0765
38 | 2705679.7981 | 1200944.3013
39 | 2705999.0876 | 1200412.1644
40 | 2705807.3869 | 1200550.7741
41 | 2705683.5538 | 1200949.7715
42 | 2705818.0957 | 1200536.8773
43 | 2706578.9046 | 1199559.4878
44 | 2706513.191 | 1199494.1239
45 | 2706956.0709 | 1199740.4406
46 | 2706879.8939 | 1199333.1911
47 | 2706503.6949 | 1199474.3588
48 | 2707037.1222 | 1199756.1521
49 | 2706499.2367 | 1199452.1956
50 | 2706495.983 | 1199435.0376
51 | 2706495.0317 | 1199418.7694
52 | 2706586.5846 | 1199169.6288
53 | 2706493.2874 | 1199388.9396
54 | 2706438.2313 | 1199374.5381
55 | 2706819.0831 | 1199156.3259
56 | 2706590.8882 | 1198952.367
57 | 2706426.7681 | 1199396.5614
58 | 2706358.8795 | 1199487.4288
59 | 2706350.2059 | 1199495.5758
60 | 2706330.8144 | 1199513.6237
61 | 2704513.4749 | 1200104.6252
62 | 2704710.6379 | 1200335.3215
63 | 2704707.8491 | 1200348.4797
64 | 2705153.2325 | 1199874.641
65 | 2705891.2382 | 1200097.1128

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99484 | -0.036898 | 0.0028974 | 0.00072615
1 | 0.99486 | -0.03673 | 0.0019011 | 0.00047646
2 | 0.99469 | -0.037982 | 0.0011504 | 0.00028831
3 | 0.9951 | -0.035062 | 0.0017075 | 0.00042795
4 | 0.994 | -0.043148 | 0 | 0
5 | 0.99522 | -0.034152 | 0.0013511 | 0.00033862
6 | 0.99034 | -0.070133 | 0.00096059 | 0.00024075
7 | 0.99583 | -0.029825 | 0 | 0
8 | 0.98823 | -0.085687 | 0 | 0
9 | 0.99517 | -0.034557 | 0 | 0
10 | 1 | 0 | -0.037098 | -0.0090341
11 | 0.995 | -0.035808 | 0 | 0
12 | 0.99426 | -0.041228 | 0.00065633 | 0.00016449
13 | 0.99656 | -0.024292 | 0.00037938 | 9.5083e-05
14 | 0.99487 | -0.036682 | 0.0013439 | 0.00033682
15 | 0.99483 | -0.03701 | 0.00068343 | 0.00017128
16 | 0.9939 | -0.043834 | 0.00066247 | 0.00016603
17 | 0.99497 | -0.035566 | 0.0016707 | 0.00041871
18 | 0.98781 | -0.089393 | 8.9039e-05 | 2.2315e-05
19 | 0.98781 | -0.089381 | 0 | 0
20 | 0.98781 | -0.089378 | 0.00026398 | 6.616e-05
21 | 0.98782 | -0.089349 | 6.8259e-05 | 1.7107e-05
22 | 0.9948 | -0.037203 | 0.001873 | 0.00046941
23 | 0.99381 | -0.044553 | 0.00079803 | 0.0002
24 | 0.99368 | -0.045485 | 0.00089328 | 0.00022388
25 | 0.99363 | -0.045845 | 0 | 0
26 | 0.9929 | -0.05135 | 0.00054986 | 0.00013781
27 | 0.99136 | -0.062854 | 9.3181e-05 | 2.3353e-05
28 | 0.99009 | -0.072446 | 8.9682e-05 | 2.2476e-05
29 | 0.99452 | -0.038747 | 0.0026457 | 0.00066307
30 | 0.99366 | -0.044912 | 0 | 0
31 | 0.99286 | -0.050611 | 0 | 0
32 | 0.99362 | -0.045229 | 0.00056816 | 0.0001424
33 | 0.99234 | -0.054255 | 0.00058287 | 0.00014608
34 | 0.99179 | -0.05827 | 0 | 0
35 | 0.99354 | -0.045841 | 0 | 0
36 | 0.99223 | -0.055087 | 0.00046063 | 0.00011545
37 | 0.99158 | -0.059767 | 0.00047071 | 0.00011797
38 | 0.99145 | -0.060685 | 0 | 0
39 | 0.99352 | -0.045954 | 0.00023947 | 6.0018e-05
40 | 0.99221 | -0.055197 | 0.0003421 | 8.5739e-05
41 | 0.99143 | -0.060797 | 0.0016573 | 0.00041537
42 | 0.99215 | -0.055625 | 0.0024101 | 0.00060402
43 | 0.98901 | -0.080511 | 0.00013885 | 3.4799e-05
44 | 0.98856 | -0.08386 | 0 | 0
45 | 0.98873 | -0.082649 | 0.00037533 | 9.4066e-05
46 | 0.98871 | -0.082694 | 0.00054993 | 0.00013783
47 | 0.98846 | -0.084579 | 0.00026807 | 6.7186e-05
48 | 0.98872 | -0.082738 | 9.714e-05 | 2.4346e-05
49 | 0.98837 | -0.085257 | 0.00013386 | 3.3548e-05
50 | 0.98831 | -0.085756 | 0.00012421 | 3.1129e-05
51 | 0.98825 | -0.086201 | 0.00020821 | 5.2182e-05
52 | 0.98805 | -0.087669 | 0.00028237 | 7.0768e-05
53 | 0.98815 | -0.086953 | 0.00025225 | 6.322e-05
54 | 0.98801 | -0.087923 | 0.00022314 | 5.5925e-05
55 | 0.98787 | -0.088999 | 0.00048074 | 0.00012048
56 | 0.98801 | -0.088031 | 0.00021433 | 5.3716e-05
57 | 0.98798 | -0.08815 | 0.0001167 | 2.9248e-05
58 | 0.98786 | -0.089048 | 0.00024626 | 6.1719e-05
59 | 0.98785 | -0.089111 | 8.895e-05 | 2.2293e-05
60 | 0.98783 | -0.089228 | 0 | 0
61 | 0.98742 | -0.091928 | 0.00019323 | 4.8429e-05
62 | 0.98751 | -0.09127 | 0 | 0
63 | 0.9875 | -0.091341 | 0.00051679 | 0.00012952
64 | 0.98816 | -0.08623 | 0.0020749 | 0.00052002
65 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0078163 | -0.0019321 | 0.0078165 | 0.0019321 | 1.7723e-07 | 4.114e-08 | 0.011682 | 0.011682 | 0.011682 | 0.99484 | -0.036898 | 0.99486 | -0.03673 | 4.3266
1 | 0.004919 | 0.0012059 | -0.0049183 | -0.0012059 | 7.0733e-07 | -4.9479e-10 | 0.0073481 | 0.0073482 | 0.0073482 | 0.99484 | -0.036898 | 0.99469 | -0.037982 | 2.7215
2 | -0.0097176 | -0.0024086 | 0.0097198 | 0.0024092 | 2.1959e-06 | 6.2795e-07 | 0.014525 | 0.014525 | 0.014525 | 0.99486 | -0.03673 | 0.9951 | -0.035062 | 5.3797
3 | 0.0037679 | 0.0009176 | -0.0037653 | -0.00091829 | 2.5535e-06 | -6.9396e-07 | 0.0056273 | 0.0056279 | 0.0056279 | 0.99469 | -0.037982 | 0.994 | -0.043148 | 2.0844
4 | -0.011427 | -0.0028371 | 0.011429 | 0.0028376 | 1.4132e-06 | 4.4264e-07 | 0.017078 | 0.017078 | 0.017078 | 0.9951 | -0.035062 | 0.99522 | -0.034152 | 6.3253
5 | 0.0037653 | 0.00091829 | -0.0037519 | -0.00092189 | 1.342e-05 | -3.6029e-06 | 0.0056279 | 0.0056309 | 0.0056309 | 0.994 | -0.043148 | 0.99034 | -0.070133 | 2.0855
6 | -0.01278 | -0.0031762 | 0.012787 | 0.0031787 | 7.534e-06 | 2.4673e-06 | 0.019099 | 0.019098 | 0.019099 | 0.99522 | -0.034152 | 0.99583 | -0.029825 | 7.0735
7 | 0.0027913 | 0.00068115 | -0.0027856 | -0.00068568 | 5.7513e-06 | -4.5326e-06 | 0.0041876 | 0.00419 | 0.00419 | 0.99034 | -0.070133 | 0.98823 | -0.085687 | 1.5518
8 | 0.011908 | 0.0029446 | -0.011901 | -0.0029421 | 7.5963e-06 | 2.421e-06 | 0.01778 | 0.01778 | 0.01778 | 0.99583 | -0.029825 | 0.99517 | -0.034557 | 6.5852
9 | -0.024696 | -0.0061232 | 0.024796 | 0.0061602 | 0.00010024 | 3.701e-05 | 0.036878 | 0.036878 | 0.036878 | 0.99583 | -0.029825 | 1 | 0 | 13.6586
10 | 0.0027856 | 0.00068568 | -0.0027854 | -0.00068584 | 2.0239e-07 | -1.5885e-07 | 0.00419 | 0.00419 | 0.00419 | 0.98823 | -0.085687 | 0.98816 | -0.08623 | 1.5519
11 | 0.0039016 | 0.00097603 | -0.003901 | -0.00097618 | 6.7332e-07 | -1.5298e-07 | 0.0058332 | 0.0058334 | 0.0058334 | 0.99517 | -0.034557 | 0.995 | -0.035808 | 2.1605
12 | 0.0079989 | 0.0019661 | -0.0079918 | -0.0019644 | 7.1104e-06 | 1.6984e-06 | 0.011947 | 0.011947 | 0.011947 | 0.99517 | -0.034557 | 0.99426 | -0.041228 | 4.4249
13 | 0.011502 | 0.0028738 | -0.011464 | -0.0028618 | 3.8348e-05 | 1.2006e-05 | 0.017113 | 0.017114 | 0.017114 | 1 | 0 | 0.99656 | -0.024292 | 6.3384
14 | 0.0013441 | 0.00033605 | -0.0013439 | -0.00033682 | 1.6208e-07 | -7.7262e-07 | 0.0020098 | 0.0020101 | 0.0020101 | 0.995 | -0.035808 | 0.99487 | -0.036682 | 0.74449
15 | 0.0025569 | 0.00064013 | -0.0025564 | -0.00064058 | 4.2494e-07 | -4.4143e-07 | 0.0038235 | 0.0038238 | 0.0038238 | 0.995 | -0.035808 | 0.99483 | -0.03701 | 1.4162
16 | 0.0073355 | 0.0017999 | -0.0073329 | -0.0017994 | 2.54e-06 | 5.3798e-07 | 0.010965 | 0.010965 | 0.010965 | 0.99426 | -0.041228 | 0.9939 | -0.043834 | 4.0611
17 | 0.011085 | 0.0027667 | -0.011068 | -0.0027614 | 1.7142e-05 | 5.2879e-06 | 0.016547 | 0.016548 | 0.016548 | 0.99656 | -0.024292 | 0.99497 | -0.035566 | 6.1287
18 | 0.001873 | 0.00046929 | -0.001873 | -0.00046941 | 4.9966e-08 | -1.1324e-07 | 0.0028015 | 0.0028016 | 0.0028016 | 0.99483 | -0.03701 | 0.9948 | -0.037203 | 1.0376
19 | 0.0066705 | 0.0016334 | -0.0066698 | -0.0016332 | 6.3504e-07 | 1.1166e-07 | 0.0099732 | 0.0099732 | 0.0099732 | 0.9939 | -0.043834 | 0.99381 | -0.044553 | 3.6938
20 | 0.0093969 | 0.0023427 | -0.0093928 | -0.0023416 | 4.0948e-06 | 1.1433e-06 | 0.014049 | 0.014049 | 0.014049 | 0.99497 | -0.035566 | 0.99452 | -0.038747 | 5.2034
21 | -8.9039e-05 | -2.2315e-05 | 8.9039e-05 | 2.2151e-05 | 1.4416e-10 | -1.6441e-07 | 0.00013413 | 0.00013407 | 0.00013413 | 0.98781 | -0.089393 | 0.98781 | -0.089381 | 0.049676
22 | -8.9039e-05 | -2.2151e-05 | 8.9039e-05 | 2.21e-05 | 4.4472e-11 | -5.072e-08 | 0.00013407 | 0.00013405 | 0.00013407 | 0.98781 | -0.089381 | 0.98781 | -0.089378 | 0.049655
23 | -0.00035302 | -8.826e-05 | 0.00035302 | 8.816e-05 | 1.3809e-09 | -9.9684e-08 | 0.00053171 | 0.00053167 | 0.00053171 | 0.98781 | -0.089378 | 0.98782 | -0.089349 | 0.19693
24 | -0.00042128 | -0.00010527 | 0.00042129 | 0.00010491 | 7.0055e-09 | -3.5438e-07 | 0.00063449 | 0.00063437 | 0.00063449 | 0.98782 | -0.089349 | 0.98783 | -0.089228 | 0.235
25 | 0.0058718 | 0.0014332 | -0.0058711 | -0.0014332 | 7.2e-07 | 8.2935e-08 | 0.0087784 | 0.0087785 | 0.0087785 | 0.99381 | -0.044553 | 0.99368 | -0.045485 | 3.2513
26 | 0.0049778 | 0.0012093 | -0.0049776 | -0.0012093 | 2.3383e-07 | 2.264e-09 | 0.0074408 | 0.0074409 | 0.0074409 | 0.99368 | -0.045485 | 0.99363 | -0.045845 | 2.7559
27 | 0.0049776 | 0.0012093 | -0.004974 | -0.0012092 | 3.5764e-06 | 3.5774e-08 | 0.0074409 | 0.0074413 | 0.0074413 | 0.99363 | -0.045845 | 0.9929 | -0.05135 | 2.756
28 | 0.0044241 | 0.0010714 | -0.0044175 | -0.001072 | 6.6095e-06 | -5.811e-07 | 0.0066173 | 0.0066184 | 0.0066184 | 0.9929 | -0.05135 | 0.99136 | -0.062854 | 2.4512
29 | 0.0043243 | 0.0010487 | -0.0043189 | -0.0010492 | 5.3989e-06 | -5.7766e-07 | 0.0064785 | 0.0064794 | 0.0064794 | 0.99136 | -0.062854 | 0.99009 | -0.072446 | 2.3998
30 | 0.0042293 | 0.0010268 | -0.0042248 | -0.0010273 | 4.4487e-06 | -5.6388e-07 | 0.0063446 | 0.0063454 | 0.0063454 | 0.99009 | -0.072446 | 0.98901 | -0.080511 | 2.3502
31 | 0.0067471 | 0.0016785 | -0.0067414 | -0.0016775 | 5.6743e-06 | 1.0246e-06 | 0.010091 | 0.010091 | 0.010091 | 0.99452 | -0.038747 | 0.99366 | -0.044912 | 3.7374
32 | 0.0059337 | 0.0014792 | -0.0059291 | -0.0014787 | 4.6323e-06 | 5.6404e-07 | 0.008883 | 0.0088834 | 0.0088834 | 0.99366 | -0.044912 | 0.99286 | -0.050611 | 3.2902
33 | 0.00080769 | 0.00019828 | -0.00080766 | -0.00019875 | 3.4109e-08 | -4.7195e-07 | 0.0012081 | 0.0012082 | 0.0012082 | 0.99366 | -0.044912 | 0.99362 | -0.045229 | 0.4475
34 | 0.0037981 | 0.0009504 | -0.0037962 | -0.00095089 | 1.9115e-06 | -4.8694e-07 | 0.0056918 | 0.0056922 | 0.0056922 | 0.99286 | -0.050611 | 0.99234 | -0.054255 | 2.1082
35 | 0.0021309 | 0.00052825 | -0.0021287 | -0.00053192 | 2.2276e-06 | -3.6683e-06 | 0.0031916 | 0.0031932 | 0.0031932 | 0.99286 | -0.050611 | 0.99179 | -0.05827 | 1.1827
36 | 0.0002395 | 5.6359e-05 | -0.00023948 | -5.9421e-05 | 1.8947e-08 | -3.0624e-06 | 0.00035741 | 0.00035845 | 0.00035845 | 0.99362 | -0.045229 | 0.99354 | -0.045841 | 0.13276
37 | 0.0032134 | 0.00080481 | -0.003213 | -0.000805 | 3.6965e-07 | -1.8744e-07 | 0.0048182 | 0.0048183 | 0.0048183 | 0.99234 | -0.054255 | 0.99223 | -0.055087 | 1.7846
38 | 0.0021287 | 0.00053192 | -0.0021283 | -0.00053264 | 4.3902e-07 | -7.2128e-07 | 0.0031932 | 0.0031935 | 0.0031935 | 0.99179 | -0.05827 | 0.99158 | -0.059767 | 1.1828
39 | 0.00023948 | 5.9421e-05 | -0.00023947 | -6.0018e-05 | 3.7024e-09 | -5.9623e-07 | 0.00035845 | 0.00035866 | 0.00035866 | 0.99354 | -0.045841 | 0.99352 | -0.045954 | 0.13284
40 | 0.0027524 | 0.00068955 | -0.0027523 | -0.00068959 | 4.1852e-08 | -3.4751e-08 | 0.0041275 | 0.0041276 | 0.0041276 | 0.99223 | -0.055087 | 0.99221 | -0.055197 | 1.5287
41 | 0.0016576 | 0.00041467 | -0.0016574 | -0.00041529 | 2.104e-07 | -6.2202e-07 | 0.0024872 | 0.0024874 | 0.0024874 | 0.99158 | -0.059767 | 0.99145 | -0.060685 | 0.92126
42 | 0.0016574 | 0.00041529 | -0.0016573 | -0.00041536 | 2.5598e-08 | -7.5653e-08 | 0.0024874 | 0.0024874 | 0.0024874 | 0.99145 | -0.060685 | 0.99143 | -0.060797 | 0.92127
43 | 0.0024102 | 0.00060385 | -0.0024101 | -0.00060402 | 1.4303e-07 | -1.7157e-07 | 0.0036145 | 0.0036146 | 0.0036146 | 0.99221 | -0.055197 | 0.99215 | -0.055625 | 1.3387
44 | 0.0030633 | 0.00074748 | -0.0030619 | -0.00074827 | 1.351e-06 | -7.9166e-07 | 0.0046018 | 0.0046022 | 0.0046022 | 0.98901 | -0.080511 | 0.98856 | -0.08386 | 1.7045
45 | 0.0004726 | 0.00011199 | -0.00047247 | -0.0001173 | 1.3149e-07 | -5.3161e-06 | 0.00070882 | 0.00071066 | 0.00071066 | 0.98901 | -0.080511 | 0.98873 | -0.082649 | 0.26321
46 | 0.00055009 | 0.00013306 | -0.00054993 | -0.00013783 | 1.6063e-07 | -4.7691e-06 | 0.00082596 | 0.00082765 | 0.00082765 | 0.98901 | -0.080511 | 0.98871 | -0.082694 | 0.30654
47 | 0.0030619 | 0.00074827 | -0.0030616 | -0.00074844 | 2.9046e-07 | -1.7001e-07 | 0.0046022 | 0.0046023 | 0.0046023 | 0.98856 | -0.08386 | 0.98846 | -0.084579 | 1.7046
48 | 9.7141e-05 | 2.3239e-05 | -9.714e-05 | -2.4345e-05 | 1.1476e-09 | -1.106e-06 | 0.00014581 | 0.0001462 | 0.0001462 | 0.98873 | -0.082649 | 0.98872 | -0.082738 | 0.054146
49 | 0.0027936 | 0.00068126 | -0.0027933 | -0.00068145 | 2.487e-07 | -1.941e-07 | 0.0041988 | 0.0041989 | 0.0041989 | 0.98846 | -0.084579 | 0.98837 | -0.085257 | 1.5551
50 | 0.0026595 | 0.0006479 | -0.0026593 | -0.00064806 | 1.7425e-07 | -1.5694e-07 | 0.0039973 | 0.0039974 | 0.0039974 | 0.98837 | -0.085257 | 0.98831 | -0.085756 | 1.4805
51 | 0.0025351 | 0.00061693 | -0.0025349 | -0.00061708 | 1.4764e-07 | -1.5202e-07 | 0.0038104 | 0.0038105 | 0.0038105 | 0.98831 | -0.085756 | 0.98825 | -0.086201 | 1.4113
52 | 0.0023267 | 0.0005649 | -0.0023265 | -0.0005652 | 2.2802e-07 | -2.9511e-07 | 0.003497 | 0.0034971 | 0.0034971 | 0.98825 | -0.086201 | 0.98815 | -0.086953 | 1.2952
53 | -0.00028237 | -7.0768e-05 | 0.00028239 | 6.7725e-05 | 2.6826e-08 | -3.0424e-06 | 0.00042525 | 0.00042419 | 0.00042525 | 0.98805 | -0.087669 | 0.98815 | -0.086953 | 0.1575
54 | 0.0010966 | 0.00027085 | -0.0010965 | -0.00027187 | 1.4373e-07 | -1.0282e-06 | 0.0016499 | 0.0016503 | 0.0016503 | 0.98815 | -0.086953 | 0.98801 | -0.087923 | 0.61123
55 | 0.00048087 | 0.00011541 | -0.00048074 | -0.00012048 | 1.3066e-07 | -5.0764e-06 | 0.00072234 | 0.00072413 | 0.00072413 | 0.98815 | -0.086953 | 0.98787 | -0.088999 | 0.26819
56 | 0.00021436 | 4.7997e-05 | -0.00021433 | -5.3716e-05 | 2.8908e-08 | -5.7187e-06 | 0.00032086 | 0.0003228 | 0.0003228 | 0.98815 | -0.086953 | 0.98801 | -0.088031 | 0.11955
57 | 0.00087333 | 0.00021595 | -0.0008733 | -0.00021626 | 2.6763e-08 | -3.0767e-07 | 0.0013143 | 0.0013144 | 0.0013144 | 0.98801 | -0.087923 | 0.98798 | -0.08815 | 0.4868
58 | 0.0007566 | 0.00018701 | -0.00075651 | -0.00018843 | 9.2167e-08 | -1.4227e-06 | 0.0011386 | 0.0011391 | 0.0011391 | 0.98798 | -0.08815 | 0.98786 | -0.089048 | 0.4219
59 | 0.00051025 | 0.00012671 | -0.00051025 | -0.00012687 | 4.3833e-09 | -1.507e-07 | 0.00076818 | 0.00076823 | 0.00076823 | 0.98786 | -0.089048 | 0.98785 | -0.089111 | 0.28453
60 | 0.00042129 | 0.00010457 | -0.00042129 | -0.00010491 | 6.7242e-09 | -3.4029e-07 | 0.00063425 | 0.00063437 | 0.00063437 | 0.98785 | -0.089111 | 0.98783 | -0.089228 | 0.23495
61 | -0.00019323 | -4.8428e-05 | 0.00019325 | 4.448e-05 | 1.6282e-08 | -3.9489e-06 | 0.0002912 | 0.00028985 | 0.0002912 | 0.98742 | -0.091928 | 0.98751 | -0.09127 | 0.10785
62 | 0.00051679 | 0.00012935 | -0.00051679 | -0.00012952 | 5.0892e-09 | -1.7012e-07 | 0.00077866 | 0.00077872 | 0.00077872 | 0.98751 | -0.09127 | 0.9875 | -0.091341 | 0.28842
63 | -0.00071004 | -0.00017383 | 0.0007105 | 0.00016582 | 4.539e-07 | -8.0039e-06 | 0.0010685 | 0.0010657 | 0.0010685 | 0.98751 | -0.09127 | 0.98816 | -0.08623 | 0.39573

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.037098 | 0.0090341

## res_load
| p_mw | q_mvar
0 | 0.0028974 | 0.00072615
1 | 0.0019011 | 0.00047646
2 | 0.0011504 | 0.00028831
3 | 0.0017075 | 0.00042795
4 | 0.0013511 | 0.00033862
5 | 0.00096059 | 0.00024075
6 | 0.00065633 | 0.00016449
7 | 0.00037938 | 9.5083e-05
8 | 0.0013439 | 0.00033682
9 | 0.00068343 | 0.00017128
10 | 0.00066247 | 0.00016603
11 | 0.0016707 | 0.00041871
12 | 8.9039e-05 | 2.2315e-05
13 | 0.00026398 | 6.616e-05
14 | 6.8259e-05 | 1.7107e-05
15 | 0.001873 | 0.00046941
16 | 0.00079803 | 0.0002
17 | 0.00089328 | 0.00022388
18 | 0.00054986 | 0.00013781
19 | 9.3181e-05 | 2.3353e-05
20 | 8.9682e-05 | 2.2476e-05
21 | 0.0026457 | 0.00066307
22 | 0.00056816 | 0.0001424
23 | 0.00058287 | 0.00014608
24 | 0.00046063 | 0.00011545
25 | 0.00047071 | 0.00011797
26 | 0.00023947 | 6.0018e-05
27 | 0.0003421 | 8.5739e-05
28 | 0.0016573 | 0.00041537
29 | 0.0024101 | 0.00060402
30 | 0.00013885 | 3.4799e-05
31 | 0.00037533 | 9.4066e-05
32 | 0.00054993 | 0.00013783
33 | 0.00026807 | 6.7186e-05
34 | 9.714e-05 | 2.4346e-05
35 | 0.00013386 | 3.3548e-05
36 | 0.00012421 | 3.1129e-05
37 | 0.00020821 | 5.2182e-05
38 | 0.00028237 | 7.0768e-05
39 | 0.00025225 | 6.322e-05
40 | 0.00022314 | 5.5925e-05
41 | 0.00048074 | 0.00012048
42 | 0.00021433 | 5.3716e-05
43 | 0.0001167 | 2.9248e-05
44 | 0.00024626 | 6.1719e-05
45 | 8.895e-05 | 2.2293e-05
46 | 0.00019323 | 4.8429e-05
47 | 0.00051679 | 0.00012952
48 | 0.0020749 | 0.00052002

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1