## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1368-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1368-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1368-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1368-2_0_4_node_107 | 0.4 | n |  | TRUE
4 | bus_LV_1368-2_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1368-2_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1368-2_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1368-2_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1368-2_0_4_node_58 | 0.4 | n |  | TRUE
9 | bus_LV_1368-2_0_4_node_57 | 0.4 | n |  | TRUE
10 | bus_LV_1368-2_0_4_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_1368-2_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1368-2_0_4_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_1368-2_0_4_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_1368-2_0_4_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_1368-2_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1368-2_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1368-2_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1368-2_0_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1368-2_0_4_node_103 | 0.4 | n |  | TRUE
20 | bus_LV_1368-2_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1368-2_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1368-2_0_4_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_1368-2_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1368-2_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1368-2_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1368-2_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1368-2_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1368-2_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1368-2_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1368-2_0_4_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_1368-2_0_4_node_51 | 0.4 | n |  | TRUE
32 | bus_LV_1368-2_0_4_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1368-2_0_4_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_1368-2_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1368-2_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_1368-2_0_4_node_102 | 0.4 | n |  | TRUE
37 | bus_LV_1368-2_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1368-2_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1368-2_0_4_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1368-2_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_1368-2_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_1368-2_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_1368-2_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1368-2_0_4_node_101 | 0.4 | n |  | TRUE
45 | bus_LV_1368-2_0_4_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1368-2_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1368-2_0_4_node_100 | 0.4 | n |  | TRUE
48 | bus_LV_1368-2_0_4_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_1368-2_0_4_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_1368-2_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_1368-2_0_4_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_1368-2_0_4_node_76 | 0.4 | n |  | TRUE
53 | bus_LV_1368-2_0_4_node_84 | 0.4 | n |  | TRUE
54 | bus_LV_1368-2_0_4_node_83 | 0.4 | n |  | TRUE
55 | bus_LV_1368-2_0_4_node_74 | 0.4 | n |  | TRUE
56 | bus_LV_1368-2_0_4_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_1368-2_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_1368-2_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_1368-2_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_1368-2_0_4_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_1368-2_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_1368-2_0_4_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_1368-2_0_4_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_1368-2_0_4_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_1368-2_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_1368-2_0_4_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_1368-2_0_4_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_1368-2_0_4_node_59 | 0.4 | n |  | TRUE
69 | bus_LV_1368-2_0_4_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_1368-2_0_4_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_1368-2_0_4_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_1368-2_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_1368-2_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_1368-2_0_4_node_91 | 0.4 | n |  | TRUE
75 | bus_LV_1368-2_0_4_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_1368-2_0_4_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_1368-2_0_4_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_1368-2_0_4_node_90 | 0.4 | n |  | TRUE
79 | bus_LV_1368-2_0_4_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_1368-2_0_4_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_1368-2_0_4_node_75 | 0.4 | n |  | TRUE
82 | bus_LV_1368-2_0_4_node_77 | 0.4 | n |  | TRUE
83 | bus_LV_1368-2_0_4_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_1368-2_0_4_node_69 | 0.4 | n |  | TRUE
85 | bus_LV_1368-2_0_4_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_1368-2_0_4_node_79 | 0.4 | n |  | TRUE
87 | bus_LV_1368-2_0_4_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_1368-2_0_4_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_1368-2_0_4_node_104 | 0.4 | n |  | TRUE
90 | bus_LV_1368-2_0_4_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_1368-2_0_4_node_87 | 0.4 | n |  | TRUE
92 | bus_LV_1368-2_0_4_node_95 | 0.4 | n |  | TRUE
93 | bus_LV_1368-2_0_4_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_1368-2_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_1368-2_0_4_node_82 | 0.4 | n |  | TRUE
96 | bus_LV_1368-2_0_4_node_92 | 0.4 | n |  | TRUE
97 | bus_LV_1368-2_0_4_node_93 | 0.4 | n |  | TRUE
98 | bus_LV_1368-2_0_4_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_1368-2_0_4_node_88 | 0.4 | n |  | TRUE
100 | bus_LV_1368-2_0_4_node_89 | 0.4 | n |  | TRUE
101 | bus_LV_1368-2_0_4_node_99 | 0.4 | n |  | TRUE
102 | bus_LV_1368-2_0_4_node_98 | 0.4 | n |  | TRUE
103 | bus_LV_1368-2_0_4_node_96 | 0.4 | n |  | TRUE
104 | bus_LV_1368-2_0_4_node_97 | 0.4 | n |  | TRUE
105 | bus_MV_135_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1368-2_0_4_load_0 | 0 | 0.00021626 | 5.42e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1368-2_0_4_load_107 | 3 | 0.00050357 | 0.00012621 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1368-2_0_4_load_3 | 4 | 0.00068901 | 0.00017268 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1368-2_0_4_load_5 | 5 | 0.0014926 | 0.00037407 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1368-2_0_4_load_58 | 8 | 0.0005036 | 0.00012621 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1368-2_0_4_load_57 | 9 | 0.00048495 | 0.00012154 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1368-2_0_4_load_38 | 12 | 0.00028789 | 7.2152e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1368-2_0_4_load_8 | 15 | 0.00074732 | 0.0001873 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1368-2_0_4_load_9 | 16 | 0.0010438 | 0.00026161 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1368-2_0_4_load_22 | 17 | 0.0012117 | 0.00030367 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1368-2_0_4_load_103 | 19 | 0.00047355 | 0.00011868 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1368-2_0_4_load_19 | 20 | 0.0012767 | 0.00031997 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1368-2_0_4_load_10 | 22 | 0.0016084 | 0.00040309 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1368-2_0_4_load_11 | 23 | 0.00060953 | 0.00015276 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1368-2_0_4_load_13 | 25 | 0.0055389 | 0.0013882 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1368-2_0_4_load_14 | 26 | 0.00072564 | 0.00018186 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1368-2_0_4_load_16 | 28 | 0.00054397 | 0.00013633 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1368-2_0_4_load_17 | 29 | 0.00043634 | 0.00010936 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1368-2_0_4_load_28 | 30 | 0.00053362 | 0.00013374 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1368-2_0_4_load_51 | 31 | 0.00041535 | 0.0001041 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1368-2_0_4_load_26 | 32 | 0.00030069 | 7.5359e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1368-2_0_4_load_21 | 34 | 0.0011742 | 0.00029428 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1368-2_0_4_load_31 | 35 | 0.00081614 | 0.00020454 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1368-2_0_4_load_23 | 37 | 0.00082734 | 0.00020735 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1368-2_0_4_load_24 | 38 | 0.0006864 | 0.00017203 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1368-2_0_4_load_29 | 41 | 0.0011136 | 0.0002791 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1368-2_0_4_load_30 | 42 | 0.00082823 | 0.00020757 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1368-2_0_4_load_101 | 44 | 0.0007136 | 0.00017885 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1368-2_0_4_load_42 | 45 | 0.00080866 | 0.00020267 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1368-2_0_4_load_100 | 47 | 0.00097767 | 0.00024503 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1368-2_0_4_load_32 | 48 | 0.001059 | 0.0002654 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1368-2_0_4_load_37 | 51 | 0.0016695 | 0.00041842 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1368-2_0_4_load_83 | 54 | 0.00063528 | 0.00015922 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1368-2_0_4_load_74 | 55 | 0.00068475 | 0.00017162 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1368-2_0_4_load_43 | 56 | 0.00075704 | 0.00018973 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1368-2_0_4_load_44 | 57 | 0.00082782 | 0.00020747 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1368-2_0_4_load_47 | 60 | 0.00095511 | 0.00023937 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1368-2_0_4_load_49 | 61 | 0.00042573 | 0.0001067 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1368-2_0_4_load_50 | 62 | 0.0003332 | 8.3507e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1368-2_0_4_load_52 | 63 | 0.00058632 | 0.00014695 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1368-2_0_4_load_53 | 64 | 0.0004246 | 0.00010641 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1368-2_0_4_load_55 | 65 | 0.00051281 | 0.00012852 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1368-2_0_4_load_54 | 66 | 0.00043335 | 0.00010861 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1368-2_0_4_load_56 | 67 | 0.00022643 | 5.6748e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1368-2_0_4_load_59 | 68 | 0.0037215 | 0.00093269 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1368-2_0_4_load_60 | 69 | 0.0043015 | 0.0010781 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1368-2_0_4_load_61 | 70 | 0.00803 | 0.0020125 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1368-2_0_4_load_63 | 72 | 0.0034427 | 0.00086283 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1368-2_0_4_load_64 | 73 | 0.0021074 | 0.00052817 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1368-2_0_4_load_91 | 74 | 0.0068687 | 0.0017215 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1368-2_0_4_load_67 | 77 | 0.0032212 | 0.0008073 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1368-2_0_4_load_90 | 78 | 0.0032758 | 0.00082099 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1368-2_0_4_load_72 | 79 | 0.0025749 | 0.00064533 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1368-2_0_4_load_68 | 80 | 0.0018736 | 0.00046957 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1368-2_0_4_load_77 | 82 | 0.0050234 | 0.001259 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1368-2_0_4_load_78 | 83 | 0.0028163 | 0.00070583 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1368-2_0_4_load_69 | 84 | 0.0028065 | 0.00070339 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1368-2_0_4_load_71 | 85 | 0.0052596 | 0.0013182 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1368-2_0_4_load_79 | 86 | 0.0081568 | 0.0020443 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1368-2_0_4_load_80 | 87 | 0.0035149 | 0.00088091 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1368-2_0_4_load_104 | 89 | 0.00096257 | 0.00024124 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1368-2_0_4_load_81 | 90 | 0.0016247 | 0.00040719 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1368-2_0_4_load_87 | 91 | 0.0083925 | 0.0021033 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1368-2_0_4_load_95 | 92 | 0.028313 | 0.0070958 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1368-2_0_4_load_86 | 94 | 0.0028515 | 0.00071465 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1368-2_0_4_load_82 | 95 | 0.0022681 | 0.00056845 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1368-2_0_4_load_92 | 96 | 0.0015583 | 0.00039054 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1368-2_0_4_load_93 | 97 | 0.034147 | 0.0085582 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1368-2_0_4_load_88 | 99 | 0.0035697 | 0.00089465 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1368-2_0_4_load_89 | 100 | 0.00046089 | 0.00011551 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1368-2_0_4_load_99 | 101 | 0.001539 | 0.0003857 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1368-2_0_4_load_98 | 102 | 0.0013636 | 0.00034175 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1368-2_0_4_load_96 | 103 | 0.008011 | 0.0020077 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1368-2_0_4_load_97 | 104 | 0.0034793 | 0.000872 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 94 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1368-2_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.12961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1368-2_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.10483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1368-2_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.33687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1368-2_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.10458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1368-2_0_4_line_4 | NAYY 4x150 SE | 4 | 7 | 0.39145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1368-2_0_4_line_5 | NAYY 4x150 SE | 5 | 6 | 0.093492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1368-2_0_4_line_6 | NAYY 4x150 SE | 6 | 11 | 0.057607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1368-2_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.30625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1368-2_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.039362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1368-2_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.21924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1368-2_0_4_line_10 | NAYY 4x150 SE | 10 | 13 | 0.052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1368-2_0_4_line_11 | NAYY 4x150 SE | 11 | 15 | 0.19312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1368-2_0_4_line_12 | NAYY 4x150 SE | 11 | 16 | 0.10927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1368-2_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.17693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1368-2_0_4_line_14 | NAYY 4x150 SE | 12 | 14 | 0.11804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1368-2_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.22508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1368-2_0_4_line_16 | NAYY 4x150 SE | 15 | 17 | 0.025569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1368-2_0_4_line_17 | NAYY 4x150 SE | 16 | 18 | 0.0045939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1368-2_0_4_line_18 | NAYY 4x150 SE | 17 | 19 | 0.03596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1368-2_0_4_line_19 | NAYY 4x150 SE | 18 | 20 | 0.039842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1368-2_0_4_line_20 | NAYY 4x150 SE | 18 | 21 | 0.32042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1368-2_0_4_line_21 | NAYY 4x150 SE | 19 | 36 | 0.03672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1368-2_0_4_line_22 | NAYY 4x150 SE | 21 | 34 | 0.10418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1368-2_0_4_line_23 | NAYY 4x150 SE | 22 | 23 | 0.011105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1368-2_0_4_line_24 | NAYY 4x150 SE | 22 | 24 | 0.026483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1368-2_0_4_line_25 | NAYY 4x150 SE | 23 | 25 | 0.014916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1368-2_0_4_line_26 | NAYY 4x150 SE | 24 | 26 | 0.19382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1368-2_0_4_line_27 | NAYY 4x150 SE | 24 | 27 | 0.013997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1368-2_0_4_line_28 | NAYY 4x150 SE | 27 | 28 | 0.01146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1368-2_0_4_line_29 | NAYY 4x150 SE | 27 | 29 | 0.044189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1368-2_0_4_line_30 | NAYY 4x150 SE | 28 | 30 | 0.017654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1368-2_0_4_line_31 | NAYY 4x150 SE | 29 | 31 | 0.0052259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1368-2_0_4_line_32 | NAYY 4x150 SE | 30 | 32 | 0.017524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1368-2_0_4_line_33 | NAYY 4x150 SE | 31 | 33 | 0.0055549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1368-2_0_4_line_34 | NAYY 4x150 SE | 32 | 38 | 0.021074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1368-2_0_4_line_35 | NAYY 4x150 SE | 33 | 63 | 0.0098952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1368-2_0_4_line_36 | NAYY 4x150 SE | 33 | 58 | 0.023774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1368-2_0_4_line_37 | NAYY 4x150 SE | 34 | 35 | 0.035524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1368-2_0_4_line_38 | NAYY 4x150 SE | 36 | 47 | 0.0033162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_1368-2_0_4_line_39 | NAYY 4x150 SE | 36 | 88 | 0.097594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1368-2_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.083719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1368-2_0_4_line_41 | NAYY 4x150 SE | 37 | 39 | 0.039082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1368-2_0_4_line_42 | NAYY 4x150 SE | 39 | 40 | 0.027871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1368-2_0_4_line_43 | NAYY 4x150 SE | 40 | 41 | 0.17247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_1368-2_0_4_line_44 | NAYY 4x150 SE | 40 | 42 | 0.072245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_1368-2_0_4_line_45 | NAYY 4x150 SE | 41 | 43 | 0.020128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_1368-2_0_4_line_46 | NAYY 4x150 SE | 42 | 44 | 0.01313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_1368-2_0_4_line_47 | NAYY 4x150 SE | 43 | 45 | 0.12192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1368-2_0_4_line_48 | NAYY 4x150 SE | 43 | 46 | 0.072094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1368-2_0_4_line_49 | NAYY 4x150 SE | 44 | 47 | 0.022408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_1368-2_0_4_line_50 | NAYY 4x150 SE | 46 | 48 | 0.0098268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_1368-2_0_4_line_51 | NAYY 4x150 SE | 48 | 49 | 0.0069527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_1368-2_0_4_line_52 | NAYY 4x150 SE | 49 | 50 | 0.016087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1368-2_0_4_line_53 | NAYY 4x150 SE | 50 | 51 | 0.013317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1368-2_0_4_line_54 | NAYY 4x150 SE | 51 | 52 | 0.1266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_1368-2_0_4_line_55 | NAYY 4x150 SE | 52 | 53 | 0.034896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_1368-2_0_4_line_56 | NAYY 4x150 SE | 52 | 54 | 0.14531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1368-2_0_4_line_57 | NAYY 4x150 SE | 52 | 55 | 0.063664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1368-2_0_4_line_58 | NAYY 4x150 SE | 53 | 93 | 0.012286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1368-2_0_4_line_59 | NAYY 4x150 SE | 53 | 94 | 0.1874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_1368-2_0_4_line_60 | NAYY 4x150 SE | 54 | 95 | 0.017403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1368-2_0_4_line_61 | NAYY 4x150 SE | 56 | 57 | 0.032997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1368-2_0_4_line_62 | NAYY 4x150 SE | 57 | 58 | 0.011866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1368-2_0_4_line_63 | NAYY 4x150 SE | 58 | 59 | 0.003706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1368-2_0_4_line_64 | NAYY 4x150 SE | 58 | 60 | 0.015923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1368-2_0_4_line_65 | NAYY 4x150 SE | 59 | 61 | 0.018965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1368-2_0_4_line_66 | NAYY 4x150 SE | 59 | 62 | 0.012963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1368-2_0_4_line_67 | NAYY 4x150 SE | 61 | 64 | 0.012167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1368-2_0_4_line_68 | NAYY 4x150 SE | 63 | 65 | 0.016895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1368-2_0_4_line_69 | NAYY 4x150 SE | 64 | 66 | 0.014587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1368-2_0_4_line_70 | NAYY 4x150 SE | 65 | 67 | 0.049904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1368-2_0_4_line_71 | NAYY 4x150 SE | 68 | 69 | 0.014757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1368-2_0_4_line_72 | NAYY 4x150 SE | 68 | 70 | 0.0065428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1368-2_0_4_line_73 | NAYY 4x150 SE | 69 | 71 | 0.033554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1368-2_0_4_line_74 | NAYY 4x150 SE | 70 | 72 | 0.01862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1368-2_0_4_line_75 | NAYY 4x150 SE | 71 | 73 | 0.022593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1368-2_0_4_line_76 | NAYY 4x150 SE | 73 | 74 | 0.032556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1368-2_0_4_line_77 | NAYY 4x150 SE | 74 | 78 | 0.036157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1368-2_0_4_line_78 | NAYY 4x150 SE | 75 | 76 | 0.009438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1368-2_0_4_line_79 | NAYY 4x150 SE | 75 | 77 | 0.028211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1368-2_0_4_line_80 | NAYY 4x150 SE | 76 | 79 | 0.012328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1368-2_0_4_line_81 | NAYY 4x150 SE | 77 | 80 | 0.0025266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1368-2_0_4_line_82 | NAYY 4x150 SE | 78 | 82 | 0.016333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1368-2_0_4_line_83 | NAYY 4x150 SE | 79 | 87 | 0.017854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1368-2_0_4_line_84 | NAYY 4x150 SE | 80 | 84 | 0.010521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1368-2_0_4_line_85 | NAYY 4x150 SE | 81 | 82 | 0.045412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1368-2_0_4_line_86 | NAYY 4x150 SE | 81 | 83 | 0.046371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1368-2_0_4_line_87 | NAYY 4x150 SE | 83 | 91 | 0.033002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_1368-2_0_4_line_88 | NAYY 4x150 SE | 83 | 92 | 0.080187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1368-2_0_4_line_89 | NAYY 4x150 SE | 84 | 85 | 0.0088027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1368-2_0_4_line_90 | NAYY 4x150 SE | 85 | 86 | 0.0030342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1368-2_0_4_line_91 | NAYY 4x150 SE | 87 | 90 | 0.027745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1368-2_0_4_line_92 | NAYY 4x150 SE | 88 | 89 | 0.062942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1368-2_0_4_line_93 | NAYY 4x150 SE | 90 | 95 | 0.0069893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1368-2_0_4_line_94 | NAYY 4x150 SE | 91 | 94 | 0.047255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
95 | LV_1368-2_0_4_line_95 | NAYY 4x150 SE | 92 | 97 | 0.023176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1368-2_0_4_line_96 | NAYY 4x150 SE | 93 | 99 | 0.16266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1368-2_0_4_line_97 | NAYY 4x150 SE | 93 | 100 | 0.038203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1368-2_0_4_line_98 | NAYY 4x150 SE | 96 | 97 | 0.010766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1368-2_0_4_line_99 | NAYY 4x150 SE | 96 | 98 | 0.16848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1368-2_0_4_line_100 | NAYY 4x150 SE | 98 | 103 | 0.039706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1368-2_0_4_line_101 | NAYY 4x150 SE | 99 | 101 | 0.093474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1368-2_0_4_line_102 | NAYY 4x150 SE | 100 | 102 | 0.077782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1368-2_0_4_line_103 | NAYY 4x150 SE | 103 | 104 | 0.0052135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1368-2_0_4_trafo_86 | 0.25 MVA 20/0.4 kV | 105 | 94 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2702239.9772 | 1209734.5531 | 2702240.7582 | 1209735.5561 | 2702242.3576 | 1209737.6071 | 2702248.7798 | 1209739.9299 | 2702257.2715 | 1209739.9421 | 2702272.6103 | 1209738.3372 | 2702280.0062 | 1209738.8532 | 2702298.1805 | 1209742.5784 | 2702302.6825 | 1209744.7127 | 2702303.8115 | 1209747.1448 | 2702302.4418 | 1209749.434 | 2702298.4 | 1209751.0548 | 2702292.3393 | 1209752.0293 | 2702280.4285 | 1209756.3393 | 2702267.9498 | 1209762.2851 | 2702259.109 | 1209768.8938 | 2702256.0265 | 1209773.5331 | 2702254.5362 | 1209778.4221
1 | 2702341.1716 | 1209822.7827 | 2702325.4759 | 1209811.5279 | 2702311.3591 | 1209799.9667 | 2702296.5992 | 1209787.3381 | 2702292.4379 | 1209784.8428 | 2702287.1739 | 1209782.8067 | 2702280.9384 | 1209782.4552 | 2702272.4259 | 1209783.2209 | 2702262.7835 | 1209785.5907 | 2702258.7908 | 1209785.2331 | 2702255.7531 | 1209783.2686 | 2702254.5362 | 1209778.4221
2 | 2702239.9772 | 1209734.5531 | 2702413.7375 | 1209445.9533
3 | 2702341.1716 | 1209822.7827 | 2702330.565 | 1209824.1907 | 2702319.4374 | 1209827.6134 | 2702303.4656 | 1209839.5368 | 2702283.3241 | 1209855.6694 | 2702276.2833 | 1209859.2846 | 2702273.6197 | 1209864.3203 | 2702274.9226 | 1209874.3496 | 2702269.5242 | 1209878.8269 | 2702263.7896 | 1209878.2529
4 | 2701925.7282 | 1209852.1705 | 2701942.6725 | 1209853.572 | 2701953.0745 | 1209861.4552 | 2701970.5366 | 1209846.3542 | 2701990.1756 | 1209848.4357 | 2702013.42 | 1209844.6304 | 2702039.3888 | 1209825.1163 | 2702053.7009 | 1209830.6205 | 2702063.286 | 1209824.4801 | 2702079.6459 | 1209812.5071 | 2702084.5511 | 1209813.2916 | 2702086.7704 | 1209806.6694 | 2702090.6851 | 1209803.5898 | 2702101.4801 | 1209809.3785 | 2702119.5916 | 1209818.0945 | 2702130.0295 | 1209823.8661 | 2702149.9685 | 1209828.4105 | 2702160.6315 | 1209841.9025 | 2702195.9252 | 1209852.3141 | 2702215.4126 | 1209862.7996 | 2702241.5067 | 1209877.2456 | 2702249.1082 | 1209884.3809 | 2702256.2507 | 1209877.4985 | 2702263.7896 | 1209878.2529
5 | 2701568.3607 | 1209807.6127 | 2701579.7022 | 1209820.1701 | 2701586.0959 | 1209828.1956 | 2701591.1731 | 1209835.3982 | 2701598.6231 | 1209847.0109 | 2701608.5949 | 1209860.0898 | 2701618.9522 | 1209874.1871 | 2701625.005 | 1209881.8444
6 | 2701532.0721 | 1209852.4264 | 2701568.3607 | 1209807.6127
7 | 2701925.7282 | 1209852.1705 | 2701921.6343 | 1209841.2819 | 2701892.6483 | 1209778.0205 | 2701858.4205 | 1209702.9171 | 2701822.925 | 1209648.1399 | 2701800.2622 | 1209605.8126 | 2701782.4047 | 1209582.6997
8 | 2701925.7282 | 1209852.1705 | 2701944.5626 | 1209886.7342
9 | 2702029.0319 | 1210086.9553 | 2702025.6739 | 1210059.7345 | 2702016.3376 | 1210024.2501 | 2701949.684 | 1209896.1326 | 2701944.5626 | 1209886.7342
10 | 2701988.1863 | 1210063.4184 | 2702008.915 | 1210075.9704 | 2702016.9893 | 1210083.0245 | 2702024.9257 | 1210091.0213 | 2702029.0319 | 1210086.9553
11 | 2701532.0721 | 1209852.4264 | 2701536.8143 | 1209871.7205 | 2701542.6209 | 1209893.2343 | 2701547.6353 | 1209910.376 | 2701550.3339 | 1209916.6374 | 2701553.1477 | 1209921.9334 | 2701579.0151 | 1209967.6167 | 2701586.9802 | 1209982.0067 | 2701590.2042 | 1209989.5446 | 2701591.7914 | 1209994.5529 | 2701592.2635 | 1209997.6298 | 2701592.011 | 1210001.7395 | 2701590.6191 | 1210005.3516 | 2701588.1306 | 1210009.5233 | 2701584.8991 | 1210012.2368 | 2701580.5181 | 1210014.1525 | 2701574.4192 | 1210015.1716 | 2701567.6908 | 1210015.6915
12 | 2701532.0721 | 1209852.4264 | 2701526.9788 | 1209839.0193 | 2701524.8097 | 1209834.7016 | 2701522.0458 | 1209830.0402 | 2701517.0074 | 1209823.2275 | 2701497.5158 | 1209798.1785 | 2701472.718 | 1209767.302 | 2701469.6535 | 1209763.5203
13 | 2701988.1863 | 1210063.4184 | 2701939.0252 | 1210034.0134 | 2701928.5711 | 1210026.0848 | 2701924.4804 | 1210016.3526 | 2701922.6946 | 1210003.4131 | 2701919.9605 | 1209994.3601 | 2701915.2283 | 1209988.3528 | 2701904.0291 | 1209985.315 | 2701876.2321 | 1209986.43 | 2701863.1548 | 1209987.8633 | 2701857.3445 | 1209987.9976 | 2701852.4166 | 1209984.5444 | 2701851.1794 | 1209983.8978
14 | 2701787.3898 | 1210064.624 | 2701799.5561 | 1210058.6496 | 2701809.0628 | 1210053.953 | 2701811.7924 | 1210050.3637 | 2701815.6939 | 1210028.8931 | 2701830.0576 | 1209988.6212 | 2701838.8122 | 1209981.2321 | 2701844.279 | 1209980.2914 | 2701851.1794 | 1209983.8978
15 | 2701567.6908 | 1210015.6915 | 2701787.3898 | 1210064.624
16 | 2701542.1978 | 1210017.6616 | 2701567.6908 | 1210015.6915
17 | 2701466.7612 | 1209759.9511 | 2701469.6535 | 1209763.5203
18 | 2701507.4747 | 1210009.8731 | 2701507.4747 | 1210009.8731 | 2701511.1234 | 1210010.3355 | 2701516.0043 | 1210011.6528 | 2701525.2755 | 1210015.4132 | 2701530.0257 | 1210016.8172 | 2701534.5336 | 1210017.7167 | 2701540.1117 | 1210017.8229 | 2701542.1978 | 1210017.6616
19 | 2701466.7612 | 1209759.9511 | 2701465.3608 | 1209764.5083 | 2701465.2823 | 1209769.1212 | 2701467.3432 | 1209789.6372 | 2701467.944 | 1209799.4543
20 | 2701367.1751 | 1209458.6713 | 2701371.7289 | 1209471.6577 | 2701390.063 | 1209508.984 | 2701414.3234 | 1209556.8073 | 2701418.3877 | 1209565.9271 | 2701421.6758 | 1209574.6446 | 2701424.5358 | 1209583.4994 | 2701428.6574 | 1209600.4257 | 2701441.3359 | 1209652.4218 | 2701443.5083 | 1209662.3656 | 2701444.8322 | 1209671.2388 | 2701448.2283 | 1209708.9116 | 2701449.8726 | 1209720.8479 | 2701452.1435 | 1209729.915 | 2701454.2101 | 1209736.2434 | 2701456.9357 | 1209743.1613 | 2701459.3955 | 1209748.2733 | 2701462.3307 | 1209753.5936 | 2701466.7612 | 1209759.9511
21 | 2701472.4269 | 1210019.8395 | 2701483.6409 | 1210014.8712 | 2701490.1402 | 1210012.658 | 2701496.0555 | 1210011.2688 | 2701502.2679 | 1210010.2849 | 2701507.4747 | 1210009.8731
22 | 2701367.1751 | 1209458.6713 | 2701364.5272 | 1209463.7187 | 2701363.8602 | 1209472.5469 | 2701361.6177 | 1209484.606 | 2701359.1097 | 1209518.0978 | 2701358.5807 | 1209525.5162 | 2701358.8041 | 1209536.0829 | 2701359.4252 | 1209541.5862 | 2701359.1648 | 1209544.8285 | 2701357.0492 | 1209548.9732 | 2701353.6493 | 1209551.7507 | 2701345.768 | 1209552.64
23 | 2701254.607 | 1209725.1341 | 2701247.5151 | 1209716.5886
24 | 2701271.5196 | 1209745.5134 | 2701254.607 | 1209725.1341
25 | 2701237.5344 | 1209705.5107 | 2701244.7892 | 1209713.3041 | 2701247.5151 | 1209716.5886
26 | 2701271.5196 | 1209745.5134 | 2701277.1091 | 1209744.5186 | 2701312.0438 | 1209764.9926 | 2701346.7679 | 1209788.4541 | 2701359.1216 | 1209798.293 | 2701364.2509 | 1209803.795 | 2701368.8795 | 1209810.1225 | 2701381.7927 | 1209833.1134 | 2701385.5397 | 1209839.4259 | 2701391.4584 | 1209846.3313 | 2701400.1079 | 1209853.5944 | 2701405.64 | 1209857.758 | 2701418.5762 | 1209862.8369
27 | 2701280.3359 | 1209756.4039 | 2701271.5196 | 1209745.5134
28 | 2701280.3359 | 1209756.4039 | 2701287.5311 | 1209765.3236
29 | 2701280.3359 | 1209756.4039 | 2701266.6761 | 1209758.9961 | 2701252.4047 | 1209759.0984 | 2701244.0516 | 1209758.99 | 2701240.3985 | 1209760.1177 | 2701237.8787 | 1209763.0103
30 | 2701287.5311 | 1209765.3236 | 2701298.6151 | 1209779.0641
31 | 2701237.8787 | 1209763.0103 | 2701235.427 | 1209767.6254
32 | 2701298.6151 | 1209779.0641 | 2701309.6178 | 1209792.7039
33 | 2701232.8211 | 1209772.5311 | 2701235.427 | 1209767.6254
34 | 2701309.6178 | 1209792.7039 | 2701322.8494 | 1209809.1068
35 | 2701232.8211 | 1209772.5311 | 2701236.2025 | 1209776.2132 | 2701239.4193 | 1209779.9042
36 | 2701232.8211 | 1209772.5311 | 2701224.7675 | 1209785.6814 | 2701220.502 | 1209792.8807
37 | 2701323.92 | 1209530.449 | 2701331.6765 | 1209548.2418 | 2701337.8055 | 1209553.5385 | 2701345.768 | 1209552.64
38 | 2701472.4269 | 1210019.8395 | 2701472.0629 | 1210016.5434
39 | 2701484.3559 | 1210116.6877 | 2701472.4269 | 1210019.8395
40 | 2701322.8494 | 1209809.1068 | 2701333.3255 | 1209822.0936 | 2701375.4149 | 1209874.2656
41 | 2701399.9538 | 1209904.6829 | 2701375.4149 | 1209874.2656
42 | 2701399.9538 | 1209904.6829 | 2701416.0488 | 1209925.1707 | 2701417.1872 | 1209926.6244
43 | 2701417.1872 | 1209926.6244 | 2701413.5761 | 1209928.8646 | 2701407.7232 | 1209934.6358 | 2701402.6741 | 1209935.6062 | 2701393.3491 | 1209934.9918 | 2701388.3282 | 1209935.1955 | 2701364.6719 | 1209932.8698 | 2701352.1454 | 1209935.003 | 2701337.83 | 1209937.2725 | 2701326.6374 | 1209936.5153 | 2701325.142 | 1209939.0694 | 2701317.9305 | 1209938.0018 | 2701314.4578 | 1209944.1805 | 2701310.5445 | 1209942.7352 | 2701307.03 | 1209941.5303 | 2701307.5347 | 1209952.0906 | 2701301.1703 | 1209951.282 | 2701296.5986 | 1209967.1154 | 2701288.5742 | 1209971.8381 | 2701291.2173 | 1209980.0331 | 2701291.0536 | 1209981.7133
44 | 2701417.1872 | 1209926.6244 | 2701454.7067 | 1209971.5824 | 2701460.9876 | 1209979.5281 | 2701462.9834 | 1209982.4756
45 | 2701285.8172 | 1210000.7781 | 2701289.9835 | 1209992.6987 | 2701291.0536 | 1209981.7133
46 | 2701462.9834 | 1209982.4756 | 2701463.5238 | 1209983.2738 | 2701465.525 | 1209987.1883 | 2701466.9442 | 1209991.3487 | 2701467.9252 | 1209994.5773
47 | 2701285.8172 | 1210000.7781 | 2701253.6058 | 1209979.3832 | 2701218.9179 | 1209956.5232 | 2701204.9822 | 1209948.9705 | 2701185.3451 | 1209940.5094 | 2701180.8906 | 1209940.071
48 | 2701285.8172 | 1210000.7781 | 2701301.7924 | 1210011.3233 | 2701303.9775 | 1210018.2874 | 2701306.7072 | 1210026.7508 | 2701307.9787 | 1210034.2443 | 2701311.74 | 1210046.8725 | 2701312.8394 | 1210053.7515 | 2701315.0017 | 1210062.5054
49 | 2701472.0629 | 1210016.5434 | 2701471.1622 | 1210008.3878 | 2701469.471 | 1209999.6641 | 2701467.9252 | 1209994.5773
50 | 2701315.0017 | 1210062.5054 | 2701317.5074 | 1210069.3861 | 2701318.6999 | 1210071.588
51 | 2701322.0109 | 1210077.7017 | 2701318.6999 | 1210071.588
52 | 2701322.0109 | 1210077.7017 | 2701325.9465 | 1210083.6504 | 2701332.5946 | 1210089.6786
53 | 2701332.5946 | 1210089.6786 | 2701339.7745 | 1210093.0362 | 2701345.1111 | 1210093.7993
54 | 2701420.8983 | 1210182.21 | 2701410.5452 | 1210166.9789 | 2701397.5206 | 1210126.4516 | 2701391.1786 | 1210114.9469 | 2701382.9061 | 1210105.6554 | 2701373.881 | 1210100.8321 | 2701361.9259 | 1210096.2035 | 2701345.1111 | 1210093.7993
55 | 2701420.8983 | 1210182.21 | 2701391.4477 | 1210201.0559
56 | 2701420.8983 | 1210182.21 | 2701425.5456 | 1210180.2654 | 2701436.8331 | 1210181.6805 | 2701447.0563 | 1210184.434 | 2701454.6721 | 1210188.0771 | 2701462.4932 | 1210195.7376 | 2701471.3541 | 1210205.2839 | 2701476.6081 | 1210211.0216 | 2701483.4544 | 1210216.1083 | 2701488.9114 | 1210218.8475 | 2701500.0394 | 1210223.818 | 2701508.0287 | 1210227.4008 | 2701512.5957 | 1210230.6252 | 2701516.6549 | 1210235.9869 | 2701521.412 | 1210247.2424 | 2701528.0517 | 1210263.9757
57 | 2701420.8983 | 1210182.21 | 2701432.9472 | 1210192.9333 | 2701467.7803 | 1210221.4232 | 2701469.3283 | 1210223.4289
58 | 2701379.9988 | 1210202.429 | 2701387.9314 | 1210203.5424 | 2701391.4477 | 1210201.0559
59 | 2701391.4477 | 1210201.0559 | 2701396.9083 | 1210206.7193 | 2701407.8467 | 1210237.5934 | 2701419.8073 | 1210277.6357 | 2701426.0008 | 1210300.5347 | 2701427.9395 | 1210338.95 | 2701426.7969 | 1210373.4991 | 2701427.9225 | 1210381.6563
60 | 2701534.3955 | 1210280.181 | 2701531.5218 | 1210272.721 | 2701528.0517 | 1210263.9757
61 | 2701196.2853 | 1209757.4669 | 2701197.1007 | 1209758.471 | 2701201.7872 | 1209764.5436 | 2701210.4524 | 1209773.5857 | 2701213.6317 | 1209778.4208 | 2701214.3083 | 1209784.1026
62 | 2701220.502 | 1209792.8807 | 2701214.9292 | 1209789.317 | 2701214.3083 | 1209784.1026
63 | 2701218.6157 | 1209796.0732 | 2701220.502 | 1209792.8807
64 | 2701235.3662 | 1209798.6035 | 2701228.8687 | 1209796.6697 | 2701220.502 | 1209792.8807
65 | 2701218.6157 | 1209796.0732 | 2701220.9587 | 1209806.2867 | 2701222.3278 | 1209814.6613
66 | 2701218.6157 | 1209796.0732 | 2701210.2164 | 1209798.6881 | 2701206.2355 | 1209799.917
67 | 2701224.2907 | 1209826.6685 | 2701222.3278 | 1209814.6613
68 | 2701239.4193 | 1209779.9042 | 2701250.5198 | 1209792.6406
69 | 2701229.8341 | 1209839.2157 | 2701225.8072 | 1209835.9451 | 2701224.2907 | 1209826.6685
70 | 2701283.3083 | 1209830.2613 | 2701250.5198 | 1209792.6406
71 | 2701554.6755 | 1210428.2926 | 2701568.546 | 1210433.3307
72 | 2701554.6755 | 1210428.2926 | 2701548.5258 | 1210426.0589
73 | 2701600.0839 | 1210444.7859 | 2701568.546 | 1210433.3307
74 | 2701531.0243 | 1210419.702 | 2701548.5258 | 1210426.0589
75 | 2701600.0839 | 1210444.7859 | 2701590.5827 | 1210462.1473 | 2701589.0869 | 1210464.5168
76 | 2701567.1252 | 1210488.0585 | 2701576.2946 | 1210480.7281 | 2701582.5204 | 1210474.919 | 2701589.0869 | 1210464.5168
77 | 2701567.1252 | 1210488.0585 | 2701563.1938 | 1210491.2013 | 2701556.3935 | 1210494.5991 | 2701549.5186 | 1210497.0171 | 2701542.4812 | 1210497.3753 | 2701533.4238 | 1210495.8312
78 | 2701570.571 | 1210331.6712 | 2701573.5809 | 1210340.6175
79 | 2701573.5809 | 1210340.6175 | 2701565.157 | 1210345.1551 | 2701562.1334 | 1210349.0619 | 2701557.3321 | 1210355.5847 | 2701553.1854 | 1210359.3524
80 | 2701570.571 | 1210331.6712 | 2701564.4104 | 1210329.1868 | 2701560.5303 | 1210325.0318
81 | 2701553.1854 | 1210359.3524 | 2701551.8424 | 1210360.5725 | 2701551.1433 | 1210360.7082
82 | 2701518.9491 | 1210488.3091 | 2701527.2603 | 1210493.08 | 2701533.4238 | 1210495.8312 | 2701533.4238 | 1210495.8312
83 | 2701560.5303 | 1210325.0318 | 2701551.3906 | 1210315.2444 | 2701548.5693 | 1210311.7863
84 | 2701540.8025 | 1210359.8066 | 2701548.4714 | 1210361.2267 | 2701551.1433 | 1210360.7082
85 | 2701498.5309 | 1210459.8013 | 2701492.2762 | 1210473.1264 | 2701511.2109 | 1210483.8671 | 2701518.9491 | 1210488.3091
86 | 2701498.5309 | 1210459.8013 | 2701459.9976 | 1210454.5312 | 2701452.8817 | 1210455.0327 | 2701452.5784 | 1210454.8666
87 | 2701437.705 | 1210427.7912 | 2701438.9717 | 1210433.5479 | 2701440.4086 | 1210442.4675 | 2701442.711 | 1210447.4323 | 2701445.4031 | 1210450.9361 | 2701452.5784 | 1210454.8666
88 | 2701452.5784 | 1210454.8666 | 2701436.6471 | 1210533.4553
89 | 2701540.8025 | 1210359.8066 | 2701532.147 | 1210358.2037
90 | 2701529.1634 | 1210357.6512 | 2701532.147 | 1210358.2037
91 | 2701548.5693 | 1210311.7863 | 2701547.9132 | 1210310.9822 | 2701545.0331 | 1210305.5739 | 2701541.9684 | 1210299.8399 | 2701536.9079 | 1210286.7031
92 | 2701484.3559 | 1210116.6877 | 2701496.9957 | 1210115.0237 | 2701503.1481 | 1210113.0937 | 2701516.7052 | 1210107.1202 | 2701532.9248 | 1210100.5916 | 2701543.898 | 1210096.809
93 | 2701536.9079 | 1210286.7031 | 2701534.3955 | 1210280.181
94 | 2701427.9225 | 1210381.6563 | 2701429.382 | 1210392.2339 | 2701435.2354 | 1210413.6706 | 2701435.8529 | 1210419.3739 | 2701437.705 | 1210427.7912
95 | 2701436.6471 | 1210533.4553 | 2701452.1474 | 1210544.2047 | 2701454.8109 | 1210547.5968
96 | 2701379.9988 | 1210202.429 | 2701375.3777 | 1210204.6187 | 2701373.2874 | 1210207.7409 | 2701371.4857 | 1210211.7687 | 2701370.7039 | 1210215.7248 | 2701370.6487 | 1210218.9706 | 2701371.6439 | 1210244.4942 | 2701372.0204 | 1210258.1212 | 2701371.934 | 1210263.201 | 2701370.8034 | 1210269.7864 | 2701366.2424 | 1210280.0716 | 2701359.7673 | 1210292.9484 | 2701354.888 | 1210301.8384 | 2701343.637 | 1210316.1795 | 2701333.6342 | 1210334.9115 | 2701326.4374 | 1210344.6405 | 2701324.6942 | 1210348.0114
97 | 2701379.9988 | 1210202.429 | 2701351.4497 | 1210209.8492 | 2701342.9444 | 1210207.9923
98 | 2701458.5385 | 1210557.629 | 2701457.0695 | 1210552.0049 | 2701454.8109 | 1210547.5968 | 2701454.8109 | 1210547.5968
99 | 2701531.6019 | 1210706.3805 | 2701528.0101 | 1210700.8155 | 2701526.5464 | 1210696.154 | 2701523.3932 | 1210683.5804 | 2701520.502 | 1210676.6042 | 2701518.2261 | 1210673.6634 | 2701515.3681 | 1210670.9796 | 2701508.4253 | 1210665.7911 | 2701504.7147 | 1210661.8475 | 2701501.0589 | 1210656.9152 | 2701496.0621 | 1210648.591 | 2701489.6241 | 1210637.8629 | 2701480.5622 | 1210620.5189 | 2701473.5659 | 1210605.0669 | 2701467.9644 | 1210591.1842 | 2701465.0342 | 1210582.4727 | 2701462.1221 | 1210571.3488 | 2701458.5385 | 1210557.629
100 | 2701531.6019 | 1210706.3805 | 2701537.8251 | 1210707.843 | 2701560.1901 | 1210717.5193 | 2701568.408 | 1210721.0502
101 | 2701358.7901 | 1210420.1982 | 2701355.3745 | 1210411.4008 | 2701357.0834 | 1210400.7557 | 2701360.3645 | 1210387.5022 | 2701358.8653 | 1210379.549 | 2701351.2442 | 1210372.2033 | 2701339.5434 | 1210370.9815 | 2701335.1929 | 1210368.8839 | 2701331.471 | 1210359.7699 | 2701326.9696 | 1210354.9234 | 2701324.6773 | 1210352.038 | 2701324.1973 | 1210348.9722 | 2701324.6942 | 1210348.0114
102 | 2701297.7502 | 1210157.0784 | 2701301.2854 | 1210161.0856 | 2701303.9623 | 1210165.5008 | 2701305.5324 | 1210169.2856 | 2701306.4852 | 1210173.1601 | 2701307.4499 | 1210176.3342 | 2701312.1002 | 1210186.2979 | 2701319.1422 | 1210202.2397 | 2701321.1921 | 1210205.5212 | 2701324.0384 | 1210208.0157 | 2701326.3608 | 1210209.5785 | 2701329.2501 | 1210210.4392 | 2701331.9479 | 1210210.4851 | 2701334.6087 | 1210210.03 | 2701342.9444 | 1210207.9923
103 | 2701568.408 | 1210721.0502 | 2701569.298 | 1210721.4326 | 2701573.2226 | 1210723.05

## bus_geodata
| x | y | coords
0 | 2702254.5362 | 1209778.4221
1 | 2702239.9772 | 1209734.5531
2 | 2702341.1716 | 1209822.7827
3 | 2702413.7375 | 1209445.9533
4 | 2702263.7896 | 1209878.2529
5 | 2701625.005 | 1209881.8444
6 | 2701568.3607 | 1209807.6127
7 | 2701925.7282 | 1209852.1705
8 | 2701782.4047 | 1209582.6997
9 | 2701944.5626 | 1209886.7342
10 | 2702029.0319 | 1210086.9553
11 | 2701532.0721 | 1209852.4264
12 | 2701851.1794 | 1209983.8978
13 | 2701988.1863 | 1210063.4184
14 | 2701787.3898 | 1210064.624
15 | 2701567.6908 | 1210015.6915
16 | 2701469.6535 | 1209763.5203
17 | 2701542.1978 | 1210017.6616
18 | 2701466.7612 | 1209759.9511
19 | 2701507.4747 | 1210009.8731
20 | 2701467.944 | 1209799.4543
21 | 2701367.1751 | 1209458.6713
22 | 2701254.607 | 1209725.1341
23 | 2701247.5151 | 1209716.5886
24 | 2701271.5196 | 1209745.5134
25 | 2701237.5344 | 1209705.5107
26 | 2701418.5762 | 1209862.8369
27 | 2701280.3359 | 1209756.4039
28 | 2701287.5311 | 1209765.3236
29 | 2701237.8787 | 1209763.0103
30 | 2701298.6151 | 1209779.0641
31 | 2701235.427 | 1209767.6254
32 | 2701309.6178 | 1209792.7039
33 | 2701232.8211 | 1209772.5311
34 | 2701345.768 | 1209552.64
35 | 2701323.92 | 1209530.449
36 | 2701472.4269 | 1210019.8395
37 | 2701375.4149 | 1209874.2656
38 | 2701322.8494 | 1209809.1068
39 | 2701399.9538 | 1209904.6829
40 | 2701417.1872 | 1209926.6244
41 | 2701291.0536 | 1209981.7133
42 | 2701462.9834 | 1209982.4756
43 | 2701285.8172 | 1210000.7781
44 | 2701467.9252 | 1209994.5773
45 | 2701180.8906 | 1209940.071
46 | 2701315.0017 | 1210062.5054
47 | 2701472.0629 | 1210016.5434
48 | 2701318.6999 | 1210071.588
49 | 2701322.0109 | 1210077.7017
50 | 2701332.5946 | 1210089.6786
51 | 2701345.1111 | 1210093.7993
52 | 2701420.8983 | 1210182.21
53 | 2701391.4477 | 1210201.0559
54 | 2701528.0517 | 1210263.9757
55 | 2701469.3283 | 1210223.4289
56 | 2701196.2853 | 1209757.4669
57 | 2701214.3083 | 1209784.1026
58 | 2701220.502 | 1209792.8807
59 | 2701218.6157 | 1209796.0732
60 | 2701235.3662 | 1209798.6035
61 | 2701222.3278 | 1209814.6613
62 | 2701206.2355 | 1209799.917
63 | 2701239.4193 | 1209779.9042
64 | 2701224.2907 | 1209826.6685
65 | 2701250.5198 | 1209792.6406
66 | 2701229.8341 | 1209839.2157
67 | 2701283.3083 | 1209830.2613
68 | 2701554.6755 | 1210428.2926
69 | 2701568.546 | 1210433.3307
70 | 2701548.5258 | 1210426.0589
71 | 2701600.0839 | 1210444.7859
72 | 2701531.0243 | 1210419.702
73 | 2701589.0869 | 1210464.5168
74 | 2701567.1252 | 1210488.0585
75 | 2701573.5808 | 1210340.6175
76 | 2701570.571 | 1210331.6712
77 | 2701553.1854 | 1210359.3524
78 | 2701533.4238 | 1210495.8312
79 | 2701560.5303 | 1210325.0318
80 | 2701551.1433 | 1210360.7082
81 | 2701498.5309 | 1210459.8013
82 | 2701518.9491 | 1210488.3091
83 | 2701452.5784 | 1210454.8666
84 | 2701540.8025 | 1210359.8066
85 | 2701532.147 | 1210358.2037
86 | 2701529.1634 | 1210357.6512
87 | 2701548.5693 | 1210311.7863
88 | 2701484.3559 | 1210116.6877
89 | 2701543.898 | 1210096.809
90 | 2701536.9079 | 1210286.7031
91 | 2701437.705 | 1210427.7912
92 | 2701436.6471 | 1210533.4553
93 | 2701379.9988 | 1210202.429
94 | 2701427.9225 | 1210381.6563
95 | 2701534.3955 | 1210280.181
96 | 2701458.5385 | 1210557.629
97 | 2701454.8109 | 1210547.5968
98 | 2701531.6019 | 1210706.3805
99 | 2701324.6942 | 1210348.0114
100 | 2701342.9444 | 1210207.9923
101 | 2701358.7901 | 1210420.1982
102 | 2701297.7502 | 1210157.0784
103 | 2701568.408 | 1210721.0502
104 | 2701573.2226 | 1210723.05
105 | 2701498.5309 | 1210459.8013

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97049 | -0.21159 | 0.00021626 | 5.42e-05
1 | 0.97039 | -0.21233 | 0 | 0
2 | 0.9706 | -0.21074 | 0 | 0
3 | 0.97014 | -0.21419 | 0.00050357 | 0.00012621
4 | 0.97071 | -0.20988 | 0.00068901 | 0.00017268
5 | 0.97257 | -0.19478 | 0.0014926 | 0.00037407
6 | 0.97278 | -0.1933 | 0 | 0
7 | 0.97151 | -0.20371 | 0 | 0
8 | 0.97129 | -0.20539 | 0.0005036 | 0.00012621
9 | 0.97162 | -0.20286 | 0.00048495 | 0.00012154
10 | 0.97239 | -0.19698 | 0 | 0
11 | 0.9729 | -0.19239 | 0 | 0
12 | 0.9732 | -0.1908 | 0.00028789 | 7.2152e-05
13 | 0.97258 | -0.19558 | 0 | 0
14 | 0.97366 | -0.18724 | 0 | 0
15 | 0.97454 | -0.18043 | 0.00074732 | 0.0001873
16 | 0.97221 | -0.19742 | 0.0010438 | 0.00026161
17 | 0.97489 | -0.17787 | 0.0012117 | 0.00030367
18 | 0.97219 | -0.19758 | 0 | 0
19 | 0.97544 | -0.17382 | 0.00047355 | 0.00011868
20 | 0.97211 | -0.19812 | 0.0012767 | 0.00031997
21 | 0.97125 | -0.20441 | 0 | 0
22 | 0.97102 | -0.20542 | 0.0016084 | 0.00040309
23 | 0.97092 | -0.20615 | 0.00060953 | 0.00015276
24 | 0.97132 | -0.20325 | 0 | 0
25 | 0.9708 | -0.20702 | 0.0055389 | 0.0013882
26 | 0.97111 | -0.20476 | 0.00072564 | 0.00018186
27 | 0.97149 | -0.20199 | 0 | 0
28 | 0.97174 | -0.20019 | 0.00054397 | 0.00013633
29 | 0.97108 | -0.20496 | 0.00043634 | 0.00010936
30 | 0.97214 | -0.19732 | 0.00053362 | 0.00013374
31 | 0.97104 | -0.20529 | 0.00041535 | 0.0001041
32 | 0.97255 | -0.19437 | 0.00030069 | 7.5359e-05
33 | 0.97099 | -0.20561 | 0 | 0
34 | 0.97095 | -0.20662 | 0.0011742 | 0.00029428
35 | 0.97091 | -0.20693 | 0.00081614 | 0.00020454
36 | 0.97573 | -0.17165 | 0 | 0
37 | 0.97513 | -0.17584 | 0.00082734 | 0.00020735
38 | 0.97305 | -0.19075 | 0.0006864 | 0.00017203
39 | 0.97614 | -0.16855 | 0 | 0
40 | 0.97687 | -0.16337 | 0 | 0
41 | 0.98092 | -0.13414 | 0.0011136 | 0.0002791
42 | 0.9761 | -0.16894 | 0.00082823 | 0.00020757
43 | 0.98141 | -0.13063 | 0 | 0
44 | 0.97597 | -0.16989 | 0.0007136 | 0.00017885
45 | 0.98127 | -0.13166 | 0.00080866 | 0.00020267
46 | 0.98321 | -0.11777 | 0 | 0
47 | 0.97576 | -0.17144 | 0.00097767 | 0.00024503
48 | 0.98346 | -0.11602 | 0.001059 | 0.0002654
49 | 0.98363 | -0.11474 | 0 | 0
50 | 0.98405 | -0.11179 | 0 | 0
51 | 0.98439 | -0.10935 | 0.0016695 | 0.00041842
52 | 0.98779 | -0.085144 | 0 | 0
53 | 0.98956 | -0.072687 | 0 | 0
54 | 0.98103 | -0.13297 | 0.00063528 | 0.00015922
55 | 0.98773 | -0.085592 | 0.00068475 | 0.00017162
56 | 0.97078 | -0.20713 | 0.00075704 | 0.00018973
57 | 0.97082 | -0.20686 | 0.00082782 | 0.00020747
58 | 0.97085 | -0.20666 | 0 | 0
59 | 0.97084 | -0.20673 | 0 | 0
60 | 0.97083 | -0.20682 | 0.00095511 | 0.00023937
61 | 0.9708 | -0.20699 | 0.00042573 | 0.0001067
62 | 0.97083 | -0.20677 | 0.0003332 | 8.3507e-05
63 | 0.97097 | -0.20575 | 0.00058632 | 0.00014695
64 | 0.97079 | -0.2071 | 0.0004246 | 0.00010641
65 | 0.97096 | -0.20589 | 0.00051281 | 0.00012852
66 | 0.97078 | -0.20716 | 0.00043335 | 0.00010861
67 | 0.97094 | -0.20601 | 0.00022643 | 5.6748e-05
68 | 0.98296 | -0.11948 | 0.0037215 | 0.00093269
69 | 0.98329 | -0.11717 | 0.0043015 | 0.0010781
70 | 0.98285 | -0.12026 | 0.00803 | 0.0020125
71 | 0.98424 | -0.11042 | 0 | 0
72 | 0.98276 | -0.12092 | 0.0034427 | 0.00086283
73 | 0.98487 | -0.10588 | 0.0021074 | 0.00052817
74 | 0.98589 | -0.098651 | 0.0068687 | 0.0017215
75 | 0.97753 | -0.15794 | 0 | 0
76 | 0.97782 | -0.15584 | 0 | 0
77 | 0.97665 | -0.16423 | 0.0032212 | 0.0008073
78 | 0.98739 | -0.088092 | 0.0032758 | 0.00082099
79 | 0.9782 | -0.1531 | 0.0025749 | 0.00064533
80 | 0.97658 | -0.16471 | 0.0018736 | 0.00046957
81 | 0.99055 | -0.06575 | 0 | 0
82 | 0.98814 | -0.082785 | 0.0050234 | 0.001259
83 | 0.99302 | -0.048438 | 0.0028163 | 0.00070583
84 | 0.97633 | -0.16649 | 0.0028065 | 0.00070339
85 | 0.97616 | -0.16773 | 0.0052596 | 0.0013182
86 | 0.97612 | -0.16799 | 0.0081568 | 0.0020443
87 | 0.97883 | -0.14865 | 0.0035149 | 0.00088091
88 | 0.9756 | -0.17265 | 0 | 0
89 | 0.97551 | -0.17329 | 0.00096257 | 0.00024124
90 | 0.97994 | -0.14073 | 0.0016247 | 0.00040719
91 | 0.99577 | -0.029259 | 0.0083925 | 0.0021033
92 | 0.98424 | -0.11029 | 0.028313 | 0.0070958
93 | 0.98944 | -0.07356 | 0 | 0
94 | 1 | 0 | -0.20428 | -0.051397
95 | 0.98023 | -0.13862 | 0.0022681 | 0.00056845
96 | 0.98245 | -0.12303 | 0.0015583 | 0.00039054
97 | 0.98265 | -0.12158 | 0.034147 | 0.0085582
98 | 0.97963 | -0.14313 | 0 | 0
99 | 0.98824 | -0.082069 | 0.0035697 | 0.00089465
100 | 0.98934 | -0.074274 | 0.00046089 | 0.00011551
101 | 0.98804 | -0.083544 | 0.001539 | 0.0003857
102 | 0.98919 | -0.075359 | 0.0013636 | 0.00034175
103 | 0.97896 | -0.14788 | 0.008011 | 0.0020077
104 | 0.97894 | -0.14807 | 0.0034793 | 0.000872
105 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00050375 | 0.00012051 | -0.0005037 | -0.0001221 | 4.8032e-08 | -1.5829e-06 | 0.00077035 | 0.00077091 | 0.00077091 | 0.97049 | -0.21159 | 0.97039 | -0.21233 | 0.28552
1 | -0.00072001 | -0.00017471 | 0.00072009 | 0.00017345 | 7.9393e-08 | -1.2649e-06 | 0.0011019 | 0.0011015 | 0.0011019 | 0.97049 | -0.21159 | 0.9706 | -0.21074 | 0.40812
2 | 0.0005037 | 0.0001221 | -0.00050357 | -0.00012621 | 1.2516e-07 | -4.1125e-06 | 0.00077091 | 0.00077239 | 0.00077239 | 0.97039 | -0.21233 | 0.97014 | -0.21419 | 0.28607
3 | -0.00072009 | -0.00017345 | 0.00072017 | 0.00017219 | 7.9142e-08 | -1.2622e-06 | 0.0011015 | 0.001101 | 0.0011015 | 0.9706 | -0.21074 | 0.97071 | -0.20988 | 0.40795
4 | -0.0014092 | -0.00034487 | 0.0014103 | 0.00034046 | 1.1358e-06 | -4.4062e-06 | 0.0021572 | 0.0021555 | 0.0021572 | 0.97071 | -0.20988 | 0.97151 | -0.20371 | 0.79896
5 | -0.0014926 | -0.00037407 | 0.0014929 | 0.00037303 | 3.0417e-07 | -1.0434e-06 | 0.0022836 | 0.0022832 | 0.0022836 | 0.97257 | -0.19478 | 0.97278 | -0.1933 | 0.84577
6 | -0.0014929 | -0.00037303 | 0.0014931 | 0.00037238 | 1.8737e-07 | -6.432e-07 | 0.0022832 | 0.0022829 | 0.0022832 | 0.97278 | -0.1933 | 0.9729 | -0.19239 | 0.84562
7 | 0.00050372 | 0.00012247 | -0.0005036 | -0.00012621 | 1.1355e-07 | -3.7475e-06 | 0.00077017 | 0.00077152 | 0.00077152 | 0.97151 | -0.20371 | 0.97129 | -0.20539 | 0.28575
8 | -0.001914 | -0.00046293 | 0.0019142 | 0.00046252 | 2.1022e-07 | -4.066e-07 | 0.0029257 | 0.0029255 | 0.0029257 | 0.97151 | -0.20371 | 0.97162 | -0.20286 | 1.0836
9 | -0.0023992 | -0.00058406 | 0.002401 | 0.00058205 | 1.8403e-06 | -2.0097e-06 | 0.0036682 | 0.0036672 | 0.0036682 | 0.97162 | -0.20286 | 0.97239 | -0.19698 | 1.3586
10 | -0.002401 | -0.00058205 | 0.0024015 | 0.00058157 | 4.3634e-07 | -4.7735e-07 | 0.0036672 | 0.003667 | 0.0036672 | 0.97239 | -0.19698 | 0.97258 | -0.19558 | 1.3582
11 | -0.0058095 | -0.0014473 | 0.005819 | 0.0014486 | 9.5064e-06 | 1.2542e-06 | 0.0088823 | 0.0088815 | 0.0088823 | 0.9729 | -0.19239 | 0.97454 | -0.18043 | 3.2898
12 | 0.0043165 | 0.001075 | -0.0043135 | -0.0010752 | 2.9699e-06 | -2.1372e-07 | 0.0065994 | 0.0065999 | 0.0065999 | 0.9729 | -0.19239 | 0.97221 | -0.19742 | 2.4444
13 | 0.0024029 | 0.00057995 | -0.0024015 | -0.00058157 | 1.4843e-06 | -1.6262e-06 | 0.0036662 | 0.003667 | 0.003667 | 0.9732 | -0.1908 | 0.97258 | -0.19558 | 1.3581
14 | -0.0026908 | -0.0006521 | 0.0026921 | 0.00065111 | 1.2418e-06 | -9.8971e-07 | 0.0041064 | 0.0041059 | 0.0041064 | 0.9732 | -0.1908 | 0.97366 | -0.18724 | 1.5209
15 | -0.0026921 | -0.00065111 | 0.0026944 | 0.00064922 | 2.3672e-06 | -1.8915e-06 | 0.0041059 | 0.0041049 | 0.0041059 | 0.97366 | -0.18724 | 0.97454 | -0.18043 | 1.5207
16 | -0.0092608 | -0.0022851 | 0.009264 | 0.002286 | 3.1843e-06 | 9.0604e-07 | 0.014127 | 0.014127 | 0.014127 | 0.97454 | -0.18043 | 0.97489 | -0.17787 | 5.2324
17 | 0.0032697 | 0.00081356 | -0.0032696 | -0.00081359 | 7.1731e-08 | -2.9376e-08 | 0.0050023 | 0.0050023 | 0.0050023 | 0.97221 | -0.19742 | 0.97219 | -0.19758 | 1.8527
18 | -0.010476 | -0.0025897 | 0.010481 | 0.0025914 | 5.7275e-06 | 1.7543e-06 | 0.015977 | 0.015976 | 0.015977 | 0.97489 | -0.17787 | 0.97544 | -0.17382 | 5.9173
19 | 0.0012768 | 0.00031951 | -0.0012767 | -0.00031997 | 9.4937e-08 | -4.5748e-07 | 0.001954 | 0.0019542 | 0.0019542 | 0.97219 | -0.19758 | 0.97211 | -0.19812 | 0.72379
20 | 0.0019928 | 0.00049408 | -0.001991 | -0.00049734 | 1.8587e-06 | -3.2545e-06 | 0.0030482 | 0.0030497 | 0.0030497 | 0.97219 | -0.19758 | 0.97125 | -0.20441 | 1.1295
21 | -0.010955 | -0.0027101 | 0.010958 | 0.0027104 | 3.1947e-06 | 3.117e-07 | 0.016699 | 0.016699 | 0.016699 | 0.97544 | -0.17382 | 0.97573 | -0.17165 | 3.0924
22 | 0.001991 | 0.00049734 | -0.0019903 | -0.00049839 | 6.0468e-07 | -1.0563e-06 | 0.0030497 | 0.0030501 | 0.0030501 | 0.97125 | -0.20441 | 0.97095 | -0.20662 | 1.1297
23 | 0.0061497 | 0.0015411 | -0.0061491 | -0.001541 | 6.1542e-07 | 9.9348e-08 | 0.009424 | 0.009424 | 0.009424 | 0.97102 | -0.20542 | 0.97092 | -0.20615 | 3.4904
24 | -0.0077581 | -0.0019442 | 0.0077604 | 0.0019448 | 2.3357e-06 | 5.7065e-07 | 0.011889 | 0.011889 | 0.011889 | 0.97102 | -0.20542 | 0.97132 | -0.20325 | 4.4032
25 | 0.0055396 | 0.0013883 | -0.0055389 | -0.0013882 | 6.7087e-07 | 7.3581e-08 | 0.0084899 | 0.0084899 | 0.0084899 | 0.97092 | -0.20615 | 0.9708 | -0.20702 | 3.1444
26 | 0.00072579 | 0.00017952 | -0.00072564 | -0.00018186 | 1.4941e-07 | -2.3411e-06 | 0.001111 | 0.0011119 | 0.0011119 | 0.97132 | -0.20325 | 0.97111 | -0.20476 | 0.41181
27 | -0.0084862 | -0.0021243 | 0.0084877 | 0.0021247 | 1.476e-06 | 3.944e-07 | 0.013 | 0.012999 | 0.013 | 0.97132 | -0.20325 | 0.97149 | -0.20199 | 4.8146
28 | -0.014826 | -0.0037102 | 0.014829 | 0.0037115 | 3.6869e-06 | 1.2761e-06 | 0.022706 | 0.022706 | 0.022706 | 0.97149 | -0.20199 | 0.97174 | -0.20019 | 8.4097
29 | 0.006338 | 0.0015855 | -0.0063354 | -0.0015851 | 2.5981e-06 | 4.5234e-07 | 0.0097067 | 0.0097069 | 0.0097069 | 0.97149 | -0.20199 | 0.97108 | -0.20496 | 3.5952
30 | -0.015373 | -0.0038478 | 0.015379 | 0.00385 | 6.1038e-06 | 2.1288e-06 | 0.023539 | 0.023539 | 0.023539 | 0.97174 | -0.20019 | 0.97214 | -0.19732 | 8.7182
31 | 0.0058991 | 0.0014757 | -0.0058988 | -0.0014757 | 2.6639e-07 | 3.7809e-08 | 0.0090383 | 0.0090383 | 0.0090383 | 0.97108 | -0.20496 | 0.97104 | -0.20529 | 3.3475
32 | -0.015913 | -0.0039837 | 0.01592 | 0.003986 | 6.4869e-06 | 2.2776e-06 | 0.024356 | 0.024356 | 0.024356 | 0.97214 | -0.19732 | 0.97255 | -0.19437 | 9.0207
33 | 0.0054835 | 0.0013716 | -0.0054832 | -0.0013716 | 2.4469e-07 | 2.5397e-08 | 0.0084019 | 0.0084019 | 0.0084019 | 0.97104 | -0.20529 | 0.97099 | -0.20561 | 3.1118
34 | -0.01622 | -0.0040613 | 0.016228 | 0.0040642 | 8.0983e-06 | 2.8531e-06 | 0.024816 | 0.024816 | 0.024816 | 0.97255 | -0.19437 | 0.97305 | -0.19075 | 9.1911
35 | 0.0013256 | 0.00033128 | -0.0013256 | -0.0003314 | 2.5473e-08 | -1.126e-07 | 0.0020311 | 0.0020311 | 0.0020311 | 0.97099 | -0.20561 | 0.97097 | -0.20575 | 0.75227
36 | 0.0041576 | 0.0010403 | -0.004157 | -0.0010403 | 6.0212e-07 | -6.2439e-08 | 0.0063708 | 0.0063709 | 0.0063709 | 0.97099 | -0.20561 | 0.97085 | -0.20666 | 2.3596
37 | 0.00081617 | 0.00020412 | -0.00081614 | -0.00020454 | 3.4676e-08 | -4.26e-07 | 0.0012507 | 0.0012508 | 0.0012508 | 0.97095 | -0.20662 | 0.97091 | -0.20693 | 0.46327
38 | -0.011921 | -0.0029498 | 0.011921 | 0.0029498 | 3.4144e-07 | 4.8481e-08 | 0.018166 | 0.018166 | 0.018166 | 0.97573 | -0.17165 | 0.97576 | -0.17144 | 3.3641
39 | 0.00096279 | 0.00023932 | -0.00096266 | -0.00024049 | 1.312e-07 | -1.1683e-06 | 0.0014676 | 0.001468 | 0.001468 | 0.97573 | -0.17165 | 0.9756 | -0.17265 | 0.54371
40 | 0.01695 | 0.0042486 | -0.016915 | -0.0042362 | 3.4949e-05 | 1.24e-05 | 0.025865 | 0.025865 | 0.025865 | 0.97513 | -0.17584 | 0.97305 | -0.19075 | 9.5798
41 | -0.017777 | -0.004456 | 0.017795 | 0.0044624 | 1.7946e-05 | 6.4144e-06 | 0.027128 | 0.027127 | 0.027128 | 0.97513 | -0.17584 | 0.97614 | -0.16855 | 10.0472
42 | -0.017795 | -0.0044624 | 0.017808 | 0.004467 | 1.2798e-05 | 4.5737e-06 | 0.027127 | 0.027127 | 0.027127 | 0.97614 | -0.16855 | 0.97687 | -0.16337 | 10.0472
43 | -0.032264 | -0.0080514 | 0.032394 | 0.0080971 | 0.0001299 | 4.5627e-05 | 0.049134 | 0.049132 | 0.049134 | 0.97687 | -0.16337 | 0.98092 | -0.13414 | 9.0988
44 | 0.014456 | 0.0035845 | -0.014445 | -0.0035821 | 1.0916e-05 | 2.3911e-06 | 0.022007 | 0.022007 | 0.022007 | 0.97687 | -0.16337 | 0.9761 | -0.16894 | 4.0754
45 | -0.033507 | -0.0083762 | 0.033524 | 0.0083819 | 1.622e-05 | 5.73e-06 | 0.050822 | 0.050821 | 0.050822 | 0.98092 | -0.13414 | 0.98141 | -0.13063 | 9.4114
46 | 0.013617 | 0.0033745 | -0.013615 | -0.0033742 | 1.763e-06 | 3.4986e-07 | 0.020745 | 0.020745 | 0.020745 | 0.9761 | -0.16894 | 0.97597 | -0.16989 | 3.8416
47 | 0.00080877 | 0.00020117 | -0.00080866 | -0.00020267 | 1.1435e-07 | -1.4964e-06 | 0.0012257 | 0.0012263 | 0.0012263 | 0.98141 | -0.13063 | 0.98127 | -0.13166 | 0.45417
48 | -0.034332 | -0.0085831 | 0.034393 | 0.0086047 | 6.0931e-05 | 2.161e-05 | 0.052047 | 0.052046 | 0.052047 | 0.98141 | -0.13063 | 0.98321 | -0.11777 | 9.6383
49 | 0.012902 | 0.0031953 | -0.012899 | -0.0031948 | 2.7014e-06 | 4.7907e-07 | 0.019657 | 0.019657 | 0.019657 | 0.97597 | -0.16989 | 0.97576 | -0.17144 | 3.6402
50 | -0.034393 | -0.0086047 | 0.034402 | 0.0086076 | 8.3052e-06 | 2.945e-06 | 0.052046 | 0.052046 | 0.052046 | 0.98321 | -0.11777 | 0.98346 | -0.11602 | 9.6382
51 | -0.035461 | -0.008873 | 0.035467 | 0.0088753 | 6.2435e-06 | 2.2249e-06 | 0.053649 | 0.053649 | 0.053649 | 0.98346 | -0.11602 | 0.98363 | -0.11474 | 9.9349
52 | -0.035467 | -0.0088753 | 0.035481 | 0.0088804 | 1.4446e-05 | 5.1475e-06 | 0.053649 | 0.053648 | 0.053649 | 0.98363 | -0.11474 | 0.98405 | -0.11179 | 9.9349
53 | -0.035481 | -0.0088804 | 0.035493 | 0.0088847 | 1.1959e-05 | 4.261e-06 | 0.053648 | 0.053648 | 0.053648 | 0.98405 | -0.11179 | 0.98439 | -0.10935 | 9.9349
54 | -0.037163 | -0.0093031 | 0.037287 | 0.0093478 | 0.00012463 | 4.4705e-05 | 0.056172 | 0.056171 | 0.056172 | 0.98439 | -0.10935 | 0.98779 | -0.085144 | 10.4022
55 | -0.070241 | -0.017647 | 0.070363 | 0.017693 | 0.00012193 | 4.6002e-05 | 0.10583 | 0.10583 | 0.10583 | 0.98779 | -0.085144 | 0.98956 | -0.072687 | 19.5975
56 | 0.032269 | 0.0081283 | -0.032054 | -0.0080477 | 0.00021439 | 8.0609e-05 | 0.048624 | 0.048625 | 0.048625 | 0.98779 | -0.085144 | 0.98103 | -0.13297 | 18.0093
57 | 0.0006848 | 0.00017082 | -0.00068475 | -0.00017162 | 4.2263e-08 | -7.9865e-07 | 0.0010313 | 0.0010316 | 0.0010316 | 0.98779 | -0.085144 | 0.98773 | -0.085592 | 0.38207
58 | 0.0069407 | 0.0017356 | -0.0069399 | -0.0017354 | 8.3486e-07 | 1.6328e-07 | 0.010435 | 0.010435 | 0.010435 | 0.98956 | -0.072687 | 0.98944 | -0.07356 | 3.865
59 | -0.077304 | -0.019429 | 0.078094 | 0.019728 | 0.0007903 | 0.0002991 | 0.11626 | 0.11626 | 0.11626 | 0.98956 | -0.072687 | 1 | 0 | 21.5299
60 | 0.031419 | 0.0078885 | -0.031394 | -0.0078792 | 2.4669e-05 | 9.2684e-06 | 0.047661 | 0.047662 | 0.047662 | 0.98103 | -0.13297 | 0.98023 | -0.13862 | 17.6524
61 | -0.00075704 | -0.00018973 | 0.00075707 | 0.00018933 | 2.7721e-08 | -3.9732e-07 | 0.0011604 | 0.0011602 | 0.0011604 | 0.97078 | -0.20713 | 0.97082 | -0.20686 | 0.42977
62 | -0.0015849 | -0.0003968 | 0.0015849 | 0.00039667 | 4.3688e-08 | -1.2992e-07 | 0.0024291 | 0.002429 | 0.0024291 | 0.97082 | -0.20686 | 0.97085 | -0.20666 | 0.89965
63 | 0.001617 | 0.00040449 | -0.0016169 | -0.00040453 | 1.4201e-08 | -4.0365e-08 | 0.002478 | 0.002478 | 0.002478 | 0.97085 | -0.20666 | 0.97084 | -0.20673 | 0.91779
64 | 0.00095513 | 0.00023918 | -0.00095511 | -0.00023937 | 2.1292e-08 | -1.887e-07 | 0.0014639 | 0.0014639 | 0.0014639 | 0.97085 | -0.20666 | 0.97083 | -0.20682 | 0.54219
65 | 0.0012837 | 0.00032118 | -0.0012837 | -0.0003214 | 4.5807e-08 | -2.1688e-07 | 0.0019674 | 0.0019675 | 0.0019675 | 0.97084 | -0.20673 | 0.9708 | -0.20699 | 0.7287
66 | 0.0003332 | 8.3348e-05 | -0.0003332 | -8.3507e-05 | 2.1095e-09 | -1.5948e-07 | 0.00051064 | 0.0005107 | 0.0005107 | 0.97084 | -0.20673 | 0.97083 | -0.20677 | 0.18915
67 | 0.00085796 | 0.0002147 | -0.00085795 | -0.00021484 | 1.3128e-08 | -1.4538e-07 | 0.0013149 | 0.001315 | 0.001315 | 0.9708 | -0.20699 | 0.97079 | -0.2071 | 0.48703
68 | 0.00073925 | 0.00018445 | -0.00073924 | -0.00018465 | 1.3525e-08 | -2.0376e-07 | 0.0011326 | 0.0011327 | 0.0011327 | 0.97097 | -0.20575 | 0.97096 | -0.20589 | 0.41951
69 | 0.00043335 | 0.00010843 | -0.00043335 | -0.00010861 | 4.0158e-09 | -1.7881e-07 | 0.00066418 | 0.00066424 | 0.00066424 | 0.97079 | -0.2071 | 0.97078 | -0.20716 | 0.24601
70 | 0.00022643 | 5.6132e-05 | -0.00022643 | -5.6748e-05 | 3.7474e-09 | -6.1577e-07 | 0.00034679 | 0.00034701 | 0.00034701 | 0.97096 | -0.20589 | 0.97094 | -0.20601 | 0.12852
71 | -0.015196 | -0.0038083 | 0.015201 | 0.00381 | 4.8727e-06 | 1.687e-06 | 0.023003 | 0.023003 | 0.023003 | 0.98296 | -0.11948 | 0.98329 | -0.11717 | 8.5198
72 | 0.011474 | 0.0028756 | -0.011473 | -0.0028752 | 1.2318e-06 | 3.9084e-07 | 0.01737 | 0.01737 | 0.01737 | 0.98296 | -0.11948 | 0.98285 | -0.12026 | 6.4333
73 | -0.019502 | -0.004888 | 0.01952 | 0.0048946 | 1.8237e-05 | 6.5881e-06 | 0.029513 | 0.029513 | 0.029513 | 0.98329 | -0.11717 | 0.98424 | -0.11042 | 10.9307
74 | 0.0034431 | 0.00086272 | -0.0034427 | -0.00086283 | 3.1571e-07 | -1.1453e-07 | 0.0052126 | 0.0052127 | 0.0052127 | 0.98285 | -0.12026 | 0.98276 | -0.12092 | 1.9306
75 | -0.01952 | -0.0048946 | 0.019533 | 0.0048991 | 1.2279e-05 | 4.4356e-06 | 0.029513 | 0.029513 | 0.029513 | 0.98424 | -0.11042 | 0.98487 | -0.10588 | 10.9306
76 | -0.02164 | -0.0054272 | 0.021662 | 0.0054352 | 2.1718e-05 | 7.9383e-06 | 0.032697 | 0.032696 | 0.032697 | 0.98487 | -0.10588 | 0.98589 | -0.098651 | 12.1098
77 | -0.02853 | -0.0071566 | 0.028572 | 0.0071723 | 4.184e-05 | 1.5631e-05 | 0.043063 | 0.043063 | 0.043063 | 0.98589 | -0.098651 | 0.98739 | -0.088092 | 15.9494
78 | -0.021344 | -0.0053522 | 0.02135 | 0.0053545 | 6.2174e-06 | 2.2729e-06 | 0.032492 | 0.032492 | 0.032492 | 0.97753 | -0.15794 | 0.97782 | -0.15584 | 12.0339
79 | 0.021344 | 0.0053522 | -0.021326 | -0.0053454 | 1.8584e-05 | 6.7944e-06 | 0.032492 | 0.032492 | 0.032492 | 0.97753 | -0.15794 | 0.97665 | -0.16423 | 12.034
80 | -0.02135 | -0.0053545 | 0.021358 | 0.0053574 | 8.1209e-06 | 2.9687e-06 | 0.032492 | 0.032491 | 0.032492 | 0.97782 | -0.15584 | 0.9782 | -0.1531 | 12.0339
81 | 0.018104 | 0.0045381 | -0.018103 | -0.0045377 | 1.1996e-06 | 4.2976e-07 | 0.027584 | 0.027584 | 0.027584 | 0.97665 | -0.16423 | 0.97658 | -0.16471 | 10.2163
82 | -0.031848 | -0.0079932 | 0.031872 | 0.0080021 | 2.3482e-05 | 8.8223e-06 | 0.048 | 0.048 | 0.048 | 0.98739 | -0.088092 | 0.98814 | -0.082785 | 17.7777
83 | -0.023933 | -0.0060028 | 0.023948 | 0.0060082 | 1.4768e-05 | 5.4558e-06 | 0.036408 | 0.036408 | 0.036408 | 0.9782 | -0.1531 | 0.97883 | -0.14865 | 13.4846
84 | 0.01623 | 0.0040681 | -0.016226 | -0.0040667 | 4.0148e-06 | 1.4125e-06 | 0.024729 | 0.024729 | 0.024729 | 0.97658 | -0.16471 | 0.97633 | -0.16649 | 9.159
85 | 0.036982 | 0.0092941 | -0.036895 | -0.0092611 | 8.7487e-05 | 3.3066e-05 | 0.055564 | 0.055565 | 0.055565 | 0.99055 | -0.06575 | 0.98814 | -0.082785 | 20.5794
86 | -0.036982 | -0.0092941 | 0.037072 | 0.0093279 | 8.9336e-05 | 3.3761e-05 | 0.055564 | 0.055564 | 0.055564 | 0.99055 | -0.06575 | 0.99302 | -0.048438 | 20.5794
87 | -0.11617 | -0.02925 | 0.11648 | 0.029369 | 0.00031217 | 0.00011921 | 0.17412 | 0.17412 | 0.17412 | 0.99302 | -0.048438 | 0.99577 | -0.029259 | 32.2447
88 | 0.076279 | 0.019216 | -0.075625 | -0.018966 | 0.00065413 | 0.00025056 | 0.11434 | 0.11434 | 0.11434 | 0.99302 | -0.048438 | 0.98424 | -0.11029 | 42.3472
89 | 0.013419 | 0.0033633 | -0.013417 | -0.0033625 | 2.2975e-06 | 7.7361e-07 | 0.020452 | 0.020452 | 0.020452 | 0.97633 | -0.16649 | 0.97616 | -0.16773 | 7.5747
90 | 0.0081571 | 0.0020444 | -0.0081568 | -0.0020443 | 2.9274e-07 | 7.4661e-08 | 0.012434 | 0.012434 | 0.012434 | 0.97616 | -0.16773 | 0.97612 | -0.16799 | 4.6053
91 | -0.027463 | -0.0068891 | 0.027493 | 0.0069004 | 3.0179e-05 | 1.1258e-05 | 0.041752 | 0.041751 | 0.041752 | 0.97883 | -0.14865 | 0.97994 | -0.14073 | 15.4635
92 | 0.00096266 | 0.00024049 | -0.00096257 | -0.00024124 | 8.4657e-08 | -7.5331e-07 | 0.001468 | 0.0014683 | 0.0014683 | 0.9756 | -0.17265 | 0.97551 | -0.17329 | 0.54381
93 | -0.029118 | -0.0073076 | 0.029126 | 0.0073108 | 8.5276e-06 | 3.1918e-06 | 0.044219 | 0.044218 | 0.044219 | 0.97994 | -0.14073 | 0.98023 | -0.13862 | 16.3772
94 | -0.12487 | -0.031473 | 0.12539 | 0.031669 | 0.0005137 | 0.00019634 | 0.18666 | 0.18666 | 0.18666 | 0.99577 | -0.029259 | 1 | 0 | 34.5671
95 | 0.047312 | 0.01187 | -0.047238 | -0.011842 | 7.4001e-05 | 2.8168e-05 | 0.071533 | 0.071533 | 0.071533 | 0.98424 | -0.11029 | 0.98265 | -0.12158 | 26.4939
96 | 0.005115 | 0.0012795 | -0.005109 | -0.0012793 | 6.0054e-06 | 2.2309e-07 | 0.0076915 | 0.0076923 | 0.0076923 | 0.98944 | -0.07356 | 0.98824 | -0.082069 | 2.849
97 | 0.0018249 | 0.00045592 | -0.0018247 | -0.00045634 | 1.795e-07 | -4.2158e-07 | 0.0027439 | 0.0027441 | 0.0027441 | 0.98944 | -0.07356 | 0.98934 | -0.074274 | 1.0163
98 | -0.013088 | -0.0032829 | 0.013091 | 0.0032837 | 2.6402e-06 | 8.7911e-07 | 0.019824 | 0.019824 | 0.019824 | 0.98245 | -0.12303 | 0.98265 | -0.12158 | 7.3424
99 | 0.01153 | 0.0028923 | -0.011498 | -0.0028821 | 3.2066e-05 | 1.0206e-05 | 0.017464 | 0.017465 | 0.017465 | 0.98245 | -0.12303 | 0.97963 | -0.14313 | 6.4685
100 | 0.011498 | 0.0028821 | -0.01149 | -0.0028797 | 7.5576e-06 | 2.4072e-06 | 0.017465 | 0.017465 | 0.017465 | 0.97963 | -0.14313 | 0.97896 | -0.14788 | 6.4686
101 | 0.0015393 | 0.00038462 | -0.001539 | -0.0003857 | 3.1327e-07 | -1.0769e-06 | 0.0023173 | 0.0023177 | 0.0023177 | 0.98824 | -0.082069 | 0.98804 | -0.083544 | 0.85842
102 | 0.0013638 | 0.00034083 | -0.0013636 | -0.00034175 | 2.0419e-07 | -9.2012e-07 | 0.0020509 | 0.0020513 | 0.0020513 | 0.98934 | -0.074274 | 0.98919 | -0.075359 | 0.75973
103 | 0.0034794 | 0.00087196 | -0.0034793 | -0.000872 | 9.0991e-08 | -3.0552e-08 | 0.0052886 | 0.0052886 | 0.0052886 | 0.97896 | -0.14788 | 0.97894 | -0.14807 | 1.9588

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20713 | 0.052111

## res_load
| p_mw | q_mvar
0 | 0.00021626 | 5.42e-05
1 | 0.00050357 | 0.00012621
2 | 0.00068901 | 0.00017268
3 | 0.0014926 | 0.00037407
4 | 0.0005036 | 0.00012621
5 | 0.00048495 | 0.00012154
6 | 0.00028789 | 7.2152e-05
7 | 0.00074732 | 0.0001873
8 | 0.0010438 | 0.00026161
9 | 0.0012117 | 0.00030367
10 | 0.00047355 | 0.00011868
11 | 0.0012767 | 0.00031997
12 | 0.0016084 | 0.00040309
13 | 0.00060953 | 0.00015276
14 | 0.0055389 | 0.0013882
15 | 0.00072564 | 0.00018186
16 | 0.00054397 | 0.00013633
17 | 0.00043634 | 0.00010936
18 | 0.00053362 | 0.00013374
19 | 0.00041535 | 0.0001041
20 | 0.00030069 | 7.5359e-05
21 | 0.0011742 | 0.00029428
22 | 0.00081614 | 0.00020454
23 | 0.00082734 | 0.00020735
24 | 0.0006864 | 0.00017203
25 | 0.0011136 | 0.0002791
26 | 0.00082823 | 0.00020757
27 | 0.0007136 | 0.00017885
28 | 0.00080866 | 0.00020267
29 | 0.00097767 | 0.00024503
30 | 0.001059 | 0.0002654
31 | 0.0016695 | 0.00041842
32 | 0.00063528 | 0.00015922
33 | 0.00068475 | 0.00017162
34 | 0.00075704 | 0.00018973
35 | 0.00082782 | 0.00020747
36 | 0.00095511 | 0.00023937
37 | 0.00042573 | 0.0001067
38 | 0.0003332 | 8.3507e-05
39 | 0.00058632 | 0.00014695
40 | 0.0004246 | 0.00010641
41 | 0.00051281 | 0.00012852
42 | 0.00043335 | 0.00010861
43 | 0.00022643 | 5.6748e-05
44 | 0.0037215 | 0.00093269
45 | 0.0043015 | 0.0010781
46 | 0.00803 | 0.0020125
47 | 0.0034427 | 0.00086283
48 | 0.0021074 | 0.00052817
49 | 0.0068687 | 0.0017215
50 | 0.0032212 | 0.0008073
51 | 0.0032758 | 0.00082099
52 | 0.0025749 | 0.00064533
53 | 0.0018736 | 0.00046957
54 | 0.0050234 | 0.001259
55 | 0.0028163 | 0.00070583
56 | 0.0028065 | 0.00070339
57 | 0.0052596 | 0.0013182
58 | 0.0081568 | 0.0020443
59 | 0.0035149 | 0.00088091
60 | 0.00096257 | 0.00024124
61 | 0.0016247 | 0.00040719
62 | 0.0083925 | 0.0021033
63 | 0.028313 | 0.0070958
64 | 0.0028515 | 0.00071465
65 | 0.0022681 | 0.00056845
66 | 0.0015583 | 0.00039054
67 | 0.034147 | 0.0085582
68 | 0.0035697 | 0.00089465
69 | 0.00046089 | 0.00011551
70 | 0.001539 | 0.0003857
71 | 0.0013636 | 0.00034175
72 | 0.008011 | 0.0020077
73 | 0.0034793 | 0.000872

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1