## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1368-3_1_2_node_15 | 0.4 | n |  | TRUE
1 | bus_LV_1368-3_1_2_node_24 | 0.4 | n |  | TRUE
2 | bus_LV_1368-3_1_2_node_22 | 0.4 | n |  | TRUE
3 | bus_LV_1368-3_1_2_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_1368-3_1_2_node_42 | 0.4 | n |  | TRUE
5 | bus_LV_1368-3_1_2_node_43 | 0.4 | n |  | TRUE
6 | bus_LV_1368-3_1_2_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_1368-3_1_2_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_1368-3_1_2_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_1368-3_1_2_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_1368-3_1_2_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1368-3_1_2_node_38 | 0.4 | n |  | TRUE
12 | bus_LV_1368-3_1_2_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_1368-3_1_2_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_1368-3_1_2_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_1368-3_1_2_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_1368-3_1_2_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_1368-3_1_2_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_1368-3_1_2_node_36 | 0.4 | n |  | TRUE
19 | bus_LV_1368-3_1_2_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_1368-3_1_2_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_1368-3_1_2_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_1368-3_1_2_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_1368-3_1_2_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_1368-3_1_2_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_1368-3_1_2_node_46 | 0.4 | n |  | TRUE
26 | bus_LV_1368-3_1_2_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_1368-3_1_2_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_1368-3_1_2_node_54 | 0.4 | n |  | TRUE
29 | bus_LV_1368-3_1_2_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_1368-3_1_2_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_1368-3_1_2_node_57 | 0.4 | n |  | TRUE
32 | bus_LV_1368-3_1_2_node_58 | 0.4 | n |  | TRUE
33 | bus_LV_1368-3_1_2_node_59 | 0.4 | n |  | TRUE
34 | bus_LV_1368-3_1_2_node_60 | 0.4 | n |  | TRUE
35 | bus_LV_1368-3_1_2_node_61 | 0.4 | n |  | TRUE
36 | bus_LV_1368-3_1_2_node_62 | 0.4 | n |  | TRUE
37 | bus_LV_1368-3_1_2_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_1368-3_1_2_node_64 | 0.4 | n |  | TRUE
39 | bus_LV_1368-3_1_2_node_65 | 0.4 | n |  | TRUE
40 | bus_MV_135_0_node_9 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1368-3_1_2_load_15 | 0 | 0.015468 | 0.0038767 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1368-3_1_2_load_24 | 1 | 0.003531 | 0.00088494 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1368-3_1_2_load_22 | 2 | 0.0044527 | 0.0011159 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1368-3_1_2_load_42 | 4 | 0.0018486 | 0.00046329 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1368-3_1_2_load_43 | 5 | 0.0022403 | 0.00056148 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1368-3_1_2_load_44 | 7 | 0.002704 | 0.00067769 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1368-3_1_2_load_23 | 8 | 0.0044655 | 0.0011192 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1368-3_1_2_load_25 | 9 | 0.0018373 | 0.00046046 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1368-3_1_2_load_26 | 10 | 0.0024016 | 0.00060189 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1368-3_1_2_load_38 | 11 | 0.0052503 | 0.0013158 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1368-3_1_2_load_31 | 13 | 0.004729 | 0.0011852 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1368-3_1_2_load_32 | 14 | 0.0044378 | 0.0011122 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1368-3_1_2_load_33 | 15 | 0.0023075 | 0.00057832 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1368-3_1_2_load_34 | 16 | 0.0083797 | 0.0021002 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1368-3_1_2_load_36 | 18 | 0.0016785 | 0.00042067 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1368-3_1_2_load_37 | 19 | 0.0010194 | 0.00025548 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1368-3_1_2_load_53 | 20 | 0.0014388 | 0.00036061 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1368-3_1_2_load_50 | 21 | 0.0011533 | 0.00028903 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1368-3_1_2_load_49 | 22 | 0.0024597 | 0.00061645 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1368-3_1_2_load_51 | 23 | 0.001585 | 0.00039725 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1368-3_1_2_load_52 | 24 | 0.0025802 | 0.00064665 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1368-3_1_2_load_46 | 25 | 0.0028765 | 0.00072091 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1368-3_1_2_load_47 | 26 | 0.0015644 | 0.00039207 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1368-3_1_2_load_48 | 27 | 0.0023913 | 0.00059931 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1368-3_1_2_load_55 | 29 | 0.0064358 | 0.001613 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1368-3_1_2_load_56 | 30 | 0.0028065 | 0.00070337 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1368-3_1_2_load_57 | 31 | 0.0041827 | 0.0010483 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1368-3_1_2_load_58 | 32 | 0.0020981 | 0.00052584 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1368-3_1_2_load_59 | 33 | 0.0024938 | 0.00062501 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1368-3_1_2_load_60 | 34 | 0.0017302 | 0.00043363 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1368-3_1_2_load_61 | 35 | 0.0014714 | 0.00036878 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1368-3_1_2_load_63 | 37 | 0.0018974 | 0.00047554 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1368-3_1_2_load_64 | 38 | 0.0041867 | 0.0010493 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1368-3_1_2_load_65 | 39 | 0.0016424 | 0.00041162 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1368-3_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.06597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1368-3_1_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.0060041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1368-3_1_2_line_2 | NAYY 4x150 SE | 2 | 8 | 0.014277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1368-3_1_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.028464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1368-3_1_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.015688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1368-3_1_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0066231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1368-3_1_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.017405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1368-3_1_2_line_7 | NAYY 4x150 SE | 6 | 25 | 0.024758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1368-3_1_2_line_8 | NAYY 4x150 SE | 8 | 9 | 0.0044548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1368-3_1_2_line_9 | NAYY 4x150 SE | 9 | 10 | 0.023894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1368-3_1_2_line_10 | NAYY 4x150 SE | 10 | 11 | 0.03262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1368-3_1_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.0047752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1368-3_1_2_line_12 | NAYY 4x150 SE | 12 | 23 | 0.035515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1368-3_1_2_line_13 | NAYY 4x150 SE | 12 | 21 | 0.0043246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1368-3_1_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.0013703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1368-3_1_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.049031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1368-3_1_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.014619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1368-3_1_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0040673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1368-3_1_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.006484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1368-3_1_2_line_19 | NAYY 4x150 SE | 17 | 19 | 0.017039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1368-3_1_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.0083467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1368-3_1_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.015573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1368-3_1_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.0012768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1368-3_1_2_line_23 | NAYY 4x150 SE | 22 | 27 | 0.0022343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1368-3_1_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.00018715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1368-3_1_2_line_25 | NAYY 4x150 SE | 24 | 28 | 0.010547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1368-3_1_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.007469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1368-3_1_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.017415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1368-3_1_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.054453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1368-3_1_2_line_29 | NAYY 4x150 SE | 28 | 30 | 0.011635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1368-3_1_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.017881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1368-3_1_2_line_31 | NAYY 4x150 SE | 31 | 32 | 0.032969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1368-3_1_2_line_32 | NAYY 4x150 SE | 32 | 33 | 0.0041546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1368-3_1_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.023395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1368-3_1_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.0062654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1368-3_1_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.0083318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1368-3_1_2_line_36 | NAYY 4x150 SE | 36 | 37 | 0.010853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1368-3_1_2_line_37 | NAYY 4x150 SE | 36 | 38 | 0.024399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1368-3_1_2_line_38 | NAYY 4x150 SE | 38 | 39 | 0.028311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1368-3_1_2_trafo_38 | 0.25 MVA 20/0.4 kV | 40 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2702184.5613 | 1210838.7203 | 2702118.6009 | 1210839.8319
1 | 2702184.5613 | 1210838.7203 | 2702187.6187 | 1210842.6088 | 2702188.221 | 1210843.4782
2 | 2702194.421 | 1210856.1272 | 2702193.5151 | 1210852.0386 | 2702191.9134 | 1210848.8089 | 2702188.221 | 1210843.4782
3 | 2702309.1587 | 1210823.5672 | 2702308.8627 | 1210828.41 | 2702305.701 | 1210851.8092
4 | 2702309.1587 | 1210823.5672 | 2702303.9789 | 1210824.2122 | 2702294.7974 | 1210829.2412
5 | 2702304.8141 | 1210858.3727 | 2702305.701 | 1210851.8092
6 | 2702279.5323 | 1210837.6024 | 2702294.7974 | 1210829.2412
7 | 2702304.8141 | 1210858.3727 | 2702282.6587 | 1210869.4231
8 | 2702195.3847 | 1210860.4765 | 2702194.421 | 1210856.1272
9 | 2702195.3847 | 1210860.4765 | 2702195.3847 | 1210860.4765 | 2702194.9603 | 1210863.9494 | 2702193.6072 | 1210867.9513 | 2702188.8559 | 1210871.9838 | 2702183.9502 | 1210874.824 | 2702181.6839 | 1210878.4433
10 | 2702202.1887 | 1210894.0487 | 2702201.6518 | 1210893.9517 | 2702194.8992 | 1210894.1251 | 2702187.2019 | 1210893.5373 | 2702184.2955 | 1210891.9308 | 2702181.7976 | 1210887.774 | 2702181.06 | 1210882.9135 | 2702181.6839 | 1210878.4433
11 | 2702206.8878 | 1210894.8977 | 2702202.1887 | 1210894.0487
12 | 2702206.8878 | 1210894.8977 | 2702192.0935 | 1210898.6135 | 2702182.506 | 1210903.6528 | 2702178.3336 | 1210912.1092
13 | 2702206.8878 | 1210894.8977 | 2702211.0825 | 1210893.8455
14 | 2702239.3057 | 1210850.963 | 2702239.0298 | 1210849.6207
15 | 2702239.3057 | 1210850.963 | 2702239.8959 | 1210853.8344 | 2702239.3725 | 1210857.7616 | 2702237.9125 | 1210862.6733 | 2702237.1379 | 1210864.8505 | 2702235.096 | 1210866.461 | 2702231.0203 | 1210868.7706 | 2702227.9678 | 1210870.3639 | 2702225.8067 | 1210873.1621 | 2702225.0085 | 1210876.7176 | 2702225.9675 | 1210879.7473 | 2702228.2293 | 1210881.7096 | 2702233.7968 | 1210883.2728 | 2702238.5245 | 1210884.3084
16 | 2702236.0864 | 1210835.3006 | 2702239.0298 | 1210849.6207
17 | 2702242.4976 | 1210885.1788 | 2702238.5245 | 1210884.3084
18 | 2702242.4976 | 1210885.1788 | 2702248.6325 | 1210883.0798
19 | 2702242.4976 | 1210885.1788 | 2702233.9419 | 1210888.112 | 2702226.1878 | 1210890.0568
20 | 2702248.6325 | 1210883.0798 | 2702256.5298 | 1210880.3779
21 | 2702226.1878 | 1210890.0568 | 2702211.0825 | 1210893.8455
22 | 2702257.7379 | 1210879.9646 | 2702256.5298 | 1210880.3779
23 | 2702257.7379 | 1210879.9646 | 2702259.8519 | 1210879.2413
24 | 2702178.2508 | 1210912.277 | 2702178.3336 | 1210912.1092
25 | 2702173.5842 | 1210921.7349 | 2702178.2508 | 1210912.277
26 | 2702282.6587 | 1210869.4231 | 2702275.975 | 1210872.7567
27 | 2702259.8519 | 1210879.2413 | 2702269.7932 | 1210875.84 | 2702275.975 | 1210872.7567
28 | 2702147.592 | 1210901.1643 | 2702137.7776 | 1210906.5779 | 2702155.0956 | 1210923.6975 | 2702162.2366 | 1210924.3647 | 2702168.2454 | 1210921.9103 | 2702173.5842 | 1210921.7349
29 | 2702173.5842 | 1210921.7349 | 2702168.4341 | 1210932.1681
30 | 2702160.5192 | 1210948.2019 | 2702168.4341 | 1210932.1681
31 | 2702160.5192 | 1210948.2019 | 2702159.3083 | 1210950.6551 | 2702156.052 | 1210959.261 | 2702156.2454 | 1210963.5006 | 2702159.1637 | 1210967.52 | 2702170.9736 | 1210968.0341
32 | 2702175.1243 | 1210968.2148 | 2702170.9736 | 1210968.0341
33 | 2702175.1243 | 1210968.2148 | 2702177.2782 | 1210968.3086 | 2702197.8415 | 1210973.6232
34 | 2702197.8415 | 1210973.6232 | 2702203.9076 | 1210975.191
35 | 2702211.9743 | 1210977.2758 | 2702203.9076 | 1210975.191
36 | 2702211.9743 | 1210977.2758 | 2702222.7686 | 1210975.882
37 | 2702211.9743 | 1210977.2758 | 2702228.5504 | 1210982.23 | 2702235.1884 | 1210984.7455
38 | 2702225.6914 | 1211008.8885 | 2702230.5549 | 1211001.4111 | 2702237.278 | 1210991.4304 | 2702237.4039 | 1210988.0747 | 2702235.1884 | 1210984.7455

## bus_geodata
| x | y | coords
0 | 2702118.6009 | 1210839.8319
1 | 2702184.5613 | 1210838.7203
2 | 2702188.221 | 1210843.4782
3 | 2702309.1587 | 1210823.5672
4 | 2702305.701 | 1210851.8092
5 | 2702294.7974 | 1210829.2412
6 | 2702304.8141 | 1210858.3727
7 | 2702279.5323 | 1210837.6024
8 | 2702194.421 | 1210856.1272
9 | 2702195.3847 | 1210860.4765
10 | 2702181.6839 | 1210878.4433
11 | 2702202.1887 | 1210894.0487
12 | 2702206.8878 | 1210894.8977
13 | 2702239.3057 | 1210850.963
14 | 2702239.0298 | 1210849.6207
15 | 2702238.5245 | 1210884.3084
16 | 2702236.0864 | 1210835.3006
17 | 2702242.4976 | 1210885.1788
18 | 2702248.6325 | 1210883.0798
19 | 2702226.1878 | 1210890.0568
20 | 2702256.5298 | 1210880.3779
21 | 2702211.0825 | 1210893.8455
22 | 2702257.7379 | 1210879.9646
23 | 2702178.3336 | 1210912.1092
24 | 2702178.2508 | 1210912.277
25 | 2702282.6587 | 1210869.4231
26 | 2702275.975 | 1210872.7567
27 | 2702259.8519 | 1210879.2413
28 | 2702173.5842 | 1210921.7349
29 | 2702147.592 | 1210901.1643
30 | 2702168.4341 | 1210932.1681
31 | 2702160.5192 | 1210948.2019
32 | 2702170.9736 | 1210968.0341
33 | 2702175.1243 | 1210968.2148
34 | 2702197.8415 | 1210973.6232
35 | 2702203.9076 | 1210975.191
36 | 2702211.9743 | 1210977.2758
37 | 2702222.7686 | 1210975.882
38 | 2702235.1884 | 1210984.7455
39 | 2702225.6914 | 1211008.8885
40 | 2702206.8878 | 1210894.8977

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9952 | -0.033642 | 0.015468 | 0.0038767
1 | 0.99666 | -0.023372 | 0.003531 | 0.00088494
2 | 0.99682 | -0.022226 | 0.0044527 | 0.0011159
3 | 0.99604 | -0.027738 | 0 | 0
4 | 0.99624 | -0.026321 | 0.0018486 | 0.00046329
5 | 0.99593 | -0.028519 | 0.0022403 | 0.00056148
6 | 0.99631 | -0.025868 | 0 | 0
7 | 0.99586 | -0.028992 | 0.002704 | 0.00067769
8 | 0.9973 | -0.018863 | 0.0044655 | 0.0011192
9 | 0.99748 | -0.017615 | 0.0018373 | 0.00046046
10 | 0.9985 | -0.010489 | 0.0024016 | 0.00060189
11 | 1 | 0 | -0.10768 | -0.026829
12 | 0.99949 | -0.003547 | 0 | 0
13 | 0.99605 | -0.027707 | 0.004729 | 0.0011852
14 | 0.99602 | -0.027884 | 0.0044378 | 0.0011122
15 | 0.99728 | -0.019061 | 0.0023075 | 0.00057832
16 | 0.99585 | -0.029116 | 0.0083797 | 0.0021002
17 | 0.99739 | -0.018251 | 0 | 0
18 | 0.99721 | -0.019501 | 0.0016785 | 0.00042067
19 | 0.99834 | -0.011577 | 0.0010194 | 0.00025548
20 | 0.99701 | -0.02097 | 0.0014388 | 0.00036061
21 | 0.99924 | -0.0053298 | 0.0011533 | 0.00028903
22 | 0.99698 | -0.021176 | 0.0024597 | 0.00061645
23 | 0.99781 | -0.015323 | 0.001585 | 0.00039725
24 | 0.9978 | -0.015382 | 0.0025802 | 0.00064665
25 | 0.99655 | -0.024176 | 0.0028765 | 0.00072091
26 | 0.99665 | -0.023449 | 0.0015644 | 0.00039207
27 | 0.99693 | -0.021482 | 0.0023913 | 0.00059931
28 | 0.99736 | -0.018446 | 0 | 0
29 | 0.99686 | -0.021966 | 0.0064358 | 0.001613
30 | 0.99699 | -0.021077 | 0.0028065 | 0.00070337
31 | 0.99649 | -0.024618 | 0.0041827 | 0.0010483
32 | 0.99575 | -0.029769 | 0.0020981 | 0.00052584
33 | 0.99567 | -0.030331 | 0.0024938 | 0.00062501
34 | 0.99531 | -0.032908 | 0.0017302 | 0.00043363
35 | 0.99522 | -0.033489 | 0.0014714 | 0.00036878
36 | 0.99513 | -0.034138 | 0 | 0
37 | 0.9951 | -0.034346 | 0.0018974 | 0.00047554
38 | 0.99493 | -0.035573 | 0.0041867 | 0.0010493
39 | 0.99486 | -0.036042 | 0.0016424 | 0.00041162
40 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.015468 | -0.0038767 | 0.01549 | 0.0038843 | 2.2019e-05 | 7.6103e-06 | 0.023128 | 0.023127 | 0.023128 | 0.9952 | -0.033642 | 0.99666 | -0.023372 | 8.5658
1 | -0.019021 | -0.0047692 | 0.019024 | 0.0047703 | 3.0217e-06 | 1.0839e-06 | 0.028399 | 0.028399 | 0.028399 | 0.99666 | -0.023372 | 0.99682 | -0.022226 | 10.5182
2 | -0.023477 | -0.0058863 | 0.023488 | 0.0058903 | 1.0942e-05 | 4.0224e-06 | 0.035046 | 0.035046 | 0.035046 | 0.99682 | -0.022226 | 0.9973 | -0.018863 | 12.98
3 | -0.0049451 | -0.001239 | 0.004946 | 0.001239 | 9.693e-07 | 2.2578e-09 | 0.0073874 | 0.0073873 | 0.0073874 | 0.99604 | -0.027738 | 0.99624 | -0.026321 | 2.7361
4 | 0.0049451 | 0.001239 | -0.0049445 | -0.001239 | 5.3426e-07 | 1.3141e-09 | 0.0073874 | 0.0073875 | 0.0073875 | 0.99604 | -0.027738 | 0.99593 | -0.028519 | 2.7361
5 | -0.0067946 | -0.0017023 | 0.006795 | 0.0017024 | 4.2563e-07 | 7.7461e-08 | 0.010148 | 0.010148 | 0.010148 | 0.99624 | -0.026321 | 0.99631 | -0.025868 | 3.7587
6 | 0.0027042 | 0.00067753 | -0.002704 | -0.00067769 | 1.7729e-07 | -1.5828e-07 | 0.0040402 | 0.0040403 | 0.0040403 | 0.99593 | -0.028519 | 0.99586 | -0.028992 | 1.4964
7 | -0.006795 | -0.0017024 | 0.0067966 | 0.0017027 | 1.5911e-06 | 2.8946e-07 | 0.010148 | 0.010148 | 0.010148 | 0.99631 | -0.025868 | 0.99655 | -0.024176 | 3.7586
8 | -0.027953 | -0.0070094 | 0.027958 | 0.0070112 | 4.8357e-06 | 1.8018e-06 | 0.041709 | 0.041709 | 0.041709 | 0.9973 | -0.018863 | 0.99748 | -0.017615 | 15.4476
9 | -0.029795 | -0.0074717 | 0.029825 | 0.0074827 | 2.9458e-05 | 1.1018e-05 | 0.044449 | 0.044449 | 0.044449 | 0.99748 | -0.017615 | 0.9985 | -0.010489 | 16.4627
10 | -0.032226 | -0.0080846 | 0.032273 | 0.0081022 | 4.6953e-05 | 1.7631e-05 | 0.048028 | 0.048028 | 0.048028 | 0.9985 | -0.010489 | 1 | 0 | 17.7882
11 | 0.074604 | 0.018726 | -0.074567 | -0.018712 | 3.6728e-05 | 1.4063e-05 | 0.11102 | 0.11102 | 0.11102 | 1 | 0 | 0.99949 | -0.003547 | 41.1193
12 | 0.033217 | 0.0083357 | -0.033163 | -0.0083153 | 5.4204e-05 | 2.0383e-05 | 0.049456 | 0.049456 | 0.049456 | 0.99949 | -0.003547 | 0.99781 | -0.015323 | 18.3171
13 | 0.04135 | 0.010377 | -0.04134 | -0.010373 | 1.0229e-05 | 3.8774e-06 | 0.061566 | 0.061566 | 0.061566 | 0.99949 | -0.003547 | 0.99924 | -0.0053298 | 22.8023
14 | 0.012819 | 0.0032128 | -0.012819 | -0.0032127 | 3.1361e-07 | 1.0278e-07 | 0.019151 | 0.019151 | 0.019151 | 0.99605 | -0.027707 | 0.99602 | -0.027884 | 7.0929
15 | -0.017548 | -0.004398 | 0.017569 | 0.0044055 | 2.1027e-05 | 7.4483e-06 | 0.026216 | 0.026215 | 0.026216 | 0.99605 | -0.027707 | 0.99728 | -0.019061 | 9.7095
16 | 0.0083811 | 0.0021005 | -0.0083797 | -0.0021001 | 1.4302e-06 | 3.5984e-07 | 0.012521 | 0.012521 | 0.012521 | 0.99602 | -0.027884 | 0.99585 | -0.029116 | 4.6375
17 | -0.019877 | -0.0049838 | 0.019879 | 0.0049846 | 2.2325e-06 | 8.0558e-07 | 0.029658 | 0.029658 | 0.029658 | 0.99728 | -0.019061 | 0.99739 | -0.018251 | 10.9846
18 | 0.019218 | 0.0048167 | -0.019214 | -0.0048155 | 3.326e-06 | 1.1946e-06 | 0.028671 | 0.028671 | 0.028671 | 0.99739 | -0.018251 | 0.99721 | -0.019501 | 10.6189
19 | -0.039097 | -0.0098013 | 0.039133 | 0.009815 | 3.6174e-05 | 1.3691e-05 | 0.05833 | 0.058329 | 0.05833 | 0.99739 | -0.018251 | 0.99834 | -0.011577 | 21.6035
20 | 0.017536 | 0.0043949 | -0.017532 | -0.0043936 | 3.5661e-06 | 1.2627e-06 | 0.026167 | 0.026167 | 0.026167 | 0.99721 | -0.019501 | 0.99701 | -0.02097 | 9.6913
21 | -0.040152 | -0.01007 | 0.040187 | 0.010084 | 3.4808e-05 | 1.3184e-05 | 0.059849 | 0.059849 | 0.059849 | 0.99834 | -0.011577 | 0.99924 | -0.0053298 | 22.1662
22 | 0.016093 | 0.004033 | -0.016093 | -0.0040328 | 4.5966e-07 | 1.6014e-07 | 0.024019 | 0.024019 | 0.024019 | 0.99701 | -0.02097 | 0.99698 | -0.021176 | 8.896
23 | 0.013633 | 0.0034164 | -0.013633 | -0.0034162 | 5.7726e-07 | 1.9289e-07 | 0.020348 | 0.020348 | 0.020348 | 0.99698 | -0.021176 | 0.99693 | -0.021482 | 7.5363
24 | 0.031578 | 0.0079181 | -0.031577 | -0.007918 | 2.5899e-07 | 9.7168e-08 | 0.047092 | 0.047092 | 0.047092 | 0.99781 | -0.015323 | 0.9978 | -0.015382 | 17.4417
25 | 0.028997 | 0.0072713 | -0.028985 | -0.0072667 | 1.2307e-05 | 4.5958e-06 | 0.043245 | 0.043245 | 0.043245 | 0.9978 | -0.015382 | 0.99736 | -0.018446 | 16.0166
26 | -0.0096731 | -0.0024236 | 0.0096741 | 0.0024239 | 9.7225e-07 | 2.7662e-07 | 0.014443 | 0.014443 | 0.014443 | 0.99655 | -0.024176 | 0.99665 | -0.023449 | 5.3494
27 | -0.011238 | -0.0028159 | 0.011241 | 0.0028169 | 3.0594e-06 | 9.4968e-07 | 0.016779 | 0.016779 | 0.016779 | 0.99665 | -0.023449 | 0.99693 | -0.021482 | 6.2144
28 | 0.006439 | 0.0016135 | -0.0064358 | -0.001613 | 3.1358e-06 | 4.9581e-07 | 0.0096065 | 0.0096067 | 0.0096067 | 0.99736 | -0.018446 | 0.99686 | -0.021966 | 3.5581
29 | 0.022546 | 0.0056533 | -0.022538 | -0.0056502 | 8.2153e-06 | 3.0079e-06 | 0.033638 | 0.033638 | 0.033638 | 0.99736 | -0.018446 | 0.99699 | -0.021077 | 12.4586
30 | 0.019731 | 0.0049469 | -0.019721 | -0.0049434 | 9.6769e-06 | 3.4888e-06 | 0.02945 | 0.02945 | 0.02945 | 0.99699 | -0.021077 | 0.99649 | -0.024618 | 10.9073
31 | 0.015539 | 0.0038951 | -0.015528 | -0.0038913 | 1.1077e-05 | 3.8311e-06 | 0.023204 | 0.023204 | 0.023204 | 0.99649 | -0.024618 | 0.99575 | -0.029769 | 8.5941
32 | 0.01343 | 0.0033654 | -0.013429 | -0.0033651 | 1.0441e-06 | 3.4755e-07 | 0.020069 | 0.020069 | 0.020069 | 0.99575 | -0.029769 | 0.99567 | -0.030331 | 7.4328
33 | 0.010935 | 0.0027401 | -0.010931 | -0.0027389 | 3.8985e-06 | 1.1953e-06 | 0.016342 | 0.016342 | 0.016342 | 0.99567 | -0.030331 | 0.99531 | -0.032908 | 6.0525
34 | 0.0092006 | 0.0023053 | -0.0091999 | -0.002305 | 7.397e-07 | 2.0308e-07 | 0.013755 | 0.013755 | 0.013755 | 0.99531 | -0.032908 | 0.99522 | -0.033489 | 5.0945
35 | 0.0077285 | 0.0019363 | -0.0077278 | -0.0019361 | 6.9417e-07 | 1.5873e-07 | 0.011555 | 0.011555 | 0.011555 | 0.99522 | -0.033489 | 0.99513 | -0.034138 | 4.2797
36 | 0.0018975 | 0.00047542 | -0.0018974 | -0.00047554 | 5.4517e-08 | -1.2003e-07 | 0.0028372 | 0.0028373 | 0.0028373 | 0.99513 | -0.034138 | 0.9951 | -0.034346 | 1.0508
37 | 0.0058303 | 0.0014607 | -0.0058292 | -0.0014606 | 1.1571e-06 | 1.2813e-07 | 0.0087179 | 0.008718 | 0.008718 | 0.99513 | -0.034138 | 0.99493 | -0.035573 | 3.2289
38 | 0.0016425 | 0.00041129 | -0.0016424 | -0.00041162 | 1.066e-07 | -3.2664e-07 | 0.0024564 | 0.0024565 | 0.0024565 | 0.99493 | -0.035573 | 0.99486 | -0.036042 | 0.90982

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11293 | 0.028145

## res_load
| p_mw | q_mvar
0 | 0.015468 | 0.0038767
1 | 0.003531 | 0.00088494
2 | 0.0044527 | 0.0011159
3 | 0.0018486 | 0.00046329
4 | 0.0022403 | 0.00056148
5 | 0.002704 | 0.00067769
6 | 0.0044655 | 0.0011192
7 | 0.0018373 | 0.00046046
8 | 0.0024016 | 0.00060189
9 | 0.0052503 | 0.0013158
10 | 0.004729 | 0.0011852
11 | 0.0044378 | 0.0011122
12 | 0.0023075 | 0.00057832
13 | 0.0083797 | 0.0021002
14 | 0.0016785 | 0.00042067
15 | 0.0010194 | 0.00025548
16 | 0.0014388 | 0.00036061
17 | 0.0011533 | 0.00028903
18 | 0.0024597 | 0.00061645
19 | 0.001585 | 0.00039725
20 | 0.0025802 | 0.00064665
21 | 0.0028765 | 0.00072091
22 | 0.0015644 | 0.00039207
23 | 0.0023913 | 0.00059931
24 | 0.0064358 | 0.001613
25 | 0.0028065 | 0.00070337
26 | 0.0041827 | 0.0010483
27 | 0.0020981 | 0.00052584
28 | 0.0024938 | 0.00062501
29 | 0.0017302 | 0.00043363
30 | 0.0014714 | 0.00036878
31 | 0.0018974 | 0.00047554
32 | 0.0041867 | 0.0010493
33 | 0.0016424 | 0.00041162

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1