## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1368-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1368-5_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1368-5_0_3_node_23 | 0.4 | n |  | TRUE
3 | bus_LV_1368-5_0_3_node_34 | 0.4 | n |  | TRUE
4 | bus_LV_1368-5_0_3_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_1368-5_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1368-5_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1368-5_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1368-5_0_3_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_1368-5_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1368-5_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1368-5_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1368-5_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1368-5_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1368-5_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1368-5_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1368-5_0_3_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_1368-5_0_3_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_1368-5_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1368-5_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1368-5_0_3_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_1368-5_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1368-5_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1368-5_0_3_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_1368-5_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1368-5_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1368-5_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1368-5_0_3_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_1368-5_0_3_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_1368-5_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1368-5_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1368-5_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1368-5_0_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1368-5_0_3_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1368-5_0_3_node_33 | 0.4 | n |  | TRUE
35 | bus_MV_135_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1368-5_0_3_load_0 | 0 | 0.0041598 | 0.0010426 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1368-5_0_3_load_2 | 1 | 0.0031721 | 0.00079501 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1368-5_0_3_load_34 | 3 | 0.0067967 | 0.0017034 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1368-5_0_3_load_21 | 4 | 0.0040134 | 0.0010058 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1368-5_0_3_load_3 | 5 | 0.0085174 | 0.0021347 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1368-5_0_3_load_4 | 6 | 0.013395 | 0.0033572 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1368-5_0_3_load_5 | 7 | 0.0057084 | 0.0014307 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1368-5_0_3_load_25 | 8 | 0.0047955 | 0.0012019 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1368-5_0_3_load_9 | 9 | 0.0049568 | 0.0012423 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1368-5_0_3_load_6 | 10 | 0.0042301 | 0.0010602 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1368-5_0_3_load_7 | 11 | 0.0051045 | 0.0012793 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1368-5_0_3_load_11 | 14 | 0.023511 | 0.0058924 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1368-5_0_3_load_14 | 15 | 0.0055204 | 0.0013836 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1368-5_0_3_load_16 | 16 | 0.015375 | 0.0038534 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1368-5_0_3_load_26 | 17 | 0.0080144 | 0.0020086 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1368-5_0_3_load_12 | 18 | 0.0072022 | 0.001805 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1368-5_0_3_load_24 | 20 | 0.0030193 | 0.00075671 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1368-5_0_3_load_13 | 21 | 0.0066653 | 0.0016705 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1368-5_0_3_load_15 | 22 | 0.014361 | 0.0035992 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1368-5_0_3_load_35 | 23 | 0.0053959 | 0.0013523 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1368-5_0_3_load_19 | 25 | 0.0356 | 0.0089223 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1368-5_0_3_load_27 | 26 | 0.013603 | 0.0034093 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1368-5_0_3_load_29 | 28 | 0.0023615 | 0.00059185 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1368-5_0_3_load_20 | 29 | 0.0063243 | 0.001585 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1368-5_0_3_load_22 | 30 | 0.0032887 | 0.00082423 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1368-5_0_3_load_32 | 31 | 0.0046736 | 0.0011713 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1368-5_0_3_load_30 | 32 | 0.00080963 | 0.00020291 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1368-5_0_3_load_31 | 33 | 0.0045853 | 0.0011492 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1368-5_0_3_load_33 | 34 | 0.016206 | 0.0040617 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1368-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.025173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1368-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.059446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1368-5_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.029785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1368-5_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.012763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1368-5_0_3_line_4 | NAYY 4x150 SE | 3 | 31 | 0.0011633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1368-5_0_3_line_5 | NAYY 4x150 SE | 4 | 29 | 0.0028713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1368-5_0_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.032878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1368-5_0_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.010839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1368-5_0_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.014655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1368-5_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.002143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1368-5_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.0090375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1368-5_0_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.009278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1368-5_0_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.014535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1368-5_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.010466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1368-5_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.023104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1368-5_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.015341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1368-5_0_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.024143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1368-5_0_3_line_17 | NAYY 4x150 SE | 14 | 17 | 0.004792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1368-5_0_3_line_18 | NAYY 4x150 SE | 15 | 18 | 0.012956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1368-5_0_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.020458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1368-5_0_3_line_20 | NAYY 4x150 SE | 17 | 20 | 0.019171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1368-5_0_3_line_21 | NAYY 4x150 SE | 18 | 21 | 0.017677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1368-5_0_3_line_22 | NAYY 4x150 SE | 19 | 24 | 0.032394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1368-5_0_3_line_23 | NAYY 4x150 SE | 19 | 25 | 0.0019698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1368-5_0_3_line_24 | NAYY 4x150 SE | 20 | 30 | 0.038274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1368-5_0_3_line_25 | NAYY 4x150 SE | 21 | 22 | 0.024297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1368-5_0_3_line_26 | NAYY 4x150 SE | 22 | 23 | 0.082108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1368-5_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.012138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1368-5_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.035732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1368-5_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.026034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1368-5_0_3_line_30 | NAYY 4x150 SE | 28 | 32 | 0.1604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1368-5_0_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.016088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1368-5_0_3_line_32 | NAYY 4x150 SE | 31 | 33 | 0.020473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1368-5_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.028517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1368-5_0_3_trafo_11 | 0.25 MVA 20/0.4 kV | 35 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2702052.3228 | 1210572.4929 | 2702033.9822 | 1210589.7358
1 | 2702023.8658 | 1210648.3149 | 2702033.9822 | 1210589.7358
2 | 2702023.8658 | 1210648.3149 | 2701998.0156 | 1210663.1115
3 | 2702023.8658 | 1210648.3149 | 2702031.4247 | 1210658.5992
4 | 2701998.0156 | 1210663.1115 | 2701997.006 | 1210663.6894
5 | 2702031.4247 | 1210658.5992 | 2702033.1252 | 1210660.9127
6 | 2702022.9794 | 1210801.7407 | 2702029.1473 | 1210796.7535 | 2702048.1662 | 1210780.6109
7 | 2702056.4297 | 1210773.5971 | 2702048.1662 | 1210780.6109
8 | 2702067.7945 | 1210764.3458 | 2702059.6064 | 1210770.9008 | 2702056.4297 | 1210773.5971
9 | 2702067.7945 | 1210764.3458 | 2702069.4674 | 1210763.0065
10 | 2702076.5227 | 1210757.3585 | 2702076.5227 | 1210757.3585 | 2702069.4674 | 1210763.0065
11 | 2702076.5227 | 1210757.3585 | 2702083.6122 | 1210751.3736
12 | 2702094.4484 | 1210741.6875 | 2702084.9525 | 1210750.2421 | 2702083.6122 | 1210751.3736
13 | 2702102.3946 | 1210734.8521 | 2702094.4484 | 1210741.6875
14 | 2702094.4484 | 1210741.6875 | 2702080.1774 | 1210723.5183
15 | 2702102.3946 | 1210734.8521 | 2702109.9563 | 1210748.2002
16 | 2702102.3946 | 1210734.8521 | 2702119.0629 | 1210726.4759 | 2702124.2457 | 1210724.6689
17 | 2702077.2174 | 1210719.7498 | 2702080.1774 | 1210723.5183
18 | 2702109.9563 | 1210748.2002 | 2702114.3397 | 1210755.9379 | 2702116.6191 | 1210759.3012
19 | 2702143.5633 | 1210717.9338 | 2702124.2457 | 1210724.6689
20 | 2702065.3758 | 1210704.6734 | 2702077.2174 | 1210719.7498
21 | 2702127.1737 | 1210773.4417 | 2702122.9322 | 1210768.6161 | 2702116.6191 | 1210759.3012
22 | 2702155.276 | 1210748.1443 | 2702143.5633 | 1210717.9338
23 | 2702143.5633 | 1210717.9338 | 2702145.4411 | 1210717.3386
24 | 2702065.3758 | 1210704.6734 | 2702064.0229 | 1210702.951 | 2702042.6532 | 1210673.8762
25 | 2702127.1737 | 1210773.4417 | 2702133.4598 | 1210780.5935 | 2702139.2482 | 1210790.5663 | 2702140.3155 | 1210793.6303
26 | 2702140.3155 | 1210793.6303 | 2702107.4252 | 1210868.8627
27 | 2702155.276 | 1210748.1443 | 2702159.8705 | 1210759.3795
28 | 2702180.1765 | 1210709.5993 | 2702162.8993 | 1210711.805 | 2702145.4411 | 1210717.3386
29 | 2702180.1765 | 1210709.5993 | 2702175.3854 | 1210684.0104
30 | 2702175.3854 | 1210684.0104 | 2702239.4841 | 1210536.9722
31 | 2702042.6532 | 1210673.8762 | 2702033.1252 | 1210660.9127
32 | 2701979.2374 | 1210673.8601 | 2701997.006 | 1210663.6894
33 | 2701961.9115 | 1210695.233 | 2701970.7145 | 1210678.7386 | 2701979.2374 | 1210673.8601

## bus_geodata
| x | y | coords
0 | 2702033.9822 | 1210589.7358
1 | 2702052.3228 | 1210572.4929
2 | 2702023.8658 | 1210648.3149
3 | 2701998.0156 | 1210663.1115
4 | 2702031.4247 | 1210658.5992
5 | 2702022.9794 | 1210801.7407
6 | 2702048.1662 | 1210780.6109
7 | 2702056.4297 | 1210773.5971
8 | 2702067.7945 | 1210764.3458
9 | 2702069.4674 | 1210763.0065
10 | 2702083.6122 | 1210751.3736
11 | 2702076.5227 | 1210757.3585
12 | 2702094.4484 | 1210741.6875
13 | 2702102.3946 | 1210734.8521
14 | 2702080.1774 | 1210723.5183
15 | 2702109.9563 | 1210748.2002
16 | 2702124.2457 | 1210724.6689
17 | 2702077.2174 | 1210719.7498
18 | 2702116.6191 | 1210759.3012
19 | 2702143.5633 | 1210717.9338
20 | 2702065.3757 | 1210704.6734
21 | 2702127.1737 | 1210773.4417
22 | 2702140.3155 | 1210793.6303
23 | 2702107.4252 | 1210868.8627
24 | 2702155.276 | 1210748.1443
25 | 2702145.4411 | 1210717.3386
26 | 2702159.8705 | 1210759.3795
27 | 2702180.1765 | 1210709.5993
28 | 2702175.3854 | 1210684.0104
29 | 2702033.1252 | 1210660.9127
30 | 2702042.6532 | 1210673.8762
31 | 2701997.006 | 1210663.6894
32 | 2702239.4841 | 1210536.9722
33 | 2701979.2374 | 1210673.8601
34 | 2701961.9115 | 1210695.2331
35 | 2702094.4484 | 1210741.6875

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99239 | -0.05325 | 0.0041598 | 0.0010426
1 | 0.99228 | -0.05406 | 0.0031721 | 0.00079501
2 | 0.99302 | -0.048833 | 0 | 0
3 | 0.99164 | -0.058574 | 0.0067967 | 0.0017034
4 | 0.99375 | -0.04372 | 0.0040134 | 0.0010058
5 | 0.99401 | -0.04195 | 0.0085174 | 0.0021347
6 | 0.99441 | -0.039122 | 0.013395 | 0.0033572
7 | 0.99475 | -0.036725 | 0.0057084 | 0.0014307
8 | 0.99533 | -0.032644 | 0.0047955 | 0.0012019
9 | 0.99543 | -0.031944 | 0.0049568 | 0.0012423
10 | 0.99648 | -0.024579 | 0.0042301 | 0.0010602
11 | 0.99592 | -0.028543 | 0.0051045 | 0.0012793
12 | 0.99746 | -0.017761 | 0 | 0
13 | 0.99665 | -0.023379 | 0 | 0
14 | 1 | 0 | -0.22 | -0.055107
15 | 0.99579 | -0.02942 | 0.0055204 | 0.0013836
16 | 0.9943 | -0.03986 | 0.015375 | 0.0038534
17 | 0.99956 | -0.0030755 | 0.0080144 | 0.0020086
18 | 0.99517 | -0.033809 | 0.0072022 | 0.001805
19 | 0.99277 | -0.050699 | 0 | 0
20 | 0.99801 | -0.013867 | 0.0030193 | 0.00075671
21 | 0.9945 | -0.038521 | 0.0066653 | 0.0016705
22 | 0.99381 | -0.043371 | 0.014361 | 0.0035992
23 | 0.99317 | -0.047854 | 0.0053959 | 0.0013523
24 | 0.99213 | -0.055165 | 0 | 0
25 | 0.99266 | -0.051473 | 0.0356 | 0.0089223
26 | 0.9919 | -0.05684 | 0.013603 | 0.0034093
27 | 0.99249 | -0.052628 | 0 | 0
28 | 0.99237 | -0.053469 | 0.0023615 | 0.00059185
29 | 0.99393 | -0.042454 | 0.0063243 | 0.001585
30 | 0.99508 | -0.034345 | 0.0032887 | 0.00082423
31 | 0.9916 | -0.058875 | 0.0046736 | 0.0011713
32 | 0.99219 | -0.054798 | 0.00080963 | 0.00020291
33 | 0.99098 | -0.063199 | 0.0045853 | 0.0011492
34 | 0.99032 | -0.067899 | 0.016206 | 0.0040617
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0031725 | 0.00079482 | -0.0031721 | -0.00079501 | 3.5543e-07 | -1.8851e-07 | 0.0047568 | 0.0047569 | 0.0047569 | 0.99239 | -0.05325 | 0.99228 | -0.05406 | 1.7618
1 | -0.0073323 | -0.0018374 | 0.0073368 | 0.0018383 | 4.4835e-06 | 9.5587e-07 | 0.010994 | 0.010994 | 0.010994 | 0.99239 | -0.05325 | 0.99302 | -0.048833 | 4.0719
2 | 0.032329 | 0.0081106 | -0.032286 | -0.0080942 | 4.3625e-05 | 1.6394e-05 | 0.048448 | 0.048448 | 0.048448 | 0.99302 | -0.048833 | 0.99164 | -0.058574 | 17.9436
3 | -0.039666 | -0.0099489 | 0.039694 | 0.0099596 | 2.814e-05 | 1.0658e-05 | 0.059442 | 0.059441 | 0.059442 | 0.99302 | -0.048833 | 0.99375 | -0.04372 | 22.0154
4 | 0.025489 | 0.0063908 | -0.025488 | -0.0063904 | 1.062e-06 | 3.9346e-07 | 0.038249 | 0.038249 | 0.038249 | 0.99164 | -0.058574 | 0.9916 | -0.058875 | 14.1663
5 | -0.043708 | -0.010965 | 0.043715 | 0.010968 | 7.6752e-06 | 2.9148e-06 | 0.065451 | 0.065451 | 0.065451 | 0.99375 | -0.04372 | 0.99393 | -0.042454 | 24.2411
6 | -0.0085174 | -0.0021347 | 0.0085207 | 0.0021355 | 3.3353e-06 | 8.5643e-07 | 0.01275 | 0.01275 | 0.01275 | 0.99401 | -0.04195 | 0.99441 | -0.039122 | 4.7224
7 | -0.021916 | -0.0054927 | 0.021923 | 0.0054954 | 7.274e-06 | 2.657e-06 | 0.032795 | 0.032795 | 0.032795 | 0.99441 | -0.039122 | 0.99475 | -0.036725 | 12.1463
8 | -0.027632 | -0.0069261 | 0.027648 | 0.0069319 | 1.5624e-05 | 5.8189e-06 | 0.041334 | 0.041334 | 0.041334 | 0.99475 | -0.036725 | 0.99533 | -0.032644 | 15.3088
9 | -0.032443 | -0.0081338 | 0.032446 | 0.0081349 | 3.1459e-06 | 1.1821e-06 | 0.048503 | 0.048503 | 0.048503 | 0.99533 | -0.032644 | 0.99543 | -0.031944 | 17.9641
10 | -0.037403 | -0.0093772 | 0.037421 | 0.0093839 | 1.763e-05 | 6.6632e-06 | 0.055913 | 0.055913 | 0.055913 | 0.99543 | -0.031944 | 0.99592 | -0.028543 | 20.7084
11 | 0.042549 | 0.010672 | -0.042525 | -0.010663 | 2.3373e-05 | 8.869e-06 | 0.063539 | 0.063539 | 0.063539 | 0.99648 | -0.024579 | 0.99592 | -0.028543 | 23.5331
12 | -0.046779 | -0.011732 | 0.046823 | 0.011749 | 4.4259e-05 | 1.6833e-05 | 0.069856 | 0.069856 | 0.069856 | 0.99648 | -0.024579 | 0.99746 | -0.017761 | 25.8726
13 | 0.10732 | 0.026946 | -0.10723 | -0.026914 | 8.3713e-05 | 3.1924e-05 | 0.16011 | 0.16011 | 0.16011 | 0.99746 | -0.017761 | 0.99665 | -0.023379 | 29.6507
14 | -0.15414 | -0.038695 | 0.15452 | 0.038841 | 0.00038122 | 0.00014602 | 0.22997 | 0.22997 | 0.22997 | 0.99746 | -0.017761 | 1 | 0 | 42.587
15 | 0.039232 | 0.0098421 | -0.039199 | -0.0098297 | 3.2847e-05 | 1.2434e-05 | 0.058577 | 0.058577 | 0.058577 | 0.99665 | -0.023379 | 0.99579 | -0.02942 | 21.6952
16 | 0.068001 | 0.017072 | -0.067846 | -0.017013 | 0.00015532 | 5.9425e-05 | 0.10154 | 0.10154 | 0.10154 | 0.99665 | -0.023379 | 0.9943 | -0.03986 | 37.6063
17 | 0.064683 | 0.016265 | -0.064656 | -0.016255 | 2.7712e-05 | 1.0596e-05 | 0.096269 | 0.096269 | 0.096269 | 1 | 0 | 0.99956 | -0.0030755 | 35.6552
18 | 0.033679 | 0.0084461 | -0.033658 | -0.0084384 | 2.0477e-05 | 7.7075e-06 | 0.050328 | 0.050328 | 0.050328 | 0.99579 | -0.02942 | 0.99517 | -0.033809 | 18.64
19 | 0.05247 | 0.013159 | -0.052392 | -0.013129 | 7.8721e-05 | 3.0012e-05 | 0.078527 | 0.078527 | 0.078527 | 0.9943 | -0.03986 | 0.99277 | -0.050699 | 29.0841
20 | 0.056641 | 0.014246 | -0.056556 | -0.014214 | 8.509e-05 | 3.2476e-05 | 0.084338 | 0.084338 | 0.084338 | 0.99956 | -0.0030755 | 0.99801 | -0.013867 | 31.2365
21 | 0.026456 | 0.0066334 | -0.026439 | -0.006627 | 1.7262e-05 | 6.4097e-06 | 0.039559 | 0.039559 | 0.039559 | 0.99517 | -0.033809 | 0.9945 | -0.038521 | 14.6515
22 | 0.013615 | 0.0034132 | -0.013607 | -0.0034104 | 8.4182e-06 | 2.8192e-06 | 0.020407 | 0.020407 | 0.020407 | 0.99277 | -0.050699 | 0.99213 | -0.055165 | 7.5583
23 | 0.038777 | 0.0097161 | -0.038772 | -0.0097146 | 4.1521e-06 | 1.5715e-06 | 0.05812 | 0.05812 | 0.05812 | 0.99277 | -0.050699 | 0.99266 | -0.051473 | 21.5259
24 | 0.053537 | 0.013457 | -0.053385 | -0.013399 | 0.00015223 | 5.805e-05 | 0.079837 | 0.079837 | 0.079837 | 0.99801 | -0.013867 | 0.99508 | -0.034345 | 29.5692
25 | 0.019773 | 0.0049565 | -0.01976 | -0.0049517 | 1.3271e-05 | 4.7893e-06 | 0.029586 | 0.029586 | 0.029586 | 0.9945 | -0.038521 | 0.99381 | -0.043371 | 10.9578
26 | 0.0053992 | 0.0013526 | -0.0053959 | -0.0013523 | 3.3484e-06 | 2.2463e-07 | 0.008084 | 0.0080843 | 0.0080843 | 0.99381 | -0.043371 | 0.99317 | -0.047854 | 2.9942
27 | 0.013607 | 0.0034104 | -0.013603 | -0.0034093 | 3.1544e-06 | 1.0565e-06 | 0.020407 | 0.020407 | 0.020407 | 0.99213 | -0.055165 | 0.9919 | -0.05684 | 7.5583
28 | 0.0031721 | 0.00079228 | -0.0031716 | -0.00079255 | 5.0397e-07 | -2.68e-07 | 0.0047542 | 0.0047543 | 0.0047543 | 0.99266 | -0.051473 | 0.99249 | -0.052628 | 1.7609
29 | 0.0031716 | 0.00079255 | -0.0031713 | -0.00079274 | 3.672e-07 | -1.9516e-07 | 0.0047543 | 0.0047544 | 0.0047544 | 0.99249 | -0.052628 | 0.99237 | -0.053469 | 1.7609
30 | 0.00080978 | 0.0002009 | -0.00080963 | -0.00020291 | 1.4748e-07 | -2.0153e-06 | 0.0012135 | 0.0012142 | 0.0012142 | 0.99237 | -0.053469 | 0.99219 | -0.054798 | 0.44971
31 | -0.05004 | -0.012553 | 0.050096 | 0.012575 | 5.6348e-05 | 2.1464e-05 | 0.074919 | 0.074919 | 0.074919 | 0.99393 | -0.042454 | 0.99508 | -0.034345 | 27.7478
32 | 0.020814 | 0.0052191 | -0.020802 | -0.0052145 | 1.2465e-05 | 4.5301e-06 | 0.031236 | 0.031236 | 0.031236 | 0.9916 | -0.058875 | 0.99098 | -0.063199 | 11.5688
33 | 0.016217 | 0.0040654 | -0.016206 | -0.0040617 | 1.0551e-05 | 3.6911e-06 | 0.024351 | 0.024351 | 0.024351 | 0.99098 | -0.063199 | 0.99032 | -0.067899 | 9.0188

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24352 | 0.060999

## res_load
| p_mw | q_mvar
0 | 0.0041598 | 0.0010426
1 | 0.0031721 | 0.00079501
2 | 0.0067967 | 0.0017034
3 | 0.0040134 | 0.0010058
4 | 0.0085174 | 0.0021347
5 | 0.013395 | 0.0033572
6 | 0.0057084 | 0.0014307
7 | 0.0047955 | 0.0012019
8 | 0.0049568 | 0.0012423
9 | 0.0042301 | 0.0010602
10 | 0.0051045 | 0.0012793
11 | 0.023511 | 0.0058924
12 | 0.0055204 | 0.0013836
13 | 0.015375 | 0.0038534
14 | 0.0080144 | 0.0020086
15 | 0.0072022 | 0.001805
16 | 0.0030193 | 0.00075671
17 | 0.0066653 | 0.0016705
18 | 0.014361 | 0.0035992
19 | 0.0053959 | 0.0013523
20 | 0.0356 | 0.0089223
21 | 0.013603 | 0.0034093
22 | 0.0023615 | 0.00059185
23 | 0.0063243 | 0.001585
24 | 0.0032887 | 0.00082423
25 | 0.0046736 | 0.0011713
26 | 0.00080963 | 0.00020291
27 | 0.0045853 | 0.0011492
28 | 0.016206 | 0.0040617

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1