## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1368-6_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1368-6_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1368-6_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1368-6_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1368-6_0_6_node_35 | 0.4 | n |  | TRUE
5 | bus_LV_1368-6_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1368-6_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1368-6_0_6_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_1368-6_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1368-6_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1368-6_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1368-6_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1368-6_0_6_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_1368-6_0_6_node_171 | 0.4 | n |  | TRUE
14 | bus_LV_1368-6_0_6_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_1368-6_0_6_node_172 | 0.4 | n |  | TRUE
16 | bus_LV_1368-6_0_6_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1368-6_0_6_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1368-6_0_6_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1368-6_0_6_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1368-6_0_6_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1368-6_0_6_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1368-6_0_6_node_50 | 0.4 | n |  | TRUE
23 | bus_LV_1368-6_0_6_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1368-6_0_6_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1368-6_0_6_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1368-6_0_6_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1368-6_0_6_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_1368-6_0_6_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1368-6_0_6_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1368-6_0_6_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_1368-6_0_6_node_174 | 0.4 | n |  | TRUE
32 | bus_LV_1368-6_0_6_node_173 | 0.4 | n |  | TRUE
33 | bus_LV_1368-6_0_6_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_1368-6_0_6_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1368-6_0_6_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1368-6_0_6_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_1368-6_0_6_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_1368-6_0_6_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_1368-6_0_6_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_1368-6_0_6_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_1368-6_0_6_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_1368-6_0_6_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_1368-6_0_6_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_1368-6_0_6_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_1368-6_0_6_node_138 | 0.4 | n |  | TRUE
46 | bus_LV_1368-6_0_6_node_136 | 0.4 | n |  | TRUE
47 | bus_LV_1368-6_0_6_node_86 | 0.4 | n |  | TRUE
48 | bus_LV_1368-6_0_6_node_87 | 0.4 | n |  | TRUE
49 | bus_LV_1368-6_0_6_node_125 | 0.4 | n |  | TRUE
50 | bus_LV_1368-6_0_6_node_88 | 0.4 | n |  | TRUE
51 | bus_LV_1368-6_0_6_node_89 | 0.4 | n |  | TRUE
52 | bus_LV_1368-6_0_6_node_90 | 0.4 | n |  | TRUE
53 | bus_LV_1368-6_0_6_node_91 | 0.4 | n |  | TRUE
54 | bus_LV_1368-6_0_6_node_92 | 0.4 | n |  | TRUE
55 | bus_LV_1368-6_0_6_node_93 | 0.4 | n |  | TRUE
56 | bus_LV_1368-6_0_6_node_98 | 0.4 | n |  | TRUE
57 | bus_LV_1368-6_0_6_node_94 | 0.4 | n |  | TRUE
58 | bus_LV_1368-6_0_6_node_95 | 0.4 | n |  | TRUE
59 | bus_LV_1368-6_0_6_node_96 | 0.4 | n |  | TRUE
60 | bus_LV_1368-6_0_6_node_97 | 0.4 | n |  | TRUE
61 | bus_LV_1368-6_0_6_node_99 | 0.4 | n |  | TRUE
62 | bus_LV_1368-6_0_6_node_100 | 0.4 | n |  | TRUE
63 | bus_LV_1368-6_0_6_node_101 | 0.4 | n |  | TRUE
64 | bus_LV_1368-6_0_6_node_102 | 0.4 | n |  | TRUE
65 | bus_LV_1368-6_0_6_node_103 | 0.4 | n |  | TRUE
66 | bus_LV_1368-6_0_6_node_104 | 0.4 | n |  | TRUE
67 | bus_LV_1368-6_0_6_node_105 | 0.4 | n |  | TRUE
68 | bus_LV_1368-6_0_6_node_106 | 0.4 | n |  | TRUE
69 | bus_LV_1368-6_0_6_node_107 | 0.4 | n |  | TRUE
70 | bus_LV_1368-6_0_6_node_108 | 0.4 | n |  | TRUE
71 | bus_LV_1368-6_0_6_node_109 | 0.4 | n |  | TRUE
72 | bus_LV_1368-6_0_6_node_110 | 0.4 | n |  | TRUE
73 | bus_LV_1368-6_0_6_node_116 | 0.4 | n |  | TRUE
74 | bus_LV_1368-6_0_6_node_111 | 0.4 | n |  | TRUE
75 | bus_LV_1368-6_0_6_node_112 | 0.4 | n |  | TRUE
76 | bus_LV_1368-6_0_6_node_114 | 0.4 | n |  | TRUE
77 | bus_LV_1368-6_0_6_node_115 | 0.4 | n |  | TRUE
78 | bus_LV_1368-6_0_6_node_117 | 0.4 | n |  | TRUE
79 | bus_LV_1368-6_0_6_node_118 | 0.4 | n |  | TRUE
80 | bus_LV_1368-6_0_6_node_119 | 0.4 | n |  | TRUE
81 | bus_LV_1368-6_0_6_node_120 | 0.4 | n |  | TRUE
82 | bus_LV_1368-6_0_6_node_121 | 0.4 | n |  | TRUE
83 | bus_LV_1368-6_0_6_node_122 | 0.4 | n |  | TRUE
84 | bus_LV_1368-6_0_6_node_126 | 0.4 | n |  | TRUE
85 | bus_LV_1368-6_0_6_node_123 | 0.4 | n |  | TRUE
86 | bus_LV_1368-6_0_6_node_127 | 0.4 | n |  | TRUE
87 | bus_LV_1368-6_0_6_node_128 | 0.4 | n |  | TRUE
88 | bus_LV_1368-6_0_6_node_129 | 0.4 | n |  | TRUE
89 | bus_LV_1368-6_0_6_node_130 | 0.4 | n |  | TRUE
90 | bus_LV_1368-6_0_6_node_131 | 0.4 | n |  | TRUE
91 | bus_LV_1368-6_0_6_node_132 | 0.4 | n |  | TRUE
92 | bus_LV_1368-6_0_6_node_133 | 0.4 | n |  | TRUE
93 | bus_LV_1368-6_0_6_node_134 | 0.4 | n |  | TRUE
94 | bus_LV_1368-6_0_6_node_135 | 0.4 | n |  | TRUE
95 | bus_LV_1368-6_0_6_node_137 | 0.4 | n |  | TRUE
96 | bus_LV_1368-6_0_6_node_48 | 0.4 | n |  | TRUE
97 | bus_LV_1368-6_0_6_node_49 | 0.4 | n |  | TRUE
98 | bus_LV_1368-6_0_6_node_139 | 0.4 | n |  | TRUE
99 | bus_LV_1368-6_0_6_node_140 | 0.4 | n |  | TRUE
100 | bus_LV_1368-6_0_6_node_52 | 0.4 | n |  | TRUE
101 | bus_LV_1368-6_0_6_node_141 | 0.4 | n |  | TRUE
102 | bus_LV_1368-6_0_6_node_142 | 0.4 | n |  | TRUE
103 | bus_LV_1368-6_0_6_node_113 | 0.4 | n |  | TRUE
104 | bus_LV_1368-6_0_6_node_146 | 0.4 | n |  | TRUE
105 | bus_LV_1368-6_0_6_node_148 | 0.4 | n |  | TRUE
106 | bus_LV_1368-6_0_6_node_143 | 0.4 | n |  | TRUE
107 | bus_LV_1368-6_0_6_node_144 | 0.4 | n |  | TRUE
108 | bus_LV_1368-6_0_6_node_145 | 0.4 | n |  | TRUE
109 | bus_LV_1368-6_0_6_node_147 | 0.4 | n |  | TRUE
110 | bus_MV_135_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1368-6_0_6_load_0 | 0 | 0.0035699 | 0.0008947 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1368-6_0_6_load_1 | 1 | 0.003191 | 0.00079974 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1368-6_0_6_load_2 | 2 | 0.0021958 | 0.00055032 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1368-6_0_6_load_3 | 3 | 0.0041491 | 0.0010399 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1368-6_0_6_load_35 | 4 | 0.001236 | 0.00030976 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1368-6_0_6_load_4 | 5 | 0.0025258 | 0.00063304 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1368-6_0_6_load_5 | 6 | 0.0015737 | 0.0003944 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1368-6_0_6_load_34 | 7 | 0.0053144 | 0.0013319 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1368-6_0_6_load_6 | 8 | 0.0037802 | 0.00094742 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1368-6_0_6_load_7 | 9 | 0.0012167 | 0.00030493 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1368-6_0_6_load_8 | 10 | 0.0052098 | 0.0013057 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1368-6_0_6_load_33 | 12 | 0.0037332 | 0.00093564 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1368-6_0_6_load_171 | 13 | 0.0026946 | 0.00067532 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1368-6_0_6_load_31 | 14 | 0.0037042 | 0.00092836 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1368-6_0_6_load_172 | 15 | 0.0040595 | 0.0010174 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1368-6_0_6_load_14 | 16 | 0.00075795 | 0.00018996 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1368-6_0_6_load_16 | 18 | 0.00069067 | 0.0001731 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1368-6_0_6_load_17 | 19 | 0.0040782 | 0.0010221 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1368-6_0_6_load_23 | 20 | 0.00055617 | 0.00013939 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1368-6_0_6_load_20 | 21 | 0.0010557 | 0.00026459 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1368-6_0_6_load_50 | 22 | 0.00051501 | 0.00012907 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1368-6_0_6_load_21 | 23 | 0.0006297 | 0.00015782 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1368-6_0_6_load_22 | 24 | 0.00057717 | 0.00014465 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1368-6_0_6_load_24 | 25 | 0.00064748 | 0.00016227 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1368-6_0_6_load_25 | 26 | 0.00066547 | 0.00016678 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1368-6_0_6_load_51 | 27 | 0.00061652 | 0.00015451 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1368-6_0_6_load_26 | 28 | 0.00066998 | 0.00016791 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1368-6_0_6_load_27 | 29 | 0.00066466 | 0.00016658 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1368-6_0_6_load_174 | 31 | 0.00040429 | 0.00010132 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1368-6_0_6_load_173 | 32 | 0.0029762 | 0.0007459 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1368-6_0_6_load_47 | 33 | 0.0015769 | 0.0003952 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1368-6_0_6_load_29 | 34 | 0.0019206 | 0.00048136 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1368-6_0_6_load_30 | 35 | 0.0036711 | 0.00092006 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1368-6_0_6_load_32 | 36 | 0.0041971 | 0.0010519 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1368-6_0_6_load_39 | 37 | 0.00080223 | 0.00020106 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1368-6_0_6_load_40 | 38 | 0.00042648 | 0.00010689 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1368-6_0_6_load_41 | 39 | 0.0061195 | 0.0015337 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1368-6_0_6_load_42 | 40 | 0.00083666 | 0.00020969 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1368-6_0_6_load_43 | 41 | 0.0045689 | 0.0011451 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1368-6_0_6_load_44 | 43 | 0.00079576 | 0.00019944 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1368-6_0_6_load_46 | 44 | 0.00047906 | 0.00012006 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1368-6_0_6_load_138 | 45 | 0.00064013 | 0.00016043 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1368-6_0_6_load_136 | 46 | 0.00081937 | 0.00020535 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1368-6_0_6_load_86 | 47 | 0.0018457 | 0.00046258 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1368-6_0_6_load_87 | 48 | 0.0017344 | 0.00043467 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1368-6_0_6_load_125 | 49 | 0.00087027 | 0.00021811 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1368-6_0_6_load_89 | 51 | 0.001672 | 0.00041905 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1368-6_0_6_load_90 | 52 | 0.0012844 | 0.0003219 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1368-6_0_6_load_91 | 53 | 0.0012484 | 0.00031287 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1368-6_0_6_load_92 | 54 | 0.001328 | 0.00033283 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1368-6_0_6_load_93 | 55 | 0.0012557 | 0.0003147 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1368-6_0_6_load_98 | 56 | 0.0017419 | 0.00043657 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1368-6_0_6_load_94 | 57 | 0.002515 | 0.00063031 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1368-6_0_6_load_95 | 58 | 0.0011611 | 0.00029099 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1368-6_0_6_load_96 | 59 | 0.0011113 | 0.00027851 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1368-6_0_6_load_97 | 60 | 0.0020711 | 0.00051907 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1368-6_0_6_load_99 | 61 | 0.0011511 | 0.00028848 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1368-6_0_6_load_100 | 62 | 0.0013538 | 0.00033929 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1368-6_0_6_load_101 | 63 | 0.0011556 | 0.00028962 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1368-6_0_6_load_102 | 64 | 0.0015872 | 0.0003978 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1368-6_0_6_load_103 | 65 | 0.0018585 | 0.00046579 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1368-6_0_6_load_104 | 66 | 0.00099962 | 0.00025053 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1368-6_0_6_load_105 | 67 | 0.0016223 | 0.00040659 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1368-6_0_6_load_106 | 68 | 0.0017119 | 0.00042904 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1368-6_0_6_load_107 | 69 | 0.0013663 | 0.00034244 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1368-6_0_6_load_108 | 70 | 0.002055 | 0.00051504 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1368-6_0_6_load_109 | 71 | 0.0016838 | 0.00042201 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1368-6_0_6_load_110 | 72 | 0.0016623 | 0.00041661 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1368-6_0_6_load_116 | 73 | 0.0019256 | 0.0004826 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1368-6_0_6_load_111 | 74 | 0.0012985 | 0.00032542 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1368-6_0_6_load_112 | 75 | 0.0016735 | 0.00041942 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1368-6_0_6_load_114 | 76 | 0.0017878 | 0.00044807 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1368-6_0_6_load_115 | 77 | 0.0020086 | 0.00050341 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1368-6_0_6_load_118 | 79 | 0.0014757 | 0.00036986 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1368-6_0_6_load_119 | 80 | 0.0016951 | 0.00042482 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1368-6_0_6_load_120 | 81 | 0.0018855 | 0.00047255 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1368-6_0_6_load_121 | 82 | 0.00084578 | 0.00021197 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1368-6_0_6_load_126 | 84 | 0.0017748 | 0.0004448 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1368-6_0_6_load_123 | 85 | 0.00086718 | 0.00021734 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1368-6_0_6_load_127 | 86 | 0.00087575 | 0.00021948 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1368-6_0_6_load_128 | 87 | 0.00080769 | 0.00020243 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1368-6_0_6_load_129 | 88 | 0.00091366 | 0.00022899 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1368-6_0_6_load_130 | 89 | 0.0017426 | 0.00043675 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1368-6_0_6_load_131 | 90 | 0.0010252 | 0.00025694 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1368-6_0_6_load_132 | 91 | 0.0011441 | 0.00028674 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1368-6_0_6_load_133 | 92 | 0.0027231 | 0.00068248 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1368-6_0_6_load_134 | 93 | 0.0014768 | 0.00037012 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1368-6_0_6_load_135 | 94 | 0.0010284 | 0.00025775 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1368-6_0_6_load_137 | 95 | 0.0032328 | 0.00081022 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1368-6_0_6_load_48 | 96 | 0.0024824 | 0.00062216 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1368-6_0_6_load_49 | 97 | 0.0016057 | 0.00040244 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1368-6_0_6_load_139 | 98 | 0.0012207 | 0.00030593 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1368-6_0_6_load_52 | 100 | 0.00045463 | 0.00011394 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1368-6_0_6_load_141 | 101 | 0.0022038 | 0.00055232 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1368-6_0_6_load_142 | 102 | 0.0021763 | 0.00054542 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1368-6_0_6_load_113 | 103 | 0.0023515 | 0.00058934 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1368-6_0_6_load_146 | 104 | 0.0020165 | 0.00050538 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1368-6_0_6_load_148 | 105 | 0.0015197 | 0.00038087 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1368-6_0_6_load_143 | 106 | 0.0014434 | 0.00036175 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1368-6_0_6_load_144 | 107 | 0.0020575 | 0.00051566 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1368-6_0_6_load_145 | 108 | 0.0017755 | 0.00044498 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1368-6_0_6_load_147 | 109 | 0.0023465 | 0.00058808 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1368-6_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0060759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1368-6_0_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.019079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1368-6_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.016885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1368-6_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.083545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1368-6_0_6_line_4 | NAYY 4x150 SE | 3 | 5 | 0.010454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1368-6_0_6_line_5 | NAYY 4x150 SE | 3 | 6 | 0.010763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1368-6_0_6_line_6 | NAYY 4x150 SE | 4 | 7 | 0.012475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1368-6_0_6_line_7 | NAYY 4x150 SE | 5 | 8 | 0.019982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1368-6_0_6_line_8 | NAYY 4x150 SE | 6 | 9 | 0.01832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1368-6_0_6_line_9 | NAYY 4x150 SE | 8 | 10 | 0.0069158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1368-6_0_6_line_10 | NAYY 4x150 SE | 10 | 11 | 0.008673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1368-6_0_6_line_11 | NAYY 4x150 SE | 11 | 12 | 0.022352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1368-6_0_6_line_12 | NAYY 4x150 SE | 11 | 13 | 0.017005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1368-6_0_6_line_13 | NAYY 4x150 SE | 12 | 14 | 0.019325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1368-6_0_6_line_14 | NAYY 4x150 SE | 13 | 15 | 0.025699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1368-6_0_6_line_15 | NAYY 4x150 SE | 14 | 34 | 0.021004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1368-6_0_6_line_16 | NAYY 4x150 SE | 15 | 32 | 0.027617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1368-6_0_6_line_17 | NAYY 4x150 SE | 16 | 17 | 0.01658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1368-6_0_6_line_18 | NAYY 4x150 SE | 17 | 18 | 0.11985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1368-6_0_6_line_19 | NAYY 4x150 SE | 17 | 19 | 0.021492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1368-6_0_6_line_20 | NAYY 4x150 SE | 18 | 20 | 0.053407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1368-6_0_6_line_21 | NAYY 4x150 SE | 19 | 21 | 0.0051526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1368-6_0_6_line_22 | NAYY 4x150 SE | 20 | 22 | 0.0092789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1368-6_0_6_line_23 | NAYY 4x150 SE | 21 | 23 | 0.025035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1368-6_0_6_line_24 | NAYY 4x150 SE | 22 | 27 | 0.062737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1368-6_0_6_line_25 | NAYY 4x150 SE | 23 | 24 | 0.003216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1368-6_0_6_line_26 | NAYY 4x150 SE | 24 | 25 | 0.028807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1368-6_0_6_line_27 | NAYY 4x150 SE | 25 | 26 | 0.0017517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1368-6_0_6_line_28 | NAYY 4x150 SE | 26 | 28 | 0.022141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1368-6_0_6_line_29 | NAYY 4x150 SE | 27 | 100 | 0.031834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1368-6_0_6_line_30 | NAYY 4x150 SE | 28 | 29 | 0.03411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1368-6_0_6_line_31 | NAYY 4x150 SE | 29 | 30 | 0.011813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1368-6_0_6_line_32 | NAYY 4x150 SE | 30 | 31 | 0.11659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1368-6_0_6_line_33 | NAYY 4x150 SE | 30 | 32 | 0.014972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1368-6_0_6_line_34 | NAYY 4x150 SE | 31 | 33 | 0.15257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1368-6_0_6_line_35 | NAYY 4x150 SE | 33 | 42 | 0.18594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1368-6_0_6_line_36 | NAYY 4x150 SE | 34 | 35 | 0.0027825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1368-6_0_6_line_37 | NAYY 4x150 SE | 35 | 36 | 0.034384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1368-6_0_6_line_38 | NAYY 4x150 SE | 37 | 38 | 0.0072324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1368-6_0_6_line_39 | NAYY 4x150 SE | 37 | 39 | 0.01982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1368-6_0_6_line_40 | NAYY 4x150 SE | 38 | 40 | 0.12548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1368-6_0_6_line_41 | NAYY 4x150 SE | 39 | 41 | 0.048967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1368-6_0_6_line_42 | NAYY 4x150 SE | 40 | 43 | 0.023604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_1368-6_0_6_line_43 | NAYY 4x150 SE | 41 | 42 | 0.075102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_1368-6_0_6_line_44 | NAYY 4x150 SE | 43 | 44 | 0.00050675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1368-6_0_6_line_45 | NAYY 4x150 SE | 44 | 45 | 0.017808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_1368-6_0_6_line_46 | NAYY 4x150 SE | 45 | 46 | 0.01271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1368-6_0_6_line_47 | NAYY 4x150 SE | 46 | 94 | 0.036885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1368-6_0_6_line_48 | NAYY 4x150 SE | 47 | 48 | 0.017588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1368-6_0_6_line_49 | NAYY 4x150 SE | 47 | 49 | 0.077333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1368-6_0_6_line_50 | NAYY 4x150 SE | 48 | 50 | 0.046507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1368-6_0_6_line_51 | NAYY 4x150 SE | 50 | 51 | 0.012169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1368-6_0_6_line_52 | NAYY 4x150 SE | 50 | 52 | 0.013505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_1368-6_0_6_line_53 | NAYY 4x150 SE | 51 | 53 | 0.0014716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_1368-6_0_6_line_54 | NAYY 4x150 SE | 52 | 54 | 0.013261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1368-6_0_6_line_55 | NAYY 4x150 SE | 53 | 55 | 0.008983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
56 | LV_1368-6_0_6_line_56 | NAYY 4x150 SE | 54 | 56 | 0.012116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_1368-6_0_6_line_57 | NAYY 4x150 SE | 55 | 57 | 0.030628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_1368-6_0_6_line_58 | NAYY 4x150 SE | 56 | 59 | 0.014675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_1368-6_0_6_line_59 | NAYY 4x150 SE | 57 | 58 | 0.049105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1368-6_0_6_line_60 | NAYY 4x150 SE | 58 | 103 | 0.021668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1368-6_0_6_line_61 | NAYY 4x150 SE | 59 | 60 | 0.0021875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1368-6_0_6_line_62 | NAYY 4x150 SE | 60 | 61 | 0.0097951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1368-6_0_6_line_63 | NAYY 4x150 SE | 61 | 62 | 0.013903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1368-6_0_6_line_64 | NAYY 4x150 SE | 62 | 63 | 0.0070088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1368-6_0_6_line_65 | NAYY 4x150 SE | 63 | 64 | 0.017755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1368-6_0_6_line_66 | NAYY 4x150 SE | 65 | 66 | 0.021804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_1368-6_0_6_line_67 | NAYY 4x150 SE | 65 | 67 | 0.0092648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_1368-6_0_6_line_68 | NAYY 4x150 SE | 66 | 68 | 0.002266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_1368-6_0_6_line_69 | NAYY 4x150 SE | 67 | 69 | 0.00086824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_1368-6_0_6_line_70 | NAYY 4x150 SE | 68 | 70 | 0.01581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
71 | LV_1368-6_0_6_line_71 | NAYY 4x150 SE | 69 | 71 | 0.012724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_1368-6_0_6_line_72 | NAYY 4x150 SE | 70 | 72 | 0.021805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_1368-6_0_6_line_73 | NAYY 4x150 SE | 71 | 73 | 0.017525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_1368-6_0_6_line_74 | NAYY 4x150 SE | 72 | 74 | 0.015679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_1368-6_0_6_line_75 | NAYY 4x150 SE | 73 | 78 | 0.023043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_1368-6_0_6_line_76 | NAYY 4x150 SE | 74 | 75 | 0.010636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1368-6_0_6_line_77 | NAYY 4x150 SE | 75 | 76 | 0.013651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_1368-6_0_6_line_78 | NAYY 4x150 SE | 76 | 77 | 0.014762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_1368-6_0_6_line_79 | NAYY 4x150 SE | 77 | 105 | 0.0020949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_1368-6_0_6_line_80 | NAYY 4x150 SE | 78 | 79 | 0.014198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1368-6_0_6_line_81 | NAYY 4x150 SE | 78 | 80 | 0.033145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
82 | LV_1368-6_0_6_line_82 | NAYY 4x150 SE | 79 | 81 | 0.0048578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1368-6_0_6_line_83 | NAYY 4x150 SE | 80 | 82 | 0.0025668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_1368-6_0_6_line_84 | NAYY 4x150 SE | 81 | 83 | 0.088054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1368-6_0_6_line_85 | NAYY 4x150 SE | 82 | 84 | 0.0044623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_1368-6_0_6_line_86 | NAYY 4x150 SE | 83 | 85 | 0.010348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1368-6_0_6_line_87 | NAYY 4x150 SE | 84 | 86 | 0.016071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1368-6_0_6_line_88 | NAYY 4x150 SE | 86 | 87 | 0.020596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_1368-6_0_6_line_89 | NAYY 4x150 SE | 87 | 88 | 0.0087006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1368-6_0_6_line_90 | NAYY 4x150 SE | 88 | 89 | 0.0047934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1368-6_0_6_line_91 | NAYY 4x150 SE | 89 | 90 | 0.0010905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_1368-6_0_6_line_92 | NAYY 4x150 SE | 90 | 91 | 0.021051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_1368-6_0_6_line_93 | NAYY 4x150 SE | 91 | 92 | 0.01103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_1368-6_0_6_line_94 | NAYY 4x150 SE | 92 | 93 | 0.011007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_1368-6_0_6_line_95 | NAYY 4x150 SE | 93 | 106 | 0.022753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_1368-6_0_6_line_96 | NAYY 4x150 SE | 94 | 95 | 0.04359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1368-6_0_6_line_97 | NAYY 4x150 SE | 95 | 98 | 0.054058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_1368-6_0_6_line_98 | NAYY 4x150 SE | 96 | 97 | 0.040594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1368-6_0_6_line_99 | NAYY 4x150 SE | 96 | 98 | 0.22501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1368-6_0_6_line_100 | NAYY 4x150 SE | 98 | 99 | 0.056645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_1368-6_0_6_line_101 | NAYY 4x150 SE | 99 | 101 | 0.027436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_1368-6_0_6_line_102 | NAYY 4x150 SE | 99 | 102 | 0.031421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1368-6_0_6_line_103 | NAYY 4x150 SE | 101 | 107 | 0.014744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_1368-6_0_6_line_104 | NAYY 4x150 SE | 102 | 108 | 0.012442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1368-6_0_6_line_105 | NAYY 4x150 SE | 103 | 104 | 0.0032809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_1368-6_0_6_line_106 | NAYY 4x150 SE | 104 | 109 | 0.0019983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_1368-6_0_6_line_107 | NAYY 4x150 SE | 105 | 109 | 0.013144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_1368-6_0_6_line_108 | NAYY 4x150 SE | 106 | 107 | 0.0078941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1368-6_0_6_trafo_40 | 0.25 MVA 20/0.4 kV | 110 | 38 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2702010.2112 | 1210841.5776 | 2702006.5415 | 1210836.7351
1 | 2702010.2112 | 1210841.5776 | 2702015.09 | 1210848.0156 | 2702013.2834 | 1210854.089 | 2702009.7846 | 1210857.174
2 | 2701996.3435 | 1210823.2778 | 2702006.5415 | 1210836.7351
3 | 2702009.7846 | 1210857.174 | 2702086.065 | 1210891.2488
4 | 2701996.3435 | 1210823.2778 | 2701988.4249 | 1210830.1026
5 | 2701996.3435 | 1210823.2778 | 2702004.713 | 1210816.5104
6 | 2702086.065 | 1210891.2488 | 2702095.9801 | 1210883.6774
7 | 2701973.2889 | 1210843.1479 | 2701988.4249 | 1210830.1026
8 | 2702018.9587 | 1210804.9917 | 2702004.713 | 1210816.5104
9 | 2701968.0503 | 1210847.6629 | 2701973.2889 | 1210843.1479
10 | 2701961.4806 | 1210853.3251 | 2701968.0503 | 1210847.6629
11 | 2701961.4806 | 1210853.3251 | 2701973.9154 | 1210868.9041 | 2701975.2338 | 1210870.9326
12 | 2701961.4806 | 1210853.3251 | 2701947.884 | 1210863.5382
13 | 2701975.2338 | 1210870.9326 | 2701985.7655 | 1210887.1362
14 | 2701947.884 | 1210863.5382 | 2701927.3358 | 1210878.973
15 | 2701986.7711 | 1210906.0832 | 2701986.7711 | 1210906.0832 | 2701990.0345 | 1210900.6018 | 2701990.3455 | 1210895.7482 | 2701986.6168 | 1210888.446 | 2701985.7655 | 1210887.1362
16 | 2701905.2545 | 1210895.5593 | 2701927.3358 | 1210878.973
17 | 2701816.6147 | 1211028.6294 | 2701822.189 | 1211031.1262 | 2701832.1992 | 1211034.2018
18 | 2701816.6147 | 1211028.6294 | 2701810.7854 | 1211039.7265 | 2701802.39 | 1211051.1023 | 2701790.2139 | 1211062.6582 | 2701777.5258 | 1211074.3833 | 2701732.9617 | 1211113.2289
19 | 2701816.6147 | 1211028.6294 | 2701820.7443 | 1211007.5382
20 | 2701692.7027 | 1211148.3219 | 2701732.9617 | 1211113.2289
21 | 2701820.7443 | 1211007.5382 | 2701821.078 | 1211005.834 | 2701821.4904 | 1211002.443
22 | 2701692.7027 | 1211148.3219 | 2701692.7027 | 1211148.3219 | 2701689.3553 | 1211156.9759
23 | 2701825.904 | 1210977.9025 | 2701823.6423 | 1210984.7519 | 2701821.4904 | 1211002.443
24 | 2701689.3553 | 1211156.9759 | 2701678.804 | 1211184.2546 | 2701679.495 | 1211203.0128 | 2701681.2563 | 1211217.6248
25 | 2701825.904 | 1210977.9025 | 2701826.9123 | 1210974.8487
26 | 2701840.5416 | 1210949.8741 | 2701836.6065 | 1210954.2074 | 2701830.3271 | 1210964.5074 | 2701826.9123 | 1210974.8487
27 | 2701841.7192 | 1210948.5772 | 2701840.5416 | 1210949.8741
28 | 2701841.7192 | 1210948.5772 | 2701843.6559 | 1210946.4445 | 2701853.92 | 1210934.7004 | 2701856.8597 | 1210932.5156
29 | 2701681.2563 | 1211217.6248 | 2701681.5391 | 1211219.9706 | 2701685.7172 | 1211231.6834 | 2701694.6046 | 1211246.2165
30 | 2701883.9609 | 1210911.8063 | 2701867.7545 | 1210924.4183 | 2701856.8597 | 1210932.5156
31 | 2701893.2833 | 1210904.5515 | 2701883.9609 | 1210911.8063
32 | 2701826.0533 | 1210817.3205 | 2701830.5555 | 1210824.7469 | 2701830.2438 | 1210842.9988 | 2701833.8529 | 1210853.7568 | 2701839.8222 | 1210861.6198 | 2701893.2833 | 1210904.5515
33 | 2701893.2833 | 1210904.5515 | 2701905.2545 | 1210895.5593
34 | 2701826.0533 | 1210817.3205 | 2701673.7438 | 1210826.2585
35 | 2701673.7438 | 1210826.2585 | 2701531.6019 | 1210706.3805
36 | 2701986.7711 | 1210906.0832 | 2701984.6661 | 1210907.9029
37 | 2701962.3672 | 1210933.93 | 2701978.8247 | 1210912.9522 | 2701984.6661 | 1210907.9029
38 | 2701436.6672 | 1210803.113 | 2701431.9026 | 1210808.5542
39 | 2701436.6672 | 1210803.113 | 2701449.7244 | 1210788.2014
40 | 2701431.9026 | 1210808.5542 | 2701385.5846 | 1210861.4501 | 2701348.0332 | 1210901.8643
41 | 2701449.7244 | 1210788.2014 | 2701460.3642 | 1210776.0506 | 2701472.2629 | 1210745.4983 | 2701472.2756 | 1210745.4726
42 | 2701331.966 | 1210919.1564 | 2701348.0332 | 1210901.8643
43 | 2701531.6019 | 1210706.3805 | 2701523.2031 | 1210705.9039 | 2701509.7267 | 1210709.8996 | 2701499.8069 | 1210716.1686 | 2701485.2421 | 1210727.3953 | 2701482.2889 | 1210729.8579 | 2701480.471 | 1210731.7172 | 2701478.6925 | 1210733.944 | 2701477.1331 | 1210736.2413 | 2701475.0973 | 1210739.7425 | 2701472.2756 | 1210745.4726
44 | 2701331.966 | 1210919.1564 | 2701331.6211 | 1210919.5276
45 | 2701319.4992 | 1210932.5737 | 2701331.6211 | 1210919.5276
46 | 2701310.8478 | 1210941.8847 | 2701319.4992 | 1210932.5737
47 | 2701294.6965 | 1210974.3084 | 2701295.7918 | 1210967.1988 | 2701305.5114 | 1210947.6279 | 2701310.8478 | 1210941.8847
48 | 2700988.0089 | 1210941.7376 | 2701003.4586 | 1210950.1416
49 | 2700988.0089 | 1210941.7376 | 2700982.2102 | 1210864.6226
50 | 2701046.8029 | 1210962.3843 | 2701026.308 | 1210962.5707 | 2701003.4586 | 1210950.1416
51 | 2701046.8029 | 1210962.3843 | 2701047.5913 | 1210974.5282
52 | 2701046.8029 | 1210962.3843 | 2701046.6156 | 1210959.5347 | 2701047.4102 | 1210948.9149
53 | 2701047.6867 | 1210975.9967 | 2701047.5913 | 1210974.5282
54 | 2701048.3997 | 1210935.6906 | 2701047.4102 | 1210948.9149
55 | 2701047.6867 | 1210975.9967 | 2701048.2686 | 1210984.9609
56 | 2701048.3997 | 1210935.6906 | 2701049.3038 | 1210923.6083
57 | 2701052.6972 | 1211015.1306 | 2701049.4067 | 1211002.4897 | 2701048.2686 | 1210984.9609
58 | 2701050.3988 | 1210908.9746 | 2701049.3038 | 1210923.6083
59 | 2701052.6972 | 1211015.1306 | 2701055.4652 | 1211025.7641 | 2701072.9104 | 1211034.6436 | 2701091.339 | 1211032.595
60 | 2701091.339 | 1211032.595 | 2701106.409 | 1211030.9197 | 2701112.2745 | 1211028.1059
61 | 2701050.3988 | 1210908.9746 | 2701050.3988 | 1210908.9746 | 2701051.3947 | 1210907.0269
62 | 2701055.8538 | 1210898.3057 | 2701051.3947 | 1210907.0269
63 | 2701055.8538 | 1210898.3057 | 2701062.183 | 1210885.9272
64 | 2701065.3737 | 1210879.6868 | 2701062.183 | 1210885.9272
65 | 2701073.4566 | 1210863.8782 | 2701065.3737 | 1210879.6868
66 | 2701117.9467 | 1210904.1046 | 2701120.1509 | 1210925.7965
67 | 2701117.9467 | 1210904.1046 | 2701117.9467 | 1210904.1046 | 2701123.7747 | 1210896.9023
68 | 2701120.1509 | 1210925.7965 | 2701120.38 | 1210928.0508
69 | 2701124.3208 | 1210896.2274 | 2701123.7747 | 1210896.9023
70 | 2701121.9926 | 1210943.7779 | 2701121.9656 | 1210943.6558 | 2701120.38 | 1210928.0508
71 | 2701124.3208 | 1210896.2274 | 2701132.3249 | 1210886.3359
72 | 2701121.9926 | 1210943.7779 | 2701126.7086 | 1210965.067
73 | 2701132.3249 | 1210886.3359 | 2701132.3249 | 1210886.3359 | 2701149.1342 | 1210891.2935
74 | 2701129.9975 | 1210980.3949 | 2701129.5977 | 1210978.1092 | 2701126.7086 | 1210965.067
75 | 2701164.9547 | 1210906.9924 | 2701153.925 | 1210892.7065 | 2701149.1342 | 1210891.2935
76 | 2701131.8298 | 1210990.8722 | 2701129.9975 | 1210980.3949
77 | 2701131.8298 | 1210990.8722 | 2701134.1817 | 1211004.3196
78 | 2701134.1817 | 1211004.3196 | 2701134.4132 | 1211005.6434 | 2701129.6314 | 1211018.1802
79 | 2701128.8848 | 1211020.1376 | 2701129.6314 | 1211018.1802
80 | 2701164.9547 | 1210906.9924 | 2701174.7052 | 1210899.4636 | 2701176.2779 | 1210898.4353
81 | 2701164.9547 | 1210906.9924 | 2701185.2164 | 1210933.2238
82 | 2701180.3438 | 1210895.777 | 2701176.2779 | 1210898.4353
83 | 2701185.2164 | 1210933.2238 | 2701186.7854 | 1210935.2551
84 | 2701206.5406 | 1210816.4567 | 2701204.7801 | 1210826.5784 | 2701203.5005 | 1210836.5859 | 2701201.6836 | 1210842.4258 | 2701198.2252 | 1210850.9286 | 2701197.2006 | 1210860.6958 | 2701196.2966 | 1210870.9654 | 2701195.8715 | 1210881.232 | 2701194.4539 | 1210885.4887 | 2701189.8393 | 1210889.5689 | 2701180.3438 | 1210895.777
85 | 2701189.5132 | 1210938.7866 | 2701189.5132 | 1210938.7866 | 2701186.7854 | 1210935.2551
86 | 2701211.7246 | 1210807.494 | 2701206.5406 | 1210816.4567
87 | 2701189.5132 | 1210938.7866 | 2701199.9976 | 1210950.9663
88 | 2701199.9976 | 1210950.9663 | 2701213.4344 | 1210966.5759
89 | 2701213.4344 | 1210966.5759 | 2701214.2525 | 1210967.5263 | 2701215.6238 | 1210974.8456
90 | 2701216.5066 | 1210979.557 | 2701215.6238 | 1210974.8456
91 | 2701216.5066 | 1210979.557 | 2701216.7074 | 1210980.6289
92 | 2701216.7074 | 1210980.6289 | 2701217.4793 | 1210984.7486 | 2701211.8504 | 1211000.6409
93 | 2701211.8504 | 1211000.6409 | 2701208.1677 | 1211011.0385
94 | 2701208.1677 | 1211011.0385 | 2701204.4931 | 1211021.4135
95 | 2701204.4931 | 1211021.4135 | 2701202.0713 | 1211028.2509 | 2701199.4843 | 1211043.5332
96 | 2701294.6965 | 1210974.3084 | 2701291.8365 | 1210992.8717 | 2701276.7939 | 1211012.598
97 | 2701276.7939 | 1211012.598 | 2701275.037 | 1211014.9019 | 2701248.8827 | 1211035.0499 | 2701240.1016 | 1211050.9291
98 | 2701388.1974 | 1211234.9359 | 2701403.4929 | 1211209.542 | 2701408.7206 | 1211199.9213
99 | 2701240.1016 | 1211050.9291 | 2701408.7206 | 1211199.9213
100 | 2701205.185 | 1211092.8821 | 2701221.8062 | 1211084.0135 | 2701240.1016 | 1211050.9291
101 | 2701205.185 | 1211092.8821 | 2701201.8264 | 1211077.1586 | 2701200.2285 | 1211065.9137
102 | 2701205.185 | 1211092.8821 | 2701199.0758 | 1211093.6791 | 2701191.1732 | 1211093.556 | 2701178.5615 | 1211091.8965 | 2701173.9394 | 1211091.5391
103 | 2701200.2285 | 1211065.9137 | 2701198.16 | 1211051.3562 | 2701198.1667 | 1211051.3165
104 | 2701173.9394 | 1211091.5391 | 2701171.5629 | 1211091.3553 | 2701166.4809 | 1211091.6359 | 2701161.6183 | 1211092.6586
105 | 2701115.2326 | 1211026.6869 | 2701112.2745 | 1211028.1059
106 | 2701117.0343 | 1211025.8225 | 2701115.2326 | 1211026.6869
107 | 2701117.0343 | 1211025.8225 | 2701128.8848 | 1211020.1376 | 2701128.8848 | 1211020.1376
108 | 2701198.1667 | 1211051.3165 | 2701199.4843 | 1211043.5332

## bus_geodata
| x | y | coords
0 | 2702010.2112 | 1210841.5776
1 | 2702006.5415 | 1210836.7351
2 | 2702009.7846 | 1210857.174
3 | 2701996.3435 | 1210823.2778
4 | 2702086.065 | 1210891.2488
5 | 2701988.4249 | 1210830.1026
6 | 2702004.713 | 1210816.5104
7 | 2702095.9801 | 1210883.6774
8 | 2701973.2889 | 1210843.1479
9 | 2702018.9587 | 1210804.9917
10 | 2701968.0503 | 1210847.6629
11 | 2701961.4806 | 1210853.3251
12 | 2701975.2338 | 1210870.9326
13 | 2701947.884 | 1210863.5382
14 | 2701985.7655 | 1210887.1362
15 | 2701927.3358 | 1210878.973
16 | 2701832.1992 | 1211034.2018
17 | 2701816.6147 | 1211028.6294
18 | 2701732.9617 | 1211113.2289
19 | 2701820.7443 | 1211007.5382
20 | 2701692.7027 | 1211148.3219
21 | 2701821.4904 | 1211002.443
22 | 2701689.3553 | 1211156.9759
23 | 2701825.904 | 1210977.9025
24 | 2701826.9123 | 1210974.8487
25 | 2701840.5416 | 1210949.8741
26 | 2701841.7192 | 1210948.5772
27 | 2701681.2563 | 1211217.6248
28 | 2701856.8597 | 1210932.5156
29 | 2701883.9609 | 1210911.8063
30 | 2701893.2833 | 1210904.5515
31 | 2701826.0533 | 1210817.3205
32 | 2701905.2545 | 1210895.5593
33 | 2701673.7438 | 1210826.2585
34 | 2701986.7711 | 1210906.0832
35 | 2701984.6661 | 1210907.9029
36 | 2701962.3672 | 1210933.93
37 | 2701436.6672 | 1210803.113
38 | 2701431.9026 | 1210808.5542
39 | 2701449.7244 | 1210788.2014
40 | 2701348.0332 | 1210901.8643
41 | 2701472.2756 | 1210745.4726
42 | 2701531.6019 | 1210706.3805
43 | 2701331.966 | 1210919.1564
44 | 2701331.6211 | 1210919.5276
45 | 2701319.4992 | 1210932.5737
46 | 2701310.8478 | 1210941.8847
47 | 2700988.0089 | 1210941.7376
48 | 2701003.4586 | 1210950.1416
49 | 2700982.2102 | 1210864.6226
50 | 2701046.8029 | 1210962.3843
51 | 2701047.5913 | 1210974.5282
52 | 2701047.4102 | 1210948.9149
53 | 2701047.6867 | 1210975.9967
54 | 2701048.3997 | 1210935.6906
55 | 2701048.2686 | 1210984.9609
56 | 2701049.3038 | 1210923.6083
57 | 2701052.6972 | 1211015.1306
58 | 2701091.339 | 1211032.595
59 | 2701050.3988 | 1210908.9746
60 | 2701051.3947 | 1210907.0269
61 | 2701055.8538 | 1210898.3057
62 | 2701062.183 | 1210885.9272
63 | 2701065.3737 | 1210879.6868
64 | 2701073.4566 | 1210863.8782
65 | 2701117.9467 | 1210904.1046
66 | 2701120.1509 | 1210925.7965
67 | 2701123.7747 | 1210896.9023
68 | 2701120.38 | 1210928.0508
69 | 2701124.3208 | 1210896.2274
70 | 2701121.9927 | 1210943.7779
71 | 2701132.3249 | 1210886.3359
72 | 2701126.7086 | 1210965.067
73 | 2701149.1342 | 1210891.2935
74 | 2701129.9975 | 1210980.3949
75 | 2701131.8298 | 1210990.8722
76 | 2701134.1817 | 1211004.3196
77 | 2701129.6314 | 1211018.1802
78 | 2701164.9547 | 1210906.9924
79 | 2701176.2779 | 1210898.4353
80 | 2701185.2164 | 1210933.2238
81 | 2701180.3438 | 1210895.777
82 | 2701186.7854 | 1210935.2551
83 | 2701206.5406 | 1210816.4567
84 | 2701189.5132 | 1210938.7866
85 | 2701211.7246 | 1210807.494
86 | 2701199.9976 | 1210950.9663
87 | 2701213.4344 | 1210966.5759
88 | 2701215.6238 | 1210974.8456
89 | 2701216.5066 | 1210979.557
90 | 2701216.7074 | 1210980.6289
91 | 2701211.8504 | 1211000.6409
92 | 2701208.1677 | 1211011.0385
93 | 2701204.4931 | 1211021.4135
94 | 2701294.6965 | 1210974.3084
95 | 2701276.7939 | 1211012.598
96 | 2701408.7206 | 1211199.9213
97 | 2701388.1974 | 1211234.9359
98 | 2701240.1016 | 1211050.9291
99 | 2701205.185 | 1211092.8821
100 | 2701694.6046 | 1211246.2165
101 | 2701200.2285 | 1211065.9137
102 | 2701173.9394 | 1211091.5391
103 | 2701112.2745 | 1211028.1059
104 | 2701115.2326 | 1211026.6869
105 | 2701128.8848 | 1211020.1376
106 | 2701199.4843 | 1211043.5332
107 | 2701198.1667 | 1211051.3165
108 | 2701161.6183 | 1211092.6586
109 | 2701117.0343 | 1211025.8225
110 | 2701431.9026 | 1210808.5542

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97184 | -0.19789 | 0.0035699 | 0.0008947
1 | 0.97195 | -0.1971 | 0.003191 | 0.00079974
2 | 0.9716 | -0.19966 | 0.0021958 | 0.00055032
3 | 0.97234 | -0.19433 | 0.0041491 | 0.0010399
4 | 0.9708 | -0.20545 | 0.001236 | 0.00030976
5 | 0.97268 | -0.19185 | 0.0025258 | 0.00063304
6 | 0.97229 | -0.19465 | 0.0015737 | 0.0003944
7 | 0.9707 | -0.20615 | 0.0053144 | 0.0013319
8 | 0.97341 | -0.18659 | 0.0037802 | 0.00094742
9 | 0.97226 | -0.19488 | 0.0012167 | 0.00030493
10 | 0.97371 | -0.1845 | 0.0052098 | 0.0013057
11 | 0.97414 | -0.18139 | 0 | 0
12 | 0.97357 | -0.18545 | 0.0037332 | 0.00093564
13 | 0.97541 | -0.17225 | 0.0026946 | 0.00067532
14 | 0.97319 | -0.1882 | 0.0037042 | 0.00092836
15 | 0.97643 | -0.16499 | 0.0040595 | 0.0010174
16 | 0.97548 | -0.17184 | 0.00075795 | 0.00018996
17 | 0.9755 | -0.1717 | 0 | 0
18 | 0.97501 | -0.17529 | 0.00069067 | 0.0001731
19 | 0.97561 | -0.17089 | 0.0040782 | 0.0010221
20 | 0.97484 | -0.1765 | 0.00055617 | 0.00013939
21 | 0.97567 | -0.17047 | 0.0010557 | 0.00026459
22 | 0.97482 | -0.17666 | 0.00051501 | 0.00012907
23 | 0.97599 | -0.16817 | 0.0006297 | 0.00015782
24 | 0.97604 | -0.16786 | 0.00057717 | 0.00014465
25 | 0.97645 | -0.16485 | 0.00064748 | 0.00016227
26 | 0.97648 | -0.16466 | 0.00066547 | 0.00016678
27 | 0.97472 | -0.17736 | 0.00061652 | 0.00015451
28 | 0.97684 | -0.16204 | 0.00066998 | 0.00016791
29 | 0.97744 | -0.15778 | 0.00066466 | 0.00016658
30 | 0.97766 | -0.15622 | 0 | 0
31 | 0.98184 | -0.12648 | 0.00040429 | 0.00010132
32 | 0.97721 | -0.1594 | 0.0029762 | 0.0007459
33 | 0.98734 | -0.087713 | 0.0015769 | 0.0003952
34 | 0.97289 | -0.19036 | 0.0019206 | 0.00048136
35 | 0.97286 | -0.1906 | 0.0036711 | 0.00092006
36 | 0.97265 | -0.19212 | 0.0041971 | 0.0010519
37 | 0.99969 | -0.0020995 | 0.00080223 | 0.00020106
38 | 1 | 0 | -0.18905 | -0.04767
39 | 0.99886 | -0.0078065 | 0.0061195 | 0.0015337
40 | 0.99408 | -0.040872 | 0.00083666 | 0.00020969
41 | 0.99695 | -0.020942 | 0.0045689 | 0.0011451
42 | 0.99419 | -0.040026 | 0 | 0
43 | 0.99297 | -0.048547 | 0.00079576 | 0.00019944
44 | 0.99295 | -0.048711 | 0.00047906 | 0.00012006
45 | 0.99212 | -0.054436 | 0.00064013 | 0.00016043
46 | 0.99154 | -0.0585 | 0.00081937 | 0.00020535
47 | 0.9702 | -0.21006 | 0.0018457 | 0.00046258
48 | 0.97027 | -0.20956 | 0.0017344 | 0.00043467
49 | 0.9701 | -0.21078 | 0.00087027 | 0.00021811
50 | 0.97058 | -0.20736 | 0 | 0
51 | 0.97068 | -0.20661 | 0.001672 | 0.00041905
52 | 0.97049 | -0.20797 | 0.0012844 | 0.0003219
53 | 0.97069 | -0.20652 | 0.0012484 | 0.00031287
54 | 0.97042 | -0.20851 | 0.001328 | 0.00033283
55 | 0.97078 | -0.20588 | 0.0012557 | 0.0003147
56 | 0.97036 | -0.20894 | 0.0017419 | 0.00043657
57 | 0.9711 | -0.20356 | 0.002515 | 0.00063031
58 | 0.97168 | -0.19941 | 0.0011611 | 0.00029099
59 | 0.97026 | -0.2096 | 0.0011113 | 0.00027851
60 | 0.97024 | -0.20977 | 0.0020711 | 0.00051907
61 | 0.97017 | -0.21031 | 0.0011511 | 0.00028848
62 | 0.97008 | -0.21092 | 0.0013538 | 0.00033929
63 | 0.97005 | -0.21112 | 0.0011556 | 0.00028962
64 | 0.97001 | -0.21142 | 0.0015872 | 0.0003978
65 | 0.9746 | -0.17839 | 0.0018585 | 0.00046579
66 | 0.9741 | -0.18195 | 0.00099962 | 0.00025053
67 | 0.97482 | -0.17682 | 0.0016223 | 0.00040659
68 | 0.97405 | -0.18231 | 0.0017119 | 0.00042904
69 | 0.97484 | -0.17666 | 0.0013663 | 0.00034244
70 | 0.97371 | -0.18475 | 0.002055 | 0.00051504
71 | 0.97516 | -0.17437 | 0.0016838 | 0.00042201
72 | 0.97327 | -0.18795 | 0.0016623 | 0.00041661
73 | 0.97561 | -0.17111 | 0.0019256 | 0.0004826
74 | 0.97296 | -0.19016 | 0.0012985 | 0.00032542
75 | 0.97276 | -0.19162 | 0.0016735 | 0.00041942
76 | 0.97251 | -0.1934 | 0.0017878 | 0.00044807
77 | 0.97225 | -0.19524 | 0.0020086 | 0.00050341
78 | 0.97623 | -0.16668 | 0 | 0
79 | 0.97614 | -0.16731 | 0.0014757 | 0.00036986
80 | 0.97719 | -0.15982 | 0.0016951 | 0.00042482
81 | 0.97612 | -0.16745 | 0.0018855 | 0.00047255
82 | 0.97727 | -0.15927 | 0.00084578 | 0.00021197
83 | 0.97601 | -0.16825 | 0 | 0
84 | 0.9774 | -0.15831 | 0.0017748 | 0.0004448
85 | 0.976 | -0.16835 | 0.00086718 | 0.00021734
86 | 0.9779 | -0.15475 | 0.00087575 | 0.00021948
87 | 0.97855 | -0.15013 | 0.00080769 | 0.00020243
88 | 0.97882 | -0.14815 | 0.00091366 | 0.00022899
89 | 0.97898 | -0.14705 | 0.0017426 | 0.00043675
90 | 0.97901 | -0.14679 | 0.0010252 | 0.00025694
91 | 0.97972 | -0.14175 | 0.0011441 | 0.00028674
92 | 0.9801 | -0.13907 | 0.0027231 | 0.00068248
93 | 0.98049 | -0.13629 | 0.0014768 | 0.00037012
94 | 0.98986 | -0.070217 | 0.0010284 | 0.00025775
95 | 0.9879 | -0.083962 | 0.0032328 | 0.00081022
96 | 0.98422 | -0.10998 | 0.0024824 | 0.00062216
97 | 0.98412 | -0.11065 | 0.0016057 | 0.00040244
98 | 0.98555 | -0.10048 | 0.0012207 | 0.00030593
99 | 0.98323 | -0.11683 | 0 | 0
100 | 0.9747 | -0.17752 | 0.00045463 | 0.00011394
101 | 0.98216 | -0.12441 | 0.0022038 | 0.00055232
102 | 0.98305 | -0.11812 | 0.0021763 | 0.00054542
103 | 0.97194 | -0.19749 | 0.0023515 | 0.00058934
104 | 0.97199 | -0.19717 | 0.0020165 | 0.00050538
105 | 0.97222 | -0.19549 | 0.0015197 | 0.00038087
106 | 0.98131 | -0.13044 | 0.0014434 | 0.00036175
107 | 0.98161 | -0.12837 | 0.0020575 | 0.00051566
108 | 0.98302 | -0.11835 | 0.0017755 | 0.00044498
109 | 0.97202 | -0.19696 | 0.0023465 | 0.00058808
110 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012324 | -0.0030883 | 0.012325 | 0.0030888 | 1.3499e-06 | 4.4391e-07 | 0.018869 | 0.018869 | 0.018869 | 0.97184 | -0.19789 | 0.97195 | -0.1971 | 6.9887
1 | 0.0087541 | 0.0021936 | -0.008752 | -0.002193 | 2.1388e-06 | 5.8628e-07 | 0.013404 | 0.013404 | 0.013404 | 0.97184 | -0.19789 | 0.9716 | -0.19966 | 4.9643
2 | -0.015516 | -0.0038885 | 0.015522 | 0.0038906 | 5.9454e-06 | 2.0773e-06 | 0.023755 | 0.023755 | 0.023755 | 0.97195 | -0.1971 | 0.97234 | -0.19433 | 8.7981
3 | 0.0065562 | 0.0016427 | -0.0065509 | -0.0016417 | 5.2559e-06 | 9.8769e-07 | 0.010041 | 0.010041 | 0.010041 | 0.9716 | -0.19966 | 0.9708 | -0.20545 | 3.7189
4 | -0.022462 | -0.0056295 | 0.02247 | 0.0056323 | 7.7079e-06 | 2.8349e-06 | 0.034375 | 0.034375 | 0.034375 | 0.97234 | -0.19433 | 0.97268 | -0.19185 | 12.7314
5 | 0.0027905 | 0.00069904 | -0.0027904 | -0.00069912 | 1.2248e-07 | -8.6387e-08 | 0.0042704 | 0.0042704 | 0.0042704 | 0.97234 | -0.19433 | 0.97229 | -0.19465 | 1.5816
6 | 0.005315 | 0.001332 | -0.0053144 | -0.0013319 | 5.1665e-07 | 4.4479e-08 | 0.0081466 | 0.0081467 | 0.0081467 | 0.9708 | -0.20545 | 0.9707 | -0.20615 | 3.0173
7 | -0.024996 | -0.0062654 | 0.025014 | 0.0062721 | 1.8232e-05 | 6.764e-06 | 0.038239 | 0.038239 | 0.038239 | 0.97268 | -0.19185 | 0.97341 | -0.18659 | 14.1625
8 | 0.0012167 | 0.00030472 | -0.0012167 | -0.00030493 | 3.9637e-08 | -2.1196e-07 | 0.001862 | 0.0018621 | 0.0018621 | 0.97229 | -0.19465 | 0.97226 | -0.19488 | 0.68967
9 | -0.028794 | -0.0072196 | 0.028802 | 0.0072227 | 8.3613e-06 | 3.1299e-06 | 0.044017 | 0.044017 | 0.044017 | 0.97341 | -0.18659 | 0.97371 | -0.1845 | 16.3027
10 | -0.034012 | -0.0085284 | 0.034027 | 0.0085339 | 1.4622e-05 | 5.5159e-06 | 0.051979 | 0.051979 | 0.051979 | 0.97371 | -0.1845 | 0.97414 | -0.18139 | 19.2514
11 | 0.017245 | 0.0043233 | -0.017235 | -0.0043199 | 9.6791e-06 | 3.4446e-06 | 0.026343 | 0.026343 | 0.026343 | 0.97414 | -0.18139 | 0.97357 | -0.18545 | 9.7566
12 | -0.051272 | -0.012857 | 0.051337 | 0.012882 | 6.5092e-05 | 2.4823e-05 | 0.078322 | 0.078322 | 0.078322 | 0.97414 | -0.18139 | 0.97541 | -0.17225 | 29.008
13 | 0.013502 | 0.0033842 | -0.013497 | -0.0033825 | 5.1358e-06 | 1.7351e-06 | 0.020637 | 0.020637 | 0.020637 | 0.97357 | -0.18545 | 0.97319 | -0.1882 | 7.6434
14 | -0.054032 | -0.013557 | 0.054086 | 0.013578 | 5.4484e-05 | 2.0313e-05 | 0.082432 | 0.082432 | 0.082432 | 0.97541 | -0.17225 | 0.97643 | -0.16499 | 15.2652
15 | 0.0097929 | 0.0024542 | -0.00979 | -0.0024533 | 2.9385e-06 | 8.693e-07 | 0.014973 | 0.014973 | 0.014973 | 0.97319 | -0.1882 | 0.97289 | -0.19036 | 5.5457
16 | -0.058146 | -0.014595 | 0.058191 | 0.014611 | 4.5111e-05 | 1.6313e-05 | 0.088618 | 0.088618 | 0.088618 | 0.97643 | -0.16499 | 0.97721 | -0.1594 | 10.9405
17 | -0.00075795 | -0.00018996 | 0.00075796 | 0.00018976 | 1.3829e-08 | -2.0167e-07 | 0.0011562 | 0.0011561 | 0.0011562 | 0.97548 | -0.17184 | 0.9755 | -0.1717 | 0.42822
18 | 0.0028349 | 0.00070729 | -0.0028335 | -0.00070825 | 1.398e-06 | -9.5786e-07 | 0.0043232 | 0.0043237 | 0.0043237 | 0.9755 | -0.1717 | 0.97501 | -0.17529 | 1.6014
19 | -0.0035929 | -0.00089705 | 0.0035933 | 0.00089694 | 4.0262e-07 | -1.1349e-07 | 0.0054793 | 0.0054792 | 0.0054793 | 0.9755 | -0.1717 | 0.97561 | -0.17089 | 2.0294
20 | 0.0021428 | 0.00053515 | -0.0021425 | -0.00053568 | 3.563e-07 | -5.2892e-07 | 0.0032696 | 0.0032699 | 0.0032699 | 0.97501 | -0.17529 | 0.97484 | -0.1765 | 1.2111
21 | -0.0076715 | -0.001919 | 0.0076719 | 0.0019191 | 4.4008e-07 | 1.0492e-07 | 0.011699 | 0.011699 | 0.011699 | 0.97561 | -0.17089 | 0.97567 | -0.17047 | 4.3331
22 | 0.0015863 | 0.00039629 | -0.0015863 | -0.0003964 | 3.3935e-08 | -1.0263e-07 | 0.0024209 | 0.002421 | 0.002421 | 0.97484 | -0.1765 | 0.97482 | -0.17666 | 0.89665
23 | -0.0087277 | -0.0021837 | 0.0087305 | 0.0021845 | 2.7672e-06 | 7.5156e-07 | 0.013309 | 0.013309 | 0.013309 | 0.97567 | -0.17047 | 0.97599 | -0.16817 | 4.9294
24 | 0.0010713 | 0.00026732 | -0.0010712 | -0.00026806 | 1.0465e-07 | -7.418e-07 | 0.0016348 | 0.0016351 | 0.0016351 | 0.97482 | -0.17666 | 0.97472 | -0.17736 | 0.60559
25 | -0.0093602 | -0.0023423 | 0.0093606 | 0.0023424 | 4.0861e-07 | 1.1697e-07 | 0.014269 | 0.014269 | 0.014269 | 0.97599 | -0.16817 | 0.97604 | -0.16786 | 5.285
26 | -0.0099377 | -0.0024871 | 0.0099419 | 0.0024883 | 4.1254e-06 | 1.2265e-06 | 0.015149 | 0.015149 | 0.015149 | 0.97604 | -0.16786 | 0.97645 | -0.16485 | 5.6109
27 | -0.010589 | -0.0026506 | 0.01059 | 0.0026507 | 2.846e-07 | 8.7549e-08 | 0.016136 | 0.016136 | 0.016136 | 0.97645 | -0.16485 | 0.97648 | -0.16466 | 5.9763
28 | -0.011255 | -0.0028175 | 0.011259 | 0.0028187 | 4.0635e-06 | 1.2858e-06 | 0.01715 | 0.01715 | 0.01715 | 0.97648 | -0.16466 | 0.97684 | -0.16204 | 6.3518
29 | 0.00045464 | 0.00011355 | -0.00045463 | -0.00011394 | 9.5671e-09 | -3.931e-07 | 0.00069392 | 0.00069406 | 0.00069406 | 0.97472 | -0.17736 | 0.9747 | -0.17752 | 0.25706
30 | -0.011929 | -0.0029866 | 0.011936 | 0.0029889 | 7.0274e-06 | 2.2756e-06 | 0.01817 | 0.01817 | 0.01817 | 0.97684 | -0.16204 | 0.97744 | -0.15778 | 6.7298
31 | -0.012601 | -0.0031555 | 0.012604 | 0.0031564 | 2.7122e-06 | 8.9507e-07 | 0.019182 | 0.019182 | 0.019182 | 0.97744 | -0.15778 | 0.97766 | -0.15622 | 7.1045
32 | -0.073797 | -0.018524 | 0.074103 | 0.018637 | 0.000306 | 0.00011329 | 0.11233 | 0.11233 | 0.11233 | 0.97766 | -0.15622 | 0.98184 | -0.12648 | 13.8681
33 | 0.061194 | 0.015367 | -0.061167 | -0.015357 | 2.7022e-05 | 9.83e-06 | 0.09315 | 0.09315 | 0.09315 | 0.97766 | -0.15622 | 0.97721 | -0.1594 | 11.5
34 | -0.074508 | -0.018738 | 0.074912 | 0.018888 | 0.00040481 | 0.00014987 | 0.11294 | 0.11294 | 0.11294 | 0.98184 | -0.12648 | 0.98734 | -0.087713 | 13.9436
35 | -0.076489 | -0.019283 | 0.077004 | 0.019474 | 0.00051431 | 0.00019063 | 0.11532 | 0.11531 | 0.11532 | 0.98734 | -0.087713 | 0.99419 | -0.040026 | 14.2367
36 | 0.0078693 | 0.0019719 | -0.0078691 | -0.0019719 | 2.5152e-07 | 6.2189e-08 | 0.012036 | 0.012036 | 0.012036 | 0.97289 | -0.19036 | 0.97286 | -0.1906 | 4.4577
37 | 0.004198 | 0.0010518 | -0.0041971 | -0.0010519 | 8.8459e-07 | -8.6623e-08 | 0.0064209 | 0.006421 | 0.006421 | 0.97286 | -0.1906 | 0.97265 | -0.19212 | 2.3782
38 | -0.088925 | -0.022514 | 0.088951 | 0.022524 | 2.6388e-05 | 9.8645e-06 | 0.13244 | 0.13244 | 0.13244 | 0.99969 | -0.0020995 | 1 | 0 | 16.3509
39 | 0.088123 | 0.022313 | -0.088052 | -0.022286 | 7.1017e-05 | 2.6535e-05 | 0.13125 | 0.13125 | 0.13125 | 0.99969 | -0.0020995 | 0.99886 | -0.0078065 | 16.2035
40 | 0.099297 | 0.025147 | -0.098727 | -0.024932 | 0.0005705 | 0.00021452 | 0.14785 | 0.14785 | 0.14785 | 1 | 0 | 0.99408 | -0.040872 | 18.253
41 | 0.081932 | 0.020752 | -0.08178 | -0.020696 | 0.00015193 | 5.6514e-05 | 0.12213 | 0.12213 | 0.12213 | 0.99886 | -0.0078065 | 0.99695 | -0.020942 | 15.0781
42 | 0.09789 | 0.024723 | -0.097785 | -0.024683 | 0.00010551 | 3.9665e-05 | 0.1466 | 0.1466 | 0.1466 | 0.99408 | -0.040872 | 0.99297 | -0.048547 | 18.0985
43 | 0.077211 | 0.019551 | -0.077004 | -0.019474 | 0.00020772 | 7.6963e-05 | 0.11531 | 0.11531 | 0.11531 | 0.99695 | -0.020942 | 0.99419 | -0.040026 | 14.2364
44 | 0.096989 | 0.024483 | -0.096987 | -0.024483 | 2.2285e-06 | 8.3746e-07 | 0.1454 | 0.1454 | 0.1454 | 0.99297 | -0.048547 | 0.99295 | -0.048711 | 17.9512
45 | 0.096508 | 0.024363 | -0.09643 | -0.024333 | 7.7544e-05 | 2.9134e-05 | 0.14469 | 0.14469 | 0.14469 | 0.99295 | -0.048711 | 0.99212 | -0.054436 | 17.8626
46 | 0.09579 | 0.024173 | -0.095735 | -0.024153 | 5.4612e-05 | 2.0512e-05 | 0.14373 | 0.14373 | 0.14373 | 0.99212 | -0.054436 | 0.99154 | -0.0585 | 17.7441
47 | 0.094916 | 0.023947 | -0.09476 | -0.023889 | 0.00015579 | 5.8493e-05 | 0.1425 | 0.1425 | 0.1425 | 0.99154 | -0.0585 | 0.98986 | -0.070217 | 17.5924
48 | -0.0027161 | -0.00067977 | 0.0027163 | 0.00067962 | 1.9041e-07 | -1.4397e-07 | 0.0041654 | 0.0041653 | 0.0041654 | 0.9702 | -0.21006 | 0.97027 | -0.20956 | 1.5427
49 | 0.00087036 | 0.00021719 | -0.00087027 | -0.00021811 | 8.5966e-08 | -9.2183e-07 | 0.0013345 | 0.0013349 | 0.0013349 | 0.9702 | -0.21006 | 0.9701 | -0.21078 | 0.4944
50 | -0.0044506 | -0.0011143 | 0.004452 | 0.0011142 | 1.3518e-06 | -5.4661e-08 | 0.0068251 | 0.0068249 | 0.0068251 | 0.97027 | -0.20956 | 0.97058 | -0.20736 | 2.5278
51 | -0.017241 | -0.0043176 | 0.017243 | 0.0043178 | 1.7683e-06 | 2.2888e-07 | 0.026431 | 0.026431 | 0.026431 | 0.97058 | -0.20736 | 0.97068 | -0.20661 | 3.2631
52 | 0.012789 | 0.0032033 | -0.012788 | -0.0032034 | 1.0798e-06 | -8.5355e-08 | 0.019606 | 0.019606 | 0.019606 | 0.97058 | -0.20736 | 0.97049 | -0.20797 | 2.4205
53 | -0.018915 | -0.0047368 | 0.018915 | 0.0047369 | 2.5731e-07 | 4.4394e-08 | 0.028994 | 0.028994 | 0.028994 | 0.97068 | -0.20661 | 0.97069 | -0.20652 | 3.5795
54 | 0.011503 | 0.0028815 | -0.011502 | -0.0028817 | 8.5804e-07 | -1.6154e-07 | 0.017637 | 0.017637 | 0.017637 | 0.97049 | -0.20797 | 0.97042 | -0.20851 | 2.1774
55 | -0.020163 | -0.0050498 | 0.020165 | 0.0050501 | 1.7849e-06 | 3.5334e-07 | 0.030908 | 0.030908 | 0.030908 | 0.97069 | -0.20652 | 0.97078 | -0.20588 | 3.8158
56 | 0.010174 | 0.0025488 | -0.010174 | -0.0025491 | 6.1338e-07 | -2.1312e-07 | 0.015601 | 0.015601 | 0.015601 | 0.97042 | -0.20851 | 0.97036 | -0.20894 | 1.9261
57 | -0.021421 | -0.0053648 | 0.021427 | 0.0053663 | 6.8672e-06 | 1.5048e-06 | 0.032832 | 0.032832 | 0.032832 | 0.97078 | -0.20588 | 0.9711 | -0.20356 | 4.0534
58 | 0.0084319 | 0.0021125 | -0.0084311 | -0.0021125 | 7.6543e-07 | -6.8118e-08 | 0.01293 | 0.01293 | 0.01293 | 0.97036 | -0.20894 | 0.97026 | -0.2096 | 2.3944
59 | -0.023942 | -0.0059966 | 0.023956 | 0.0060001 | 1.3746e-05 | 3.4632e-06 | 0.036686 | 0.036685 | 0.036686 | 0.9711 | -0.20356 | 0.97168 | -0.19941 | 4.5291
60 | -0.025117 | -0.0062911 | 0.025124 | 0.0062928 | 6.6676e-06 | 1.759e-06 | 0.038463 | 0.038463 | 0.038463 | 0.97168 | -0.19941 | 0.97194 | -0.19749 | 4.7485
61 | 0.0073198 | 0.001834 | -0.0073197 | -0.001834 | 1.7202e-07 | 3.9143e-08 | 0.011226 | 0.011226 | 0.011226 | 0.97026 | -0.2096 | 0.97024 | -0.20977 | 4.1577
62 | 0.0052486 | 0.0013149 | -0.0052482 | -0.0013149 | 3.9602e-07 | 3.1353e-08 | 0.0080493 | 0.0080493 | 0.0080493 | 0.97024 | -0.20977 | 0.97017 | -0.21031 | 2.9812
63 | 0.0040971 | 0.0010264 | -0.0040968 | -0.0010265 | 3.4257e-07 | -3.9901e-08 | 0.0062839 | 0.006284 | 0.006284 | 0.97017 | -0.21031 | 0.97008 | -0.21092 | 2.3274
64 | 0.002743 | 0.00068717 | -0.0027429 | -0.00068722 | 7.7419e-08 | -5.6751e-08 | 0.0042074 | 0.0042074 | 0.0042074 | 0.97008 | -0.21092 | 0.97005 | -0.21112 | 1.5583
65 | 0.0015873 | 0.0003976 | -0.0015872 | -0.0003978 | 6.568e-08 | -1.9392e-07 | 0.0024348 | 0.0024348 | 0.0024348 | 0.97005 | -0.21112 | 0.97001 | -0.21142 | 0.90179
66 | 0.046662 | 0.0117 | -0.046639 | -0.011692 | 2.302e-05 | 8.0392e-06 | 0.071246 | 0.071246 | 0.071246 | 0.9746 | -0.17839 | 0.9741 | -0.18195 | 8.7958
67 | -0.04852 | -0.012166 | 0.048531 | 0.012169 | 1.0576e-05 | 3.7214e-06 | 0.074083 | 0.074083 | 0.074083 | 0.9746 | -0.17839 | 0.97482 | -0.17682 | 9.1461
68 | 0.045639 | 0.011441 | -0.045637 | -0.011441 | 2.291e-06 | 7.9652e-07 | 0.069719 | 0.069719 | 0.069719 | 0.9741 | -0.18195 | 0.97405 | -0.18231 | 8.6073
69 | -0.050153 | -0.012576 | 0.050154 | 0.012576 | 1.0585e-06 | 3.7465e-07 | 0.076559 | 0.076559 | 0.076559 | 0.97482 | -0.17682 | 0.97484 | -0.17666 | 9.4518
70 | 0.043925 | 0.011012 | -0.04391 | -0.011006 | 1.4808e-05 | 5.1052e-06 | 0.067104 | 0.067104 | 0.067104 | 0.97405 | -0.18231 | 0.97371 | -0.18475 | 8.2844
71 | -0.051521 | -0.012919 | 0.051537 | 0.012925 | 1.637e-05 | 5.8199e-06 | 0.078645 | 0.078645 | 0.078645 | 0.97484 | -0.17666 | 0.97516 | -0.17437 | 9.7093
72 | 0.041855 | 0.010491 | -0.041837 | -0.010485 | 1.8556e-05 | 6.3237e-06 | 0.063963 | 0.063964 | 0.063964 | 0.97371 | -0.18475 | 0.97327 | -0.18795 | 7.8967
73 | -0.053221 | -0.013347 | 0.053245 | 0.013355 | 2.4043e-05 | 8.5911e-06 | 0.081214 | 0.081214 | 0.081214 | 0.97516 | -0.17437 | 0.97561 | -0.17111 | 10.0264
74 | 0.040174 | 0.010068 | -0.040162 | -0.010064 | 1.2303e-05 | 4.1477e-06 | 0.061422 | 0.061422 | 0.061422 | 0.97327 | -0.18795 | 0.97296 | -0.19016 | 7.583
75 | -0.055171 | -0.013838 | 0.055205 | 0.01385 | 3.3941e-05 | 1.219e-05 | 0.084151 | 0.084151 | 0.084151 | 0.97561 | -0.17111 | 0.97623 | -0.16668 | 10.389
76 | 0.038864 | 0.0097389 | -0.038856 | -0.0097363 | 7.8156e-06 | 2.6098e-06 | 0.059437 | 0.059437 | 0.059437 | 0.97296 | -0.19016 | 0.97276 | -0.19162 | 7.3379
77 | 0.037182 | 0.0093169 | -0.037173 | -0.0093139 | 9.1858e-06 | 3.0247e-06 | 0.056877 | 0.056877 | 0.056877 | 0.97276 | -0.19162 | 0.97251 | -0.1934 | 7.0218
78 | 0.035385 | 0.0088658 | -0.035376 | -0.0088629 | 9.0004e-06 | 2.9124e-06 | 0.054141 | 0.054142 | 0.054142 | 0.97251 | -0.1934 | 0.97225 | -0.19524 | 6.6842
79 | 0.033368 | 0.0083595 | -0.033367 | -0.0083591 | 1.1364e-06 | 3.5913e-07 | 0.051067 | 0.051068 | 0.051068 | 0.97225 | -0.19524 | 0.97222 | -0.19549 | 6.3046
80 | 0.004229 | 0.0010585 | -0.0042286 | -0.0010585 | 3.6806e-07 | -3.5937e-08 | 0.0064455 | 0.0064455 | 0.0064455 | 0.97623 | -0.16668 | 0.97614 | -0.16731 | 2.3872
81 | -0.059434 | -0.014909 | 0.05949 | 0.014929 | 5.6585e-05 | 2.0519e-05 | 0.090596 | 0.090596 | 0.090596 | 0.97623 | -0.16668 | 0.97719 | -0.15982 | 11.1847
82 | 0.0027529 | 0.00068866 | -0.0027528 | -0.0006887 | 5.3368e-08 | -4.0198e-08 | 0.004196 | 0.004196 | 0.004196 | 0.97614 | -0.16731 | 0.97612 | -0.16745 | 1.5541
83 | -0.061185 | -0.015354 | 0.06119 | 0.015356 | 4.6352e-06 | 1.6863e-06 | 0.093177 | 0.093177 | 0.093177 | 0.97719 | -0.15982 | 0.97727 | -0.15927 | 11.5033
84 | 0.00086729 | 0.00021615 | -0.00086719 | -0.00021721 | 9.6009e-08 | -1.0637e-06 | 0.0013217 | 0.0013221 | 0.0013221 | 0.97612 | -0.16745 | 0.97601 | -0.16825 | 0.48965
85 | -0.062036 | -0.015568 | 0.062044 | 0.015571 | 8.2824e-06 | 3.0178e-06 | 0.094465 | 0.094465 | 0.094465 | 0.97727 | -0.15927 | 0.9774 | -0.15831 | 11.6623
86 | 0.00086719 | 0.00021721 | -0.00086718 | -0.00021734 | 1.1287e-08 | -1.2498e-07 | 0.0013221 | 0.0013221 | 0.0013221 | 0.97601 | -0.16825 | 0.976 | -0.16835 | 0.48967
87 | -0.063819 | -0.016015 | 0.06385 | 0.016027 | 3.156e-05 | 1.1534e-05 | 0.097166 | 0.097166 | 0.097166 | 0.9774 | -0.15831 | 0.9779 | -0.15475 | 11.9959
88 | -0.064726 | -0.016246 | 0.064768 | 0.016262 | 4.1564e-05 | 1.521e-05 | 0.098499 | 0.098499 | 0.098499 | 0.9779 | -0.15475 | 0.97855 | -0.15013 | 12.1604
89 | -0.065575 | -0.016464 | 0.065593 | 0.016471 | 1.7999e-05 | 6.5945e-06 | 0.099727 | 0.099727 | 0.099727 | 0.97855 | -0.15013 | 0.97882 | -0.14815 | 12.3119
90 | -0.066507 | -0.0167 | 0.066517 | 0.016703 | 1.0194e-05 | 3.74e-06 | 0.10112 | 0.10112 | 0.10112 | 0.97882 | -0.14815 | 0.97898 | -0.14705 | 12.4834
91 | -0.06826 | -0.01714 | 0.068262 | 0.017141 | 2.4423e-06 | 8.9821e-07 | 0.10376 | 0.10376 | 0.10376 | 0.97898 | -0.14705 | 0.97901 | -0.14679 | 12.8104
92 | -0.069287 | -0.017398 | 0.069336 | 0.017416 | 4.8571e-05 | 1.7887e-05 | 0.10532 | 0.10532 | 0.10532 | 0.97901 | -0.14679 | 0.97972 | -0.14175 | 13.0028
93 | -0.07048 | -0.017703 | 0.070506 | 0.017712 | 2.6297e-05 | 9.6975e-06 | 0.10706 | 0.10706 | 0.10706 | 0.97972 | -0.14175 | 0.9801 | -0.13907 | 13.2173
94 | -0.073229 | -0.018395 | 0.073258 | 0.018405 | 2.8306e-05 | 1.0471e-05 | 0.11119 | 0.11119 | 0.11119 | 0.9801 | -0.13907 | 0.98049 | -0.13629 | 13.7277
95 | -0.074735 | -0.018775 | 0.074795 | 0.018798 | 6.0898e-05 | 2.2561e-05 | 0.11344 | 0.11343 | 0.11344 | 0.98049 | -0.13629 | 0.98131 | -0.13044 | 14.0043
96 | 0.093732 | 0.023631 | -0.093552 | -0.023563 | 0.00018013 | 6.7604e-05 | 0.14095 | 0.14095 | 0.14095 | 0.98986 | -0.070217 | 0.9879 | -0.083962 | 17.4016
97 | 0.090319 | 0.022753 | -0.09011 | -0.022675 | 0.00020823 | 7.8015e-05 | 0.13608 | 0.13608 | 0.13608 | 0.9879 | -0.083962 | 0.98555 | -0.10048 | 16.8005
98 | 0.0016059 | 0.00040198 | -0.0016057 | -0.00040244 | 1.4931e-07 | -4.5841e-07 | 0.0024277 | 0.0024279 | 0.0024279 | 0.98422 | -0.10998 | 0.98412 | -0.11065 | 0.89923
99 | -0.0040883 | -0.0010241 | 0.0040937 | 0.0010233 | 5.3632e-06 | -8.0069e-07 | 0.0061809 | 0.0061799 | 0.0061809 | 0.98422 | -0.10998 | 0.98555 | -0.10048 | 2.2892
100 | 0.084796 | 0.021346 | -0.084603 | -0.021274 | 0.00019323 | 7.2157e-05 | 0.12806 | 0.12806 | 0.12806 | 0.98555 | -0.10048 | 0.98323 | -0.11683 | 15.8101
101 | 0.08065 | 0.020284 | -0.080565 | -0.020252 | 8.5051e-05 | 3.1669e-05 | 0.12208 | 0.12208 | 0.12208 | 0.98323 | -0.11683 | 0.98216 | -0.12441 | 15.0717
102 | 0.0039525 | 0.00099014 | -0.0039518 | -0.00099027 | 7.0152e-07 | -1.2863e-07 | 0.0059815 | 0.0059817 | 0.0059817 | 0.98323 | -0.11683 | 0.98305 | -0.11812 | 2.2154
103 | 0.078362 | 0.0197 | -0.078318 | -0.019683 | 4.324e-05 | 1.6071e-05 | 0.11874 | 0.11874 | 0.11874 | 0.98216 | -0.12441 | 0.98161 | -0.12837 | 14.6596
104 | 0.0017755 | 0.00044484 | -0.0017755 | -0.00044498 | 5.6079e-08 | -1.3617e-07 | 0.0026875 | 0.0026876 | 0.0026876 | 0.98305 | -0.11812 | 0.98302 | -0.11835 | 0.9954
105 | -0.027475 | -0.0068822 | 0.027477 | 0.0068825 | 1.2074e-06 | 3.4239e-07 | 0.042063 | 0.042063 | 0.042063 | 0.97194 | -0.19749 | 0.97199 | -0.19717 | 5.1929
106 | -0.029493 | -0.0073879 | 0.029494 | 0.0073881 | 8.4731e-07 | 2.5158e-07 | 0.04515 | 0.04515 | 0.04515 | 0.97199 | -0.19717 | 0.97202 | -0.19696 | 5.574
107 | 0.031847 | 0.0079782 | -0.03184 | -0.0079762 | 6.495e-06 | 2.0092e-06 | 0.048742 | 0.048742 | 0.048742 | 0.97222 | -0.19549 | 0.97202 | -0.19696 | 6.0175
108 | -0.076239 | -0.01916 | 0.076261 | 0.019168 | 2.1951e-05 | 8.1435e-06 | 0.11562 | 0.11562 | 0.11562 | 0.98131 | -0.13044 | 0.98161 | -0.12837 | 14.2745

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18948 | 0.047777

## res_load
| p_mw | q_mvar
0 | 0.0035699 | 0.0008947
1 | 0.003191 | 0.00079974
2 | 0.0021958 | 0.00055032
3 | 0.0041491 | 0.0010399
4 | 0.001236 | 0.00030976
5 | 0.0025258 | 0.00063304
6 | 0.0015737 | 0.0003944
7 | 0.0053144 | 0.0013319
8 | 0.0037802 | 0.00094742
9 | 0.0012167 | 0.00030493
10 | 0.0052098 | 0.0013057
11 | 0.0037332 | 0.00093564
12 | 0.0026946 | 0.00067532
13 | 0.0037042 | 0.00092836
14 | 0.0040595 | 0.0010174
15 | 0.00075795 | 0.00018996
16 | 0.00069067 | 0.0001731
17 | 0.0040782 | 0.0010221
18 | 0.00055617 | 0.00013939
19 | 0.0010557 | 0.00026459
20 | 0.00051501 | 0.00012907
21 | 0.0006297 | 0.00015782
22 | 0.00057717 | 0.00014465
23 | 0.00064748 | 0.00016227
24 | 0.00066547 | 0.00016678
25 | 0.00061652 | 0.00015451
26 | 0.00066998 | 0.00016791
27 | 0.00066466 | 0.00016658
28 | 0.00040429 | 0.00010132
29 | 0.0029762 | 0.0007459
30 | 0.0015769 | 0.0003952
31 | 0.0019206 | 0.00048136
32 | 0.0036711 | 0.00092006
33 | 0.0041971 | 0.0010519
34 | 0.00080223 | 0.00020106
35 | 0.00042648 | 0.00010689
36 | 0.0061195 | 0.0015337
37 | 0.00083666 | 0.00020969
38 | 0.0045689 | 0.0011451
39 | 0.00079576 | 0.00019944
40 | 0.00047906 | 0.00012006
41 | 0.00064013 | 0.00016043
42 | 0.00081937 | 0.00020535
43 | 0.0018457 | 0.00046258
44 | 0.0017344 | 0.00043467
45 | 0.00087027 | 0.00021811
46 | 0.001672 | 0.00041905
47 | 0.0012844 | 0.0003219
48 | 0.0012484 | 0.00031287
49 | 0.001328 | 0.00033283
50 | 0.0012557 | 0.0003147
51 | 0.0017419 | 0.00043657
52 | 0.002515 | 0.00063031
53 | 0.0011611 | 0.00029099
54 | 0.0011113 | 0.00027851
55 | 0.0020711 | 0.00051907
56 | 0.0011511 | 0.00028848
57 | 0.0013538 | 0.00033929
58 | 0.0011556 | 0.00028962
59 | 0.0015872 | 0.0003978
60 | 0.0018585 | 0.00046579
61 | 0.00099962 | 0.00025053
62 | 0.0016223 | 0.00040659
63 | 0.0017119 | 0.00042904
64 | 0.0013663 | 0.00034244
65 | 0.002055 | 0.00051504
66 | 0.0016838 | 0.00042201
67 | 0.0016623 | 0.00041661
68 | 0.0019256 | 0.0004826
69 | 0.0012985 | 0.00032542
70 | 0.0016735 | 0.00041942
71 | 0.0017878 | 0.00044807
72 | 0.0020086 | 0.00050341
73 | 0.0014757 | 0.00036986
74 | 0.0016951 | 0.00042482
75 | 0.0018855 | 0.00047255
76 | 0.00084578 | 0.00021197
77 | 0.0017748 | 0.0004448
78 | 0.00086718 | 0.00021734
79 | 0.00087575 | 0.00021948
80 | 0.00080769 | 0.00020243
81 | 0.00091366 | 0.00022899
82 | 0.0017426 | 0.00043675
83 | 0.0010252 | 0.00025694
84 | 0.0011441 | 0.00028674
85 | 0.0027231 | 0.00068248
86 | 0.0014768 | 0.00037012
87 | 0.0010284 | 0.00025775
88 | 0.0032328 | 0.00081022
89 | 0.0024824 | 0.00062216
90 | 0.0016057 | 0.00040244
91 | 0.0012207 | 0.00030593
92 | 0.00045463 | 0.00011394
93 | 0.0022038 | 0.00055232
94 | 0.0021763 | 0.00054542
95 | 0.0023515 | 0.00058934
96 | 0.0020165 | 0.00050538
97 | 0.0015197 | 0.00038087
98 | 0.0014434 | 0.00036175
99 | 0.0020575 | 0.00051566
100 | 0.0017755 | 0.00044498
101 | 0.0023465 | 0.00058808

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1