## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1370-11_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1370-11_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1370-11_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1370-11_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1370-11_0_2_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_1370-11_0_2_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1370-11_0_2_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1370-11_0_2_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_1370-11_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1370-11_0_2_node_74 | 0.4 | n |  | TRUE
10 | bus_LV_1370-11_0_2_node_73 | 0.4 | n |  | TRUE
11 | bus_LV_1370-11_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1370-11_0_2_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_1370-11_0_2_node_37 | 0.4 | n |  | TRUE
14 | bus_LV_1370-11_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1370-11_0_2_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1370-11_0_2_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1370-11_0_2_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1370-11_0_2_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_1370-11_0_2_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_1370-11_0_2_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1370-11_0_2_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1370-11_0_2_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_1370-11_0_2_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_1370-11_0_2_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_1370-11_0_2_node_43 | 0.4 | n |  | TRUE
26 | bus_LV_1370-11_0_2_node_71 | 0.4 | n |  | TRUE
27 | bus_LV_1370-11_0_2_node_70 | 0.4 | n |  | TRUE
28 | bus_LV_1370-11_0_2_node_81 | 0.4 | n |  | TRUE
29 | bus_MV_22_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1370-11_0_2_load_0 | 0 | 0.0019371 | 0.00048548 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1370-11_0_2_load_13 | 4 | 0.0037391 | 0.00093711 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1370-11_0_2_load_12 | 5 | 0.0063078 | 0.0015809 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1370-11_0_2_load_36 | 7 | 0.013932 | 0.0034916 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1370-11_0_2_load_73 | 10 | 0.0033615 | 0.00084247 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1370-11_0_2_load_40 | 12 | 0.007036 | 0.0017634 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1370-11_0_2_load_37 | 13 | 0.0095894 | 0.0024033 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1370-11_0_2_load_8 | 14 | 0.0037966 | 0.00095152 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1370-11_0_2_load_10 | 16 | 0.0010094 | 0.00025298 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1370-11_0_2_load_11 | 17 | 0.0011067 | 0.00027736 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1370-11_0_2_load_42 | 18 | 0.001298 | 0.00032531 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1370-11_0_2_load_63 | 19 | 0.00024315 | 6.094e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1370-11_0_2_load_14 | 20 | 0.00078792 | 0.00019747 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1370-11_0_2_load_15 | 21 | 0.012659 | 0.0031726 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1370-11_0_2_load_38 | 22 | 0.0011801 | 0.00029576 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1370-11_0_2_load_39 | 23 | 0.010663 | 0.0026725 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1370-11_0_2_load_44 | 24 | 0.0073286 | 0.0018367 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1370-11_0_2_load_43 | 25 | 0.0098117 | 0.002459 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1370-11_0_2_load_71 | 26 | 0.0046286 | 0.00116 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1370-11_0_2_load_70 | 27 | 0.0012849 | 0.00032204 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1370-11_0_2_load_81 | 28 | 0.0051512 | 0.001291 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1370-11_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.016502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1370-11_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.01225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1370-11_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.065474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1370-11_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.028155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1370-11_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.065524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1370-11_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.010364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1370-11_0_2_line_6 | NAYY 4x150 SE | 3 | 7 | 0.0036429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1370-11_0_2_line_7 | NAYY 4x150 SE | 4 | 20 | 0.025817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1370-11_0_2_line_8 | NAYY 4x150 SE | 6 | 10 | 0.027425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1370-11_0_2_line_9 | NAYY 4x150 SE | 6 | 11 | 0.010519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1370-11_0_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.040674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1370-11_0_2_line_11 | NAYY 4x150 SE | 8 | 10 | 0.064603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1370-11_0_2_line_12 | NAYY 4x150 SE | 9 | 28 | 0.071726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1370-11_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.02026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1370-11_0_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.03971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1370-11_0_2_line_15 | NAYY 4x150 SE | 12 | 24 | 0.037872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1370-11_0_2_line_16 | NAYY 4x150 SE | 13 | 22 | 0.030123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1370-11_0_2_line_17 | NAYY 4x150 SE | 14 | 15 | 0.072471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1370-11_0_2_line_18 | NAYY 4x150 SE | 15 | 16 | 0.069552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1370-11_0_2_line_19 | NAYY 4x150 SE | 15 | 17 | 0.013813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1370-11_0_2_line_20 | NAYY 4x150 SE | 16 | 18 | 0.016806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1370-11_0_2_line_21 | NAYY 4x150 SE | 17 | 19 | 0.0040597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1370-11_0_2_line_22 | NAYY 4x150 SE | 18 | 25 | 0.0077828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1370-11_0_2_line_23 | NAYY 4x150 SE | 19 | 26 | 0.069825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1370-11_0_2_line_24 | NAYY 4x150 SE | 20 | 21 | 0.014986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1370-11_0_2_line_25 | NAYY 4x150 SE | 22 | 23 | 0.0015555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1370-11_0_2_line_26 | NAYY 4x150 SE | 24 | 25 | 0.0077871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1370-11_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.0776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1370-11_0_2_trafo_37 | 0.25 MVA 20/0.4 kV | 29 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2693770.1247 | 1217462.304 | 2693771.7758 | 1217478.7229
1 | 2693758.2964 | 1217459.8718 | 2693760.2243 | 1217460.8695 | 2693764.72 | 1217462.2412 | 2693767.5645 | 1217462.4083 | 2693770.1247 | 1217462.304
2 | 2693813.7598 | 1217499.2496 | 2693811.4105 | 1217492.23 | 2693809.7911 | 1217489.4804 | 2693807.4731 | 1217485.7746 | 2693803.8888 | 1217479.5584 | 2693801.2346 | 1217474.5465 | 2693798.8156 | 1217469.5383 | 2693796.9665 | 1217466.4293 | 2693794.2732 | 1217463.8962 | 2693791.9216 | 1217462.3248 | 2693789.6785 | 1217461.5779 | 2693786.832 | 1217461.055 | 2693784.4582 | 1217460.8953 | 2693780.773 | 1217461.0819 | 2693776.8491 | 1217461.4871 | 2693774.9771 | 1217461.7578 | 2693771.6062 | 1217462.2384 | 2693770.1247 | 1217462.304
3 | 2693758.2964 | 1217459.8718 | 2693756.6922 | 1217459.046 | 2693753.0669 | 1217455.4309 | 2693751.3372 | 1217451.968 | 2693749.6093 | 1217448.3939 | 2693748.838 | 1217444.8238 | 2693748.4195 | 1217441.0257 | 2693748.3482 | 1217437.8335 | 2693748.3911 | 1217435.11 | 2693748.3911 | 1217435.11
4 | 2693758.2964 | 1217459.8718 | 2693755.827 | 1217462.4014 | 2693709.8684 | 1217474.1756 | 2693695.8812 | 1217478.1688
5 | 2693823.7418 | 1217496.4603 | 2693819.5859 | 1217497.6179 | 2693813.7598 | 1217499.2496
6 | 2693813.7598 | 1217499.2496 | 2693815.0743 | 1217502.6471
7 | 2693748.3911 | 1217435.11 | 2693750.1608 | 1217409.354
8 | 2693823.7418 | 1217496.4603 | 2693825.6198 | 1217502.0715 | 2693831.167 | 1217522.8521
9 | 2693823.7418 | 1217496.4603 | 2693820.1395 | 1217486.5746
10 | 2693883.9765 | 1217577.4759 | 2693844.1184 | 1217586.132
11 | 2693844.1184 | 1217586.132 | 2693842.4329 | 1217577.4661 | 2693832.7315 | 1217528.713 | 2693831.167 | 1217522.8521
12 | 2693883.9765 | 1217577.4759 | 2693881.4401 | 1217560.6577 | 2693874.5337 | 1217539.312 | 2693872.0432 | 1217528.7321 | 2693867.9999 | 1217507.704
13 | 2693820.1395 | 1217486.5746 | 2693839.2931 | 1217479.9713
14 | 2693820.1395 | 1217486.5746 | 2693817.4906 | 1217479.2945 | 2693804.3605 | 1217450.1532
15 | 2693839.2931 | 1217479.9713 | 2693842.3457 | 1217478.9189 | 2693853.6722 | 1217478.5081 | 2693874.6207 | 1217468.2865 | 2693874.6207 | 1217468.2865
16 | 2693804.3605 | 1217450.1532 | 2693797.4346 | 1217434.7814 | 2693792.4246 | 1217422.5011
17 | 2693941.4408 | 1217396.0117 | 2693953.2857 | 1217390.1832 | 2693960.9264 | 1217382.2982 | 2693966.1939 | 1217372.7747 | 2693971.7239 | 1217357.6848 | 2693974.5878 | 1217341.2186 | 2693970.3552 | 1217339.3614
18 | 2693941.4408 | 1217396.0117 | 2693924.0102 | 1217404.5984 | 2693910.7569 | 1217413.0843 | 2693903.9788 | 1217421.639 | 2693895.4673 | 1217439.9731 | 2693894.0697 | 1217442.9133
19 | 2693941.4408 | 1217396.0117 | 2693947.3345 | 1217408.5047
20 | 2693885.4971 | 1217457.1453 | 2693889.0203 | 1217453.5365 | 2693894.0697 | 1217442.9133
21 | 2693949.0667 | 1217412.1764 | 2693947.3345 | 1217408.5047
22 | 2693885.4971 | 1217457.1453 | 2693880.0604 | 1217462.7144
23 | 2693949.0667 | 1217412.1764 | 2693969.8176 | 1217478.8465
24 | 2693751.188 | 1217394.4037 | 2693750.1608 | 1217409.354
25 | 2693791.8371 | 1217421.0608 | 2693792.4246 | 1217422.5011
26 | 2693874.6207 | 1217468.2865 | 2693880.0604 | 1217462.7144
27 | 2693867.9999 | 1217507.704 | 2693945.1746 | 1217515.8138

## bus_geodata
| x | y | coords
0 | 2693771.7757 | 1217478.7229
1 | 2693770.1247 | 1217462.304
2 | 2693758.2964 | 1217459.8718
3 | 2693813.7598 | 1217499.2496
4 | 2693748.3911 | 1217435.11
5 | 2693695.8812 | 1217478.1688
6 | 2693823.7418 | 1217496.4603
7 | 2693815.0743 | 1217502.6471
8 | 2693844.1184 | 1217586.132
9 | 2693883.9765 | 1217577.4759
10 | 2693831.167 | 1217522.8521
11 | 2693820.1395 | 1217486.5746
12 | 2693839.2931 | 1217479.9713
13 | 2693804.3605 | 1217450.1532
14 | 2693970.3552 | 1217339.3614
15 | 2693941.4408 | 1217396.0117
16 | 2693894.0697 | 1217442.9133
17 | 2693947.3345 | 1217408.5047
18 | 2693885.4971 | 1217457.1453
19 | 2693949.0667 | 1217412.1764
20 | 2693750.1608 | 1217409.354
21 | 2693751.188 | 1217394.4037
22 | 2693792.4246 | 1217422.5011
23 | 2693791.8371 | 1217421.0608
24 | 2693874.6207 | 1217468.2865
25 | 2693880.0604 | 1217462.7144
26 | 2693969.8176 | 1217478.8465
27 | 2693945.1746 | 1217515.8138
28 | 2693867.9999 | 1217507.704
29 | 2693820.1395 | 1217486.5746

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99135 | -0.060599 | 0.0019371 | 0.00048548
1 | 0.9914 | -0.060275 | 0 | 0
2 | 0.99098 | -0.0632 | 0 | 0
3 | 0.9938 | -0.043396 | 0 | 0
4 | 0.99029 | -0.068122 | 0.0037391 | 0.00093711
5 | 0.99039 | -0.067405 | 0.0063078 | 0.0015809
6 | 0.99438 | -0.039273 | 0 | 0
7 | 0.99372 | -0.043909 | 0.013932 | 0.0034916
8 | 0.9934 | -0.04621 | 0 | 0
9 | 0.99302 | -0.048865 | 0 | 0
10 | 0.994 | -0.041993 | 0.0033615 | 0.00084247
11 | 0.99513 | -0.034052 | 0 | 0
12 | 0.99407 | -0.04147 | 0.007036 | 0.0017634
13 | 1 | 0 | -0.098749 | -0.024629
14 | 0.99046 | -0.066921 | 0.0037966 | 0.00095152
15 | 0.99086 | -0.06412 | 0 | 0
16 | 0.99184 | -0.057203 | 0.0010094 | 0.00025298
17 | 0.99074 | -0.064961 | 0.0011067 | 0.00027736
18 | 0.9921 | -0.05536 | 0.001298 | 0.00032531
19 | 0.99071 | -0.065162 | 0.00024315 | 6.094e-05
20 | 0.98979 | -0.071658 | 0.00078792 | 0.00019747
21 | 0.98951 | -0.073591 | 0.012659 | 0.0031726
22 | 0.99949 | -0.0035629 | 0.0011801 | 0.00029576
23 | 0.99947 | -0.0037286 | 0.010663 | 0.0026725
24 | 0.99248 | -0.052675 | 0.0073286 | 0.0018367
25 | 0.99223 | -0.054405 | 0.0098117 | 0.002459
26 | 0.99025 | -0.068452 | 0.0046286 | 0.00116
27 | 0.99222 | -0.054562 | 0.0012849 | 0.00032204
28 | 0.99236 | -0.053549 | 0.0051512 | 0.001291
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0019371 | -0.00048548 | 0.0019372 | 0.0004853 | 8.7047e-08 | -1.7929e-07 | 0.0029075 | 0.0029075 | 0.0029075 | 0.99135 | -0.060599 | 0.9914 | -0.060275 | 1.0769
1 | 0.023528 | 0.0058996 | -0.023519 | -0.0058961 | 9.5335e-06 | 3.5088e-06 | 0.035315 | 0.035315 | 0.035315 | 0.9914 | -0.060275 | 0.99098 | -0.0632 | 13.0798
2 | -0.025466 | -0.0063849 | 0.025525 | 0.006407 | 5.9689e-05 | 2.2111e-05 | 0.038223 | 0.038223 | 0.038223 | 0.9914 | -0.060275 | 0.9938 | -0.043396 | 14.1566
3 | 0.017207 | 0.0043146 | -0.017196 | -0.0043105 | 1.173e-05 | 4.1489e-06 | 0.025839 | 0.025839 | 0.025839 | 0.99098 | -0.0632 | 0.99029 | -0.068122 | 9.5699
4 | 0.0063115 | 0.0015815 | -0.0063078 | -0.0015809 | 3.6722e-06 | 5.6871e-07 | 0.0094769 | 0.0094772 | 0.0094772 | 0.99098 | -0.0632 | 0.99039 | -0.067405 | 3.5101
5 | -0.039458 | -0.0098989 | 0.039481 | 0.0099075 | 2.2577e-05 | 8.5492e-06 | 0.059084 | 0.059084 | 0.059084 | 0.9938 | -0.043396 | 0.99438 | -0.039273 | 21.883
6 | 0.013933 | 0.0034919 | -0.013932 | -0.0034916 | 9.8929e-07 | 3.333e-07 | 0.020861 | 0.020861 | 0.020861 | 0.9938 | -0.043396 | 0.99372 | -0.043909 | 7.7265
7 | 0.013457 | 0.0033733 | -0.01345 | -0.0033711 | 6.5866e-06 | 2.2013e-06 | 0.02022 | 0.02022 | 0.02022 | 0.99029 | -0.068122 | 0.98979 | -0.071658 | 7.489
8 | 0.0098118 | 0.0024573 | -0.0098081 | -0.0024563 | 3.689e-06 | 1.0632e-06 | 0.014682 | 0.014682 | 0.014682 | 0.99438 | -0.039273 | 0.994 | -0.041993 | 5.4378
9 | -0.049292 | -0.012365 | 0.049328 | 0.012378 | 3.5717e-05 | 1.3601e-05 | 0.073766 | 0.073766 | 0.073766 | 0.99438 | -0.039273 | 0.99513 | -0.034052 | 27.3207
10 | 0.0064429 | 0.0016132 | -0.0064405 | -0.0016128 | 2.3637e-06 | 3.8271e-07 | 0.0096503 | 0.0096504 | 0.0096504 | 0.9934 | -0.04621 | 0.99302 | -0.048865 | 3.5742
11 | -0.0064429 | -0.0016132 | 0.0064466 | 0.0016138 | 3.7541e-06 | 6.0698e-07 | 0.0096503 | 0.00965 | 0.0096503 | 0.9934 | -0.04621 | 0.994 | -0.041993 | 3.5742
12 | 0.0064405 | 0.0016128 | -0.0064363 | -0.0016121 | 4.1684e-06 | 6.7594e-07 | 0.0096504 | 0.0096508 | 0.0096508 | 0.99302 | -0.048865 | 0.99236 | -0.053549 | 3.5744
13 | 0.036365 | 0.009124 | -0.036327 | -0.0091099 | 3.7385e-05 | 1.4116e-05 | 0.05438 | 0.05438 | 0.05438 | 0.99513 | -0.034052 | 0.99407 | -0.04147 | 20.1408
14 | -0.085693 | -0.021502 | 0.0861 | 0.021658 | 0.0004069 | 0.00015598 | 0.12815 | 0.12815 | 0.12815 | 0.99513 | -0.034052 | 1 | 0 | 47.4615
15 | 0.029291 | 0.0073465 | -0.029246 | -0.0073295 | 4.5437e-05 | 1.6985e-05 | 0.043848 | 0.043848 | 0.043848 | 0.99407 | -0.04147 | 0.99248 | -0.052675 | 16.2401
16 | 0.011849 | 0.0029702 | -0.011844 | -0.0029683 | 5.844e-06 | 1.8527e-06 | 0.017632 | 0.017633 | 0.017633 | 1 | 0 | 0.99949 | -0.0035629 | 6.5306
17 | -0.0037966 | -0.00095152 | 0.0037981 | 0.00095115 | 1.4711e-06 | -3.6727e-07 | 0.0057038 | 0.0057035 | 0.0057038 | 0.99046 | -0.066921 | 0.99086 | -0.06412 | 2.1125
18 | -0.0097794 | -0.0024495 | 0.0097888 | 0.0024522 | 9.3598e-06 | 2.7032e-06 | 0.014686 | 0.014685 | 0.014686 | 0.99086 | -0.06412 | 0.99184 | -0.057203 | 5.4391
19 | 0.0059813 | 0.0014983 | -0.0059806 | -0.0014982 | 6.9543e-07 | 8.9568e-08 | 0.0089822 | 0.0089822 | 0.0089822 | 0.99086 | -0.06412 | 0.99074 | -0.064961 | 3.3268
20 | -0.010798 | -0.0027052 | 0.010801 | 0.002706 | 2.752e-06 | 8.4151e-07 | 0.0162 | 0.0162 | 0.0162 | 0.99184 | -0.057203 | 0.9921 | -0.05536 | 5.9999
21 | 0.004874 | 0.0012209 | -0.0048738 | -0.0012209 | 1.3574e-07 | -6.9067e-11 | 0.0073201 | 0.0073201 | 0.0073201 | 0.99074 | -0.064961 | 0.99071 | -0.065162 | 2.7111
22 | -0.012099 | -0.0030313 | 0.012101 | 0.0030318 | 1.5992e-06 | 5.1457e-07 | 0.018146 | 0.018146 | 0.018146 | 0.9921 | -0.05536 | 0.99223 | -0.054405 | 6.7209
23 | 0.0046307 | 0.0011599 | -0.0046286 | -0.00116 | 2.1076e-06 | -8.8065e-08 | 0.0069549 | 0.0069552 | 0.0069552 | 0.99071 | -0.065162 | 0.99025 | -0.068452 | 2.576
24 | 0.012662 | 0.0031737 | -0.012659 | -0.0031726 | 3.3885e-06 | 1.1107e-06 | 0.019036 | 0.019036 | 0.019036 | 0.98979 | -0.071658 | 0.98951 | -0.073591 | 7.0503
25 | 0.010664 | 0.0026725 | -0.010663 | -0.0026725 | 2.4464e-07 | 7.3705e-08 | 0.015876 | 0.015876 | 0.015876 | 0.99949 | -0.0035629 | 0.99947 | -0.0037286 | 5.8799
26 | 0.021917 | 0.0054928 | -0.021912 | -0.0054909 | 5.247e-06 | 1.9175e-06 | 0.032861 | 0.032861 | 0.032861 | 0.99248 | -0.052675 | 0.99223 | -0.054405 | 12.1706
27 | -0.0012849 | -0.00032204 | 0.0012851 | 0.00032111 | 1.7978e-07 | -9.3327e-07 | 0.001927 | 0.0019267 | 0.001927 | 0.99222 | -0.054562 | 0.99236 | -0.053549 | 0.71371

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10834 | 0.027032

## res_load
| p_mw | q_mvar
0 | 0.0019371 | 0.00048548
1 | 0.0037391 | 0.00093711
2 | 0.0063078 | 0.0015809
3 | 0.013932 | 0.0034916
4 | 0.0033615 | 0.00084247
5 | 0.007036 | 0.0017634
6 | 0.0095894 | 0.0024033
7 | 0.0037966 | 0.00095152
8 | 0.0010094 | 0.00025298
9 | 0.0011067 | 0.00027736
10 | 0.001298 | 0.00032531
11 | 0.00024315 | 6.094e-05
12 | 0.00078792 | 0.00019747
13 | 0.012659 | 0.0031726
14 | 0.0011801 | 0.00029576
15 | 0.010663 | 0.0026725
16 | 0.0073286 | 0.0018367
17 | 0.0098117 | 0.002459
18 | 0.0046286 | 0.00116
19 | 0.0012849 | 0.00032204
20 | 0.0051512 | 0.001291

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1