## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1370-12_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1370-12_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1370-12_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1370-12_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1370-12_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1370-12_0_3_node_55 | 0.4 | n |  | TRUE
6 | bus_LV_1370-12_0_3_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1370-12_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1370-12_0_3_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1370-12_0_3_node_54 | 0.4 | n |  | TRUE
10 | bus_LV_1370-12_0_3_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_1370-12_0_3_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_1370-12_0_3_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_1370-12_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1370-12_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1370-12_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1370-12_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1370-12_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1370-12_0_3_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_1370-12_0_3_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1370-12_0_3_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_1370-12_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1370-12_0_3_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1370-12_0_3_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_1370-12_0_3_node_49 | 0.4 | n |  | TRUE
25 | bus_LV_1370-12_0_3_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_1370-12_0_3_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_1370-12_0_3_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_1370-12_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1370-12_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1370-12_0_3_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1370-12_0_3_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1370-12_0_3_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_1370-12_0_3_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_1370-12_0_3_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_1370-12_0_3_node_56 | 0.4 | n |  | TRUE
36 | bus_LV_1370-12_0_3_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1370-12_0_3_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_1370-12_0_3_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1370-12_0_3_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_1370-12_0_3_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_1370-12_0_3_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_1370-12_0_3_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_1370-12_0_3_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_1370-12_0_3_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_1370-12_0_3_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1370-12_0_3_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_1370-12_0_3_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_1370-12_0_3_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_1370-12_0_3_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_1370-12_0_3_node_53 | 0.4 | n |  | TRUE
51 | bus_LV_1370-12_0_3_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_1370-12_0_3_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_1370-12_0_3_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1370-12_0_3_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_1370-12_0_3_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_1370-12_0_3_node_57 | 0.4 | n |  | TRUE
57 | bus_MV_22_0_node_202 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1370-12_0_3_load_0 | 0 | 0.0020582 | 0.00051584 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1370-12_0_3_load_1 | 1 | 0.0082497 | 0.0020676 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1370-12_0_3_load_2 | 2 | 0.0034457 | 0.00086357 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1370-12_0_3_load_8 | 6 | 0.0031358 | 0.00078592 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1370-12_0_3_load_4 | 7 | 0.0034741 | 0.0008707 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1370-12_0_3_load_54 | 9 | 0.0028294 | 0.00070911 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1370-12_0_3_load_31 | 10 | 0.005345 | 0.0013396 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1370-12_0_3_load_32 | 11 | 0.0014671 | 0.00036769 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1370-12_0_3_load_6 | 13 | 0.0015073 | 0.00037776 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1370-12_0_3_load_13 | 16 | 0.0032875 | 0.00082393 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1370-12_0_3_load_9 | 17 | 0.010585 | 0.0026529 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1370-12_0_3_load_44 | 18 | 0.0014333 | 0.00035923 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1370-12_0_3_load_29 | 19 | 0.0012528 | 0.00031398 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1370-12_0_3_load_12 | 21 | 0.0033213 | 0.00083241 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1370-12_0_3_load_27 | 23 | 0.0012109 | 0.00030348 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1370-12_0_3_load_49 | 24 | 0.002964 | 0.00074284 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1370-12_0_3_load_33 | 26 | 0.0017971 | 0.0004504 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1370-12_0_3_load_14 | 27 | 0.0034146 | 0.00085577 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1370-12_0_3_load_16 | 29 | 0.00065102 | 0.00016316 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1370-12_0_3_load_34 | 30 | 0.0048648 | 0.0012192 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1370-12_0_3_load_18 | 31 | 0.0014708 | 0.00036861 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1370-12_0_3_load_19 | 34 | 0.00062875 | 0.00015758 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1370-12_0_3_load_56 | 35 | 0.0016828 | 0.00042176 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1370-12_0_3_load_47 | 37 | 0.0097724 | 0.0024492 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1370-12_0_3_load_23 | 38 | 0.0014216 | 0.00035629 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1370-12_0_3_load_20 | 39 | 0.00047004 | 0.0001178 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1370-12_0_3_load_25 | 41 | 0.0021566 | 0.0005405 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1370-12_0_3_load_45 | 42 | 0.0011806 | 0.00029589 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1370-12_0_3_load_38 | 43 | 0.0041334 | 0.0010359 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1370-12_0_3_load_28 | 44 | 0.006774 | 0.0016977 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1370-12_0_3_load_42 | 45 | 0.0014928 | 0.00037413 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1370-12_0_3_load_37 | 46 | 0.0017429 | 0.0004368 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1370-12_0_3_load_40 | 47 | 0.0017053 | 0.0004274 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1370-12_0_3_load_41 | 48 | 0.0029289 | 0.00073404 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1370-12_0_3_load_43 | 49 | 0.0033556 | 0.000841 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1370-12_0_3_load_53 | 50 | 0.0019912 | 0.00049905 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1370-12_0_3_load_46 | 52 | 0.0012109 | 0.00030347 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1370-12_0_3_load_48 | 53 | 0.0061074 | 0.0015306 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1370-12_0_3_load_50 | 54 | 0.0028203 | 0.00070684 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1370-12_0_3_load_57 | 56 | 0.004969 | 0.0012453 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1370-12_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1370-12_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0031927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1370-12_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.014716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1370-12_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.021282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1370-12_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.067468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1370-12_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0090418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1370-12_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.027983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1370-12_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.063783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1370-12_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.073937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1370-12_0_3_line_9 | NAYY 4x150 SE | 6 | 12 | 0.010351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1370-12_0_3_line_10 | NAYY 4x150 SE | 7 | 10 | 0.17642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1370-12_0_3_line_11 | NAYY 4x150 SE | 8 | 21 | 0.092509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1370-12_0_3_line_12 | NAYY 4x150 SE | 9 | 24 | 0.023469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1370-12_0_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.051376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1370-12_0_3_line_14 | NAYY 4x150 SE | 11 | 14 | 0.017928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1370-12_0_3_line_15 | NAYY 4x150 SE | 12 | 18 | 0.011733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1370-12_0_3_line_16 | NAYY 4x150 SE | 12 | 19 | 0.044384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1370-12_0_3_line_17 | NAYY 4x150 SE | 13 | 14 | 0.021795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1370-12_0_3_line_18 | NAYY 4x150 SE | 13 | 15 | 0.11379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1370-12_0_3_line_19 | NAYY 4x150 SE | 15 | 16 | 0.029214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1370-12_0_3_line_20 | NAYY 4x150 SE | 15 | 17 | 0.081718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1370-12_0_3_line_21 | NAYY 4x150 SE | 16 | 20 | 0.044563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1370-12_0_3_line_22 | NAYY 4x150 SE | 18 | 45 | 0.020855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1370-12_0_3_line_23 | NAYY 4x150 SE | 19 | 44 | 0.090008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1370-12_0_3_line_24 | NAYY 4x150 SE | 20 | 25 | 0.009784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1370-12_0_3_line_25 | NAYY 4x150 SE | 20 | 26 | 0.014764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1370-12_0_3_line_26 | NAYY 4x150 SE | 21 | 22 | 0.013876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1370-12_0_3_line_27 | NAYY 4x150 SE | 22 | 23 | 0.035494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1370-12_0_3_line_28 | NAYY 4x150 SE | 23 | 32 | 0.0083239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1370-12_0_3_line_29 | NAYY 4x150 SE | 24 | 37 | 0.060861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1370-12_0_3_line_30 | NAYY 4x150 SE | 25 | 46 | 0.011538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1370-12_0_3_line_31 | NAYY 4x150 SE | 26 | 30 | 0.065154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1370-12_0_3_line_32 | NAYY 4x150 SE | 27 | 28 | 0.097562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1370-12_0_3_line_33 | NAYY 4x150 SE | 28 | 29 | 0.053381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1370-12_0_3_line_34 | NAYY 4x150 SE | 29 | 31 | 0.030856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1370-12_0_3_line_35 | NAYY 4x150 SE | 31 | 34 | 0.0045565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1370-12_0_3_line_36 | NAYY 4x150 SE | 32 | 33 | 0.077684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1370-12_0_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.024299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1370-12_0_3_line_38 | NAYY 4x150 SE | 33 | 36 | 0.047965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1370-12_0_3_line_39 | NAYY 4x150 SE | 34 | 36 | 0.029264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1370-12_0_3_line_40 | NAYY 4x150 SE | 36 | 38 | 0.029209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1370-12_0_3_line_41 | NAYY 4x150 SE | 36 | 39 | 0.051839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1370-12_0_3_line_42 | NAYY 4x150 SE | 37 | 42 | 0.043615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1370-12_0_3_line_43 | NAYY 4x150 SE | 39 | 40 | 0.020517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1370-12_0_3_line_44 | NAYY 4x150 SE | 40 | 41 | 0.10469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1370-12_0_3_line_45 | NAYY 4x150 SE | 41 | 43 | 0.033127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1370-12_0_3_line_46 | NAYY 4x150 SE | 42 | 52 | 0.0049987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1370-12_0_3_line_47 | NAYY 4x150 SE | 45 | 47 | 0.026471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1370-12_0_3_line_48 | NAYY 4x150 SE | 47 | 48 | 0.017772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1370-12_0_3_line_49 | NAYY 4x150 SE | 48 | 49 | 0.033208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1370-12_0_3_line_50 | NAYY 4x150 SE | 49 | 50 | 0.027919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1370-12_0_3_line_51 | NAYY 4x150 SE | 50 | 51 | 0.0063253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1370-12_0_3_line_52 | NAYY 4x150 SE | 51 | 55 | 0.050168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1370-12_0_3_line_53 | NAYY 4x150 SE | 51 | 54 | 0.016998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1370-12_0_3_line_54 | NAYY 4x150 SE | 52 | 53 | 0.022019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1370-12_0_3_line_55 | NAYY 4x150 SE | 55 | 56 | 0.008939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1370-12_0_3_trafo_11 | 0.25 MVA 20/0.4 kV | 57 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2693404.7345 | 1216598.2249 | 2693422.4888 | 1216587.1079
1 | 2693404.7345 | 1216598.2249 | 2693402.0285 | 1216599.9193
2 | 2693389.5559 | 1216607.7292 | 2693402.0285 | 1216599.9193
3 | 2693398.0862 | 1216626.9094 | 2693395.3725 | 1216616.4374 | 2693389.5559 | 1216607.7292
4 | 2693370.529 | 1216546.0888 | 2693369.5481 | 1216553.4451 | 2693368.2671 | 1216562.9872 | 2693372.158 | 1216581.6832 | 2693389.5559 | 1216607.7292
5 | 2693398.0862 | 1216626.9094 | 2693392.1673 | 1216627.6282 | 2693389.409 | 1216626.259
6 | 2693398.0862 | 1216626.9094 | 2693408.3101 | 1216647.5171 | 2693409.8645 | 1216652.2469
7 | 2693370.529 | 1216546.0888 | 2693414.9766 | 1216500.3426
8 | 2693370.529 | 1216546.0888 | 2693363.6942 | 1216538.3875 | 2693333.2716 | 1216482.8841 | 2693333.1271 | 1216482.5699
9 | 2693382.241 | 1216619.0335 | 2693387.1945 | 1216625.1597 | 2693389.409 | 1216626.259
10 | 2693409.8645 | 1216652.2469 | 2693392.3187 | 1216827.7947
11 | 2693414.9766 | 1216500.3426 | 2693421.0343 | 1216497.0686 | 2693457.0324 | 1216477.3749 | 2693468.2889 | 1216461.6962 | 2693474.3285 | 1216442.6445 | 2693476.8092 | 1216437.9579
12 | 2693323.3242 | 1216461.2458 | 2693333.1271 | 1216482.5699
13 | 2693392.3187 | 1216827.7947 | 2693395.6438 | 1216825.7745 | 2693441.1065 | 1216812.0641
14 | 2693458.2712 | 1216806.8876 | 2693441.1065 | 1216812.0641
15 | 2693382.241 | 1216619.0335 | 2693375.742 | 1216609.2649
16 | 2693382.241 | 1216619.0335 | 2693375.6722 | 1216623.4336 | 2693369.6467 | 1216626.597 | 2693361.5505 | 1216627.682 | 2693348.2745 | 1216625.4503 | 2693340.2504 | 1216625.9741
17 | 2693458.2712 | 1216806.8876 | 2693451.8606 | 1216786.0566
18 | 2693526.2226 | 1216699.9243 | 2693451.8606 | 1216786.0566
19 | 2693526.2226 | 1216699.9243 | 2693538.2685 | 1216691.9856 | 2693548.3983 | 1216681.2134
20 | 2693526.2226 | 1216699.9243 | 2693486.4053 | 1216628.5629
21 | 2693578.9259 | 1216648.7496 | 2693548.3983 | 1216681.2134
22 | 2693375.742 | 1216609.2649 | 2693364.1899 | 1216591.9012
23 | 2693262.78 | 1216661.4701 | 2693269.2818 | 1216662.795 | 2693276.2719 | 1216658.6349 | 2693288.3655 | 1216645.2149 | 2693303.3504 | 1216632.8743 | 2693323.2747 | 1216627.0822 | 2693340.2504 | 1216625.9741
24 | 2693586.9676 | 1216643.4055 | 2693581.3508 | 1216646.1636 | 2693578.9259 | 1216648.7496
25 | 2693578.9259 | 1216648.7496 | 2693577.997 | 1216644.0762 | 2693571.2091 | 1216636.7343
26 | 2693489.6257 | 1216436.5913 | 2693486.4966 | 1216435.1746 | 2693481.9725 | 1216435.0702 | 2693476.8092 | 1216437.9579
27 | 2693489.6257 | 1216436.5913 | 2693510.5463 | 1216407.9186
28 | 2693515.4526 | 1216401.1943 | 2693510.5463 | 1216407.9186
29 | 2693323.3242 | 1216461.2458 | 2693297.9031 | 1216405.948
30 | 2693586.9676 | 1216643.4055 | 2693592.1936 | 1216643.2874 | 2693598.397 | 1216644.445
31 | 2693561.0019 | 1216606.4613 | 2693573.3345 | 1216599.1388 | 2693577.0011 | 1216599.1964 | 2693577.3601 | 1216602.4487 | 2693574.0224 | 1216607.0661 | 2693567.032 | 1216611.2259 | 2693565.1325 | 1216615.6547 | 2693562.1628 | 1216627.7831 | 2693567.9099 | 1216633.1659 | 2693571.2091 | 1216636.7343
32 | 2693606.2287 | 1216400.0516 | 2693660.5655 | 1216428.7137 | 2693695.5659 | 1216437.672
33 | 2693606.2287 | 1216400.0516 | 2693585.6754 | 1216358.3224 | 2693583.7494 | 1216351.7338
34 | 2693583.7494 | 1216351.7338 | 2693582.5767 | 1216347.7221 | 2693573.7779 | 1216337.4324 | 2693565.0948 | 1216332.8263 | 2693562.3063 | 1216331.0461
35 | 2693562.3063 | 1216331.0461 | 2693558.4657 | 1216328.5943
36 | 2693510.6588 | 1216325.3892 | 2693509.1118 | 1216341.2203 | 2693515.6329 | 1216361.1696 | 2693519.4505 | 1216382.5776 | 2693515.4526 | 1216401.1943
37 | 2693510.6588 | 1216325.3892 | 2693521.5466 | 1216330.319 | 2693526.9635 | 1216335.4742 | 2693528.9279 | 1216339.9748
38 | 2693510.6588 | 1216325.3892 | 2693518.1073 | 1216314.3207 | 2693542.0892 | 1216302.6445 | 2693549.8955 | 1216300.7101
39 | 2693549.8955 | 1216300.7101 | 2693555.3074 | 1216320.6866 | 2693558.2381 | 1216328.449 | 2693558.4657 | 1216328.5943
40 | 2693549.8955 | 1216300.7101 | 2693550.2276 | 1216285.8496 | 2693552.8636 | 1216271.7492
41 | 2693549.8955 | 1216300.7101 | 2693558.622 | 1216300.1356 | 2693577.5038 | 1216300.8547 | 2693591.7034 | 1216304.2799 | 2693600.3736 | 1216308.3811
42 | 2693279.6856 | 1216366.3199 | 2693297.9031 | 1216405.948
43 | 2693617.955 | 1216318.7577 | 2693610.4495 | 1216313.147 | 2693600.3736 | 1216308.3811
44 | 2693617.955 | 1216318.7577 | 2693636.3211 | 1216317.0116 | 2693645.9435 | 1216314.5166 | 2693661.4849 | 1216310.836 | 2693679.543 | 1216305.9831 | 2693699.969 | 1216301.7012 | 2693715.3772 | 1216299.7309 | 2693720.586 | 1216299.2615
45 | 2693720.586 | 1216299.2615 | 2693732.0767 | 1216298.2258 | 2693745.8336 | 1216298.887 | 2693753.6448 | 1216298.5763
46 | 2693279.6856 | 1216366.3199 | 2693277.5977 | 1216361.7782
47 | 2693349.5272 | 1216569.862 | 2693364.1899 | 1216591.9012
48 | 2693349.5272 | 1216569.862 | 2693341.1794 | 1216557.3146 | 2693339.145 | 1216555.5368
49 | 2693314.1397 | 1216533.6852 | 2693339.145 | 1216555.5368
50 | 2693314.1397 | 1216533.6852 | 2693310.7593 | 1216530.7312 | 2693290.8385 | 1216518.3984
51 | 2693285.4604 | 1216515.0689 | 2693290.8385 | 1216518.3984
52 | 2693285.4604 | 1216515.0689 | 2693279.6965 | 1216518.9814 | 2693247.9946 | 1216526.2237 | 2693237.1834 | 1216526.5993
53 | 2693285.4604 | 1216515.0689 | 2693270.979 | 1216506.1687
54 | 2693268.4005 | 1216341.7718 | 2693277.5977 | 1216361.7782
55 | 2693237.1834 | 1216526.5993 | 2693230.5812 | 1216532.6446

## bus_geodata
| x | y | coords
0 | 2693404.7345 | 1216598.2249
1 | 2693422.4888 | 1216587.1079
2 | 2693402.0285 | 1216599.9193
3 | 2693389.5559 | 1216607.7292
4 | 2693398.0862 | 1216626.9094
5 | 2693370.529 | 1216546.0888
6 | 2693389.409 | 1216626.259
7 | 2693409.8645 | 1216652.2469
8 | 2693414.9766 | 1216500.3426
9 | 2693333.1271 | 1216482.5699
10 | 2693392.3187 | 1216827.7947
11 | 2693441.1065 | 1216812.0641
12 | 2693382.241 | 1216619.0335
13 | 2693451.8606 | 1216786.0566
14 | 2693458.2712 | 1216806.8876
15 | 2693526.2226 | 1216699.9243
16 | 2693548.3983 | 1216681.2134
17 | 2693486.4053 | 1216628.5629
18 | 2693375.742 | 1216609.2649
19 | 2693340.2504 | 1216625.9741
20 | 2693578.9259 | 1216648.7496
21 | 2693476.8092 | 1216437.9579
22 | 2693489.6257 | 1216436.5913
23 | 2693510.5463 | 1216407.9186
24 | 2693323.3242 | 1216461.2458
25 | 2693586.9676 | 1216643.4055
26 | 2693571.2091 | 1216636.7343
27 | 2693695.5659 | 1216437.672
28 | 2693606.2287 | 1216400.0516
29 | 2693583.7494 | 1216351.7338
30 | 2693561.0019 | 1216606.4613
31 | 2693562.3063 | 1216331.0461
32 | 2693515.4526 | 1216401.1943
33 | 2693510.6588 | 1216325.3892
34 | 2693558.4657 | 1216328.5943
35 | 2693528.9279 | 1216339.9748
36 | 2693549.8955 | 1216300.7101
37 | 2693297.9031 | 1216405.948
38 | 2693552.8636 | 1216271.7492
39 | 2693600.3736 | 1216308.3811
40 | 2693617.955 | 1216318.7577
41 | 2693720.586 | 1216299.2615
42 | 2693279.6856 | 1216366.3199
43 | 2693753.6448 | 1216298.5763
44 | 2693262.78 | 1216661.4701
45 | 2693364.1899 | 1216591.9012
46 | 2693598.397 | 1216644.445
47 | 2693349.5272 | 1216569.862
48 | 2693339.145 | 1216555.5368
49 | 2693314.1397 | 1216533.6852
50 | 2693290.8385 | 1216518.3984
51 | 2693285.4604 | 1216515.0689
52 | 2693277.5977 | 1216361.7782
53 | 2693268.4005 | 1216341.7718
54 | 2693270.979 | 1216506.1687
55 | 2693237.1834 | 1216526.5993
56 | 2693230.5812 | 1216532.6446
57 | 2693489.6257 | 1216436.5913

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99097 | -0.062849 | 0.0020582 | 0.00051584
1 | 0.99072 | -0.064606 | 0.0082497 | 0.0020676
2 | 0.99102 | -0.062515 | 0.0034457 | 0.00086357
3 | 0.99131 | -0.060458 | 0 | 0
4 | 0.98927 | -0.074759 | 0 | 0
5 | 0.99521 | -0.033227 | 0 | 0
6 | 0.98885 | -0.077701 | 0.0031358 | 0.00078592
7 | 0.98787 | -0.084513 | 0.0034741 | 0.0008707
8 | 1 | 0 | -0.12686 | -0.031797
9 | 0.99265 | -0.051216 | 0.0028294 | 0.00070911
10 | 0.97997 | -0.14026 | 0.005345 | 0.0013396
11 | 0.97807 | -0.15379 | 0.0014671 | 0.00036769
12 | 0.98842 | -0.080741 | 0 | 0
13 | 0.97669 | -0.16367 | 0.0015073 | 0.00037776
14 | 0.97745 | -0.15824 | 0 | 0
15 | 0.97297 | -0.19033 | 0 | 0
16 | 0.97247 | -0.19394 | 0.0032875 | 0.00082393
17 | 0.9717 | -0.19946 | 0.010585 | 0.0026529
18 | 0.98807 | -0.083225 | 0.0014333 | 0.00035923
19 | 0.98791 | -0.084387 | 0.0012528 | 0.00031398
20 | 0.97192 | -0.1979 | 0 | 0
21 | 0.99727 | -0.019099 | 0.0033213 | 0.00083241
22 | 0.99693 | -0.02151 | 0 | 0
23 | 0.99605 | -0.027682 | 0.0012109 | 0.00030348
24 | 0.99193 | -0.056271 | 0.002964 | 0.00074284
25 | 0.97189 | -0.19808 | 0 | 0
26 | 0.97177 | -0.19894 | 0.0017971 | 0.0004504
27 | 0.99186 | -0.057205 | 0.0034146 | 0.00085577
28 | 0.99234 | -0.053823 | 0 | 0
29 | 0.9926 | -0.051969 | 0.00065102 | 0.00016316
30 | 0.97131 | -0.20229 | 0.0048648 | 0.0012192
31 | 0.99278 | -0.050694 | 0.0014708 | 0.00036861
32 | 0.99586 | -0.029029 | 0 | 0
33 | 0.99407 | -0.041626 | 0 | 0
34 | 0.99282 | -0.050438 | 0.00062875 | 0.00015758
35 | 0.99401 | -0.042039 | 0.0016828 | 0.00042176
36 | 0.99308 | -0.048606 | 0 | 0
37 | 0.99033 | -0.067575 | 0.0097724 | 0.0024492
38 | 0.99302 | -0.049026 | 0.0014216 | 0.00035629
39 | 0.99258 | -0.052163 | 0.00047004 | 0.0001178
40 | 0.99239 | -0.053474 | 0 | 0
41 | 0.99144 | -0.060162 | 0.0021566 | 0.0005405
42 | 0.9898 | -0.071351 | 0.0011806 | 0.00029589
43 | 0.99125 | -0.061553 | 0.0041334 | 0.0010359
44 | 0.98703 | -0.090631 | 0.006774 | 0.0016977
45 | 0.98749 | -0.087338 | 0.0014928 | 0.00037413
46 | 0.97186 | -0.19829 | 0.0017429 | 0.0004368
47 | 0.98681 | -0.09216 | 0.0017053 | 0.0004274
48 | 0.9864 | -0.09509 | 0.0029289 | 0.00073404
49 | 0.98577 | -0.099572 | 0.0033556 | 0.000841
50 | 0.98537 | -0.10238 | 0.0019912 | 0.00049905
51 | 0.9853 | -0.10289 | 0 | 0
52 | 0.98974 | -0.071724 | 0.0012109 | 0.00030347
53 | 0.98955 | -0.073094 | 0.0061074 | 0.0015306
54 | 0.98523 | -0.10338 | 0.0028203 | 0.00070684
55 | 0.98494 | -0.10545 | 0 | 0
56 | 0.98487 | -0.10591 | 0.004969 | 0.0012453
57 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0082517 | 0.0020681 | -0.0082497 | -0.0020676 | 2.0068e-06 | 5.0203e-07 | 0.012391 | 0.012391 | 0.012391 | 0.99097 | -0.062849 | 0.99072 | -0.064606 | 4.5891
1 | -0.01031 | -0.0025839 | 0.01031 | 0.002584 | 4.7747e-07 | 1.4251e-07 | 0.015481 | 0.015481 | 0.015481 | 0.99097 | -0.062849 | 0.99102 | -0.062515 | 5.7337
2 | -0.013756 | -0.0034476 | 0.01376 | 0.0034489 | 3.9176e-06 | 1.3171e-06 | 0.020655 | 0.020655 | 0.020655 | 0.99102 | -0.062515 | 0.99131 | -0.060458 | 7.6499
3 | 0.066628 | 0.016779 | -0.066495 | -0.016728 | 0.00013291 | 5.0845e-05 | 0.10004 | 0.10004 | 0.10004 | 0.99131 | -0.060458 | 0.98927 | -0.074759 | 37.0522
4 | -0.080388 | -0.020227 | 0.080694 | 0.020344 | 0.00030664 | 0.00011619 | 0.1207 | 0.12069 | 0.1207 | 0.99131 | -0.060458 | 0.99521 | -0.033227 | 22.351
5 | 0.031946 | 0.0080131 | -0.031933 | -0.0080082 | 1.3028e-05 | 4.8949e-06 | 0.048054 | 0.048054 | 0.048054 | 0.98927 | -0.074759 | 0.98885 | -0.077701 | 17.7977
6 | 0.034549 | 0.0087146 | -0.034502 | -0.0086968 | 4.7193e-05 | 1.7792e-05 | 0.051987 | 0.051987 | 0.051987 | 0.98927 | -0.074759 | 0.98787 | -0.084513 | 19.2546
7 | -0.10487 | -0.026414 | 0.10536 | 0.026601 | 0.00048955 | 0.00018662 | 0.15684 | 0.15684 | 0.15684 | 0.99521 | -0.033227 | 1 | 0 | 29.0452
8 | 0.024174 | 0.0060705 | -0.024114 | -0.0060482 | 6.0291e-05 | 2.223e-05 | 0.036149 | 0.03615 | 0.03615 | 0.99521 | -0.033227 | 0.99265 | -0.051216 | 13.3888
9 | 0.028797 | 0.0072223 | -0.028785 | -0.0072178 | 1.2129e-05 | 4.5323e-06 | 0.043335 | 0.043335 | 0.043335 | 0.98885 | -0.077701 | 0.98842 | -0.080741 | 16.05
10 | 0.031028 | 0.0078261 | -0.030787 | -0.0077358 | 0.00024065 | 9.0318e-05 | 0.046754 | 0.046755 | 0.046755 | 0.98787 | -0.084513 | 0.97997 | -0.14026 | 17.3167
11 | 0.020698 | 0.005196 | -0.020644 | -0.0051761 | 5.477e-05 | 1.9855e-05 | 0.030802 | 0.030803 | 0.030803 | 1 | 0 | 0.99727 | -0.019099 | 11.4084
12 | 0.021285 | 0.0053391 | -0.02127 | -0.0053337 | 1.4911e-05 | 5.4317e-06 | 0.031908 | 0.031908 | 0.031908 | 0.99265 | -0.051216 | 0.99193 | -0.056271 | 11.8179
13 | 0.025442 | 0.0063962 | -0.025394 | -0.0063784 | 4.7863e-05 | 1.7763e-05 | 0.038639 | 0.038639 | 0.038639 | 0.97997 | -0.14026 | 0.97807 | -0.15379 | 14.3109
14 | 0.023927 | 0.0060107 | -0.023912 | -0.0060053 | 1.4829e-05 | 5.4785e-06 | 0.036407 | 0.036408 | 0.036408 | 0.97807 | -0.15379 | 0.97745 | -0.15824 | 13.4843
15 | 0.020748 | 0.005204 | -0.020741 | -0.0052014 | 7.1435e-06 | 2.5972e-06 | 0.031236 | 0.031236 | 0.031236 | 0.98842 | -0.080741 | 0.98807 | -0.083225 | 11.569
16 | 0.0080367 | 0.0020138 | -0.0080327 | -0.0020128 | 4.0541e-06 | 9.9069e-07 | 0.012099 | 0.012099 | 0.012099 | 0.98842 | -0.080741 | 0.98791 | -0.084387 | 4.4811
17 | -0.023894 | -0.0059986 | 0.023912 | 0.0060053 | 1.8027e-05 | 6.6606e-06 | 0.036408 | 0.036408 | 0.036408 | 0.97669 | -0.16367 | 0.97745 | -0.15824 | 13.4843
18 | 0.022387 | 0.0056208 | -0.022304 | -0.0055905 | 8.2622e-05 | 3.0359e-05 | 0.034111 | 0.034112 | 0.034112 | 0.97669 | -0.16367 | 0.97297 | -0.19033 | 12.634
19 | 0.011706 | 0.0029335 | -0.0117 | -0.0029316 | 5.8426e-06 | 1.8845e-06 | 0.017903 | 0.017903 | 0.017903 | 0.97297 | -0.19033 | 0.97247 | -0.19394 | 6.6307
20 | 0.010598 | 0.002657 | -0.010585 | -0.0026529 | 1.3398e-05 | 4.1393e-06 | 0.016209 | 0.016209 | 0.016209 | 0.97297 | -0.19033 | 0.9717 | -0.19946 | 6.0035
21 | 0.0084127 | 0.0021077 | -0.0084081 | -0.0021065 | 4.6077e-06 | 1.2196e-06 | 0.012872 | 0.012873 | 0.012873 | 0.97247 | -0.19394 | 0.97192 | -0.1979 | 4.7677
22 | 0.019307 | 0.0048421 | -0.019296 | -0.0048382 | 1.1003e-05 | 3.9651e-06 | 0.029078 | 0.029078 | 0.029078 | 0.98807 | -0.083225 | 0.98749 | -0.087338 | 10.7696
23 | 0.0067799 | 0.0016988 | -0.006774 | -0.0016977 | 5.8573e-06 | 1.1014e-06 | 0.010212 | 0.010212 | 0.010212 | 0.98791 | -0.084387 | 0.98703 | -0.090631 | 3.7823
24 | 0.001743 | 0.00043658 | -0.0017429 | -0.00043668 | 4.3472e-08 | -1.0453e-07 | 0.0026684 | 0.0026685 | 0.0026685 | 0.97192 | -0.1979 | 0.97189 | -0.19808 | 0.98832
25 | 0.0066652 | 0.0016699 | -0.0066642 | -0.0016697 | 9.5928e-07 | 1.8602e-07 | 0.010204 | 0.010204 | 0.010204 | 0.97192 | -0.1979 | 0.97177 | -0.19894 | 3.7794
26 | 0.017322 | 0.0043437 | -0.017316 | -0.0043417 | 5.7846e-06 | 2.0439e-06 | 0.025847 | 0.025847 | 0.025847 | 0.99727 | -0.019099 | 0.99693 | -0.02151 | 9.573
27 | 0.017316 | 0.0043417 | -0.017302 | -0.0043364 | 1.4797e-05 | 5.2286e-06 | 0.025847 | 0.025847 | 0.025847 | 0.99693 | -0.02151 | 0.99605 | -0.027682 | 9.5731
28 | 0.016091 | 0.004033 | -0.016088 | -0.0040319 | 3.0014e-06 | 1.0461e-06 | 0.024038 | 0.024038 | 0.024038 | 0.99605 | -0.027682 | 0.99586 | -0.029029 | 8.9031
29 | 0.018306 | 0.0045908 | -0.018277 | -0.0045806 | 2.8642e-05 | 1.0232e-05 | 0.027462 | 0.027462 | 0.027462 | 0.99193 | -0.056271 | 0.99033 | -0.067575 | 10.1713
30 | 0.0017429 | 0.00043668 | -0.0017429 | -0.0004368 | 5.1267e-08 | -1.2326e-07 | 0.0026685 | 0.0026685 | 0.0026685 | 0.97189 | -0.19808 | 0.97186 | -0.19829 | 0.98834
31 | 0.0048671 | 0.0012193 | -0.0048648 | -0.0012192 | 2.2581e-06 | 6.1694e-08 | 0.0074525 | 0.0074528 | 0.0074528 | 0.97177 | -0.19894 | 0.97131 | -0.20229 | 2.7603
32 | -0.0034146 | -0.00085577 | 0.0034162 | 0.00085513 | 1.5974e-06 | -6.4542e-07 | 0.0051226 | 0.0051222 | 0.0051226 | 0.99186 | -0.057205 | 0.99234 | -0.053823 | 1.8973
33 | -0.0034162 | -0.00085513 | 0.0034171 | 0.00085478 | 8.7389e-07 | -3.537e-07 | 0.0051222 | 0.0051219 | 0.0051222 | 0.99234 | -0.053823 | 0.9926 | -0.051969 | 1.8971
34 | -0.0040681 | -0.0010179 | 0.0040688 | 0.0010178 | 7.1593e-07 | -1.2356e-07 | 0.0060979 | 0.0060977 | 0.0060979 | 0.9926 | -0.051969 | 0.99278 | -0.050694 | 2.2585
35 | -0.0055396 | -0.0013864 | 0.0055398 | 0.0013864 | 1.9598e-07 | 1.6454e-08 | 0.0083022 | 0.0083022 | 0.0083022 | 0.99278 | -0.050694 | 0.99282 | -0.050438 | 3.0749
36 | 0.016088 | 0.0040319 | -0.01606 | -0.0040221 | 2.8011e-05 | 9.7646e-06 | 0.024038 | 0.024039 | 0.024039 | 0.99586 | -0.029029 | 0.99407 | -0.041626 | 8.9032
37 | 0.0016829 | 0.00042148 | -0.0016828 | -0.00042176 | 9.622e-08 | -2.7799e-07 | 0.002519 | 0.0025192 | 0.0025192 | 0.99407 | -0.041626 | 0.99401 | -0.042039 | 0.93302
38 | 0.014377 | 0.0036007 | -0.014363 | -0.003596 | 1.3861e-05 | 4.7098e-06 | 0.02152 | 0.02152 | 0.02152 | 0.99407 | -0.041626 | 0.99308 | -0.048606 | 7.9703
39 | -0.0061685 | -0.001544 | 0.0061701 | 0.0015442 | 1.5606e-06 | 2.2169e-07 | 0.0092445 | 0.0092444 | 0.0092445 | 0.99282 | -0.050438 | 0.99308 | -0.048606 | 3.4239
40 | 0.0014217 | 0.00035594 | -0.0014216 | -0.00035629 | 8.2705e-08 | -3.4608e-07 | 0.0021301 | 0.0021302 | 0.0021302 | 0.99308 | -0.048606 | 0.99302 | -0.049026 | 0.78898
41 | 0.0067711 | 0.0016958 | -0.0067678 | -0.0016952 | 3.3295e-06 | 6.1022e-07 | 0.010145 | 0.010146 | 0.010146 | 0.99308 | -0.048606 | 0.99258 | -0.052163 | 3.7576
42 | 0.0085048 | 0.0021314 | -0.0085004 | -0.0021303 | 4.4444e-06 | 1.1485e-06 | 0.012779 | 0.012779 | 0.012779 | 0.99033 | -0.067575 | 0.9898 | -0.071351 | 4.733
43 | 0.0062978 | 0.0015774 | -0.0062966 | -0.0015772 | 1.1411e-06 | 1.7375e-07 | 0.0094409 | 0.009441 | 0.009441 | 0.99258 | -0.052163 | 0.99239 | -0.053474 | 3.4967
44 | 0.0062966 | 0.0015772 | -0.0062908 | -0.0015763 | 5.8232e-06 | 8.8831e-07 | 0.009441 | 0.0094415 | 0.0094415 | 0.99239 | -0.053474 | 0.99144 | -0.060162 | 3.4968
45 | 0.0041342 | 0.0010358 | -0.0041334 | -0.0010359 | 7.9584e-07 | -1.2103e-07 | 0.0062047 | 0.0062048 | 0.0062048 | 0.99144 | -0.060162 | 0.99125 | -0.061553 | 2.2981
46 | 0.0073198 | 0.0018344 | -0.0073194 | -0.0018343 | 3.7771e-07 | 8.1028e-08 | 0.011004 | 0.011004 | 0.011004 | 0.9898 | -0.071351 | 0.98974 | -0.071724 | 4.0756
47 | 0.017804 | 0.0044641 | -0.017792 | -0.0044598 | 1.1889e-05 | 4.2343e-06 | 0.026828 | 0.026828 | 0.026828 | 0.98749 | -0.087338 | 0.98681 | -0.09216 | 9.9365
48 | 0.016086 | 0.0040324 | -0.01608 | -0.0040301 | 6.5254e-06 | 2.2828e-06 | 0.024257 | 0.024257 | 0.024257 | 0.98681 | -0.09216 | 0.9864 | -0.09509 | 8.9841
49 | 0.013151 | 0.0032961 | -0.013143 | -0.0032934 | 8.1556e-06 | 2.7132e-06 | 0.019839 | 0.019839 | 0.019839 | 0.9864 | -0.09509 | 0.98577 | -0.099572 | 7.3477
50 | 0.0097872 | 0.0024524 | -0.0097834 | -0.0024513 | 3.8024e-06 | 1.1067e-06 | 0.014774 | 0.014774 | 0.014774 | 0.98577 | -0.099572 | 0.98537 | -0.10238 | 5.4717
51 | 0.0077921 | 0.0019522 | -0.0077916 | -0.0019521 | 5.4649e-07 | 1.2962e-07 | 0.011767 | 0.011767 | 0.011767 | 0.98537 | -0.10238 | 0.9853 | -0.10289 | 4.3581
52 | 0.0049711 | 0.0012454 | -0.0049693 | -0.0012454 | 1.7643e-06 | 3.9867e-08 | 0.0075072 | 0.0075074 | 0.0075074 | 0.9853 | -0.10289 | 0.98494 | -0.10545 | 2.7805
53 | 0.0028205 | 0.0007067 | -0.0028203 | -0.00070684 | 1.9245e-07 | -1.4246e-07 | 0.0042595 | 0.0042596 | 0.0042596 | 0.9853 | -0.10289 | 0.98523 | -0.10338 | 1.5776
54 | 0.0061085 | 0.0015308 | -0.0061074 | -0.0015306 | 1.1589e-06 | 1.6279e-07 | 0.0091837 | 0.0091838 | 0.0091838 | 0.98974 | -0.071724 | 0.98955 | -0.073094 | 3.4014
55 | 0.0049693 | 0.0012454 | -0.004969 | -0.0012453 | 3.1438e-07 | 7.1571e-09 | 0.0075074 | 0.0075075 | 0.0075075 | 0.98494 | -0.10545 | 0.98487 | -0.10591 | 2.7806

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.12686 | 0.031797

## res_load
| p_mw | q_mvar
0 | 0.0020582 | 0.00051584
1 | 0.0082497 | 0.0020676
2 | 0.0034457 | 0.00086357
3 | 0.0031358 | 0.00078592
4 | 0.0034741 | 0.0008707
5 | 0.0028294 | 0.00070911
6 | 0.005345 | 0.0013396
7 | 0.0014671 | 0.00036769
8 | 0.0015073 | 0.00037776
9 | 0.0032875 | 0.00082393
10 | 0.010585 | 0.0026529
11 | 0.0014333 | 0.00035923
12 | 0.0012528 | 0.00031398
13 | 0.0033213 | 0.00083241
14 | 0.0012109 | 0.00030348
15 | 0.002964 | 0.00074284
16 | 0.0017971 | 0.0004504
17 | 0.0034146 | 0.00085577
18 | 0.00065102 | 0.00016316
19 | 0.0048648 | 0.0012192
20 | 0.0014708 | 0.00036861
21 | 0.00062875 | 0.00015758
22 | 0.0016828 | 0.00042176
23 | 0.0097724 | 0.0024492
24 | 0.0014216 | 0.00035629
25 | 0.00047004 | 0.0001178
26 | 0.0021566 | 0.0005405
27 | 0.0011806 | 0.00029589
28 | 0.0041334 | 0.0010359
29 | 0.006774 | 0.0016977
30 | 0.0014928 | 0.00037413
31 | 0.0017429 | 0.0004368
32 | 0.0017053 | 0.0004274
33 | 0.0029289 | 0.00073404
34 | 0.0033556 | 0.000841
35 | 0.0019912 | 0.00049905
36 | 0.0012109 | 0.00030347
37 | 0.0061074 | 0.0015306
38 | 0.0028203 | 0.00070684
39 | 0.004969 | 0.0012453

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1