## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1373-16_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1373-16_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1373-16_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1373-16_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1373-16_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1373-16_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1373-16_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1373-16_0_3_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1373-16_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1373-16_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1373-16_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1373-16_0_3_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1373-16_0_3_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1373-16_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1373-16_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1373-16_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1373-16_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1373-16_0_3_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1373-16_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1373-16_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1373-16_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1373-16_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1373-16_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1373-16_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1373-16_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1373-16_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1373-16_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1373-16_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1373-16_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1373-16_0_3_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1373-16_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1373-16_0_3_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1373-16_0_3_node_31 | 0.4 | n |  | TRUE
33 | bus_MV_127_0_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1373-16_0_3_load_0 | 0 | 0.0048791 | 0.0012228 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1373-16_0_3_load_1 | 1 | 0.01154 | 0.0028921 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1373-16_0_3_load_3 | 3 | 0.03152 | 0.0078997 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1373-16_0_3_load_4 | 4 | 0.00085188 | 0.0002135 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1373-16_0_3_load_32 | 7 | 0.012892 | 0.0032309 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1373-16_0_3_load_9 | 9 | 0.010844 | 0.0027177 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1373-16_0_3_load_13 | 12 | 0.0094889 | 0.0023781 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1373-16_0_3_load_11 | 13 | 0.0085176 | 0.0021347 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1373-16_0_3_load_14 | 14 | 0.003516 | 0.00088118 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1373-16_0_3_load_10 | 15 | 0.027889 | 0.0069896 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1373-16_0_3_load_15 | 16 | 0.0095312 | 0.0023887 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1373-16_0_3_load_23 | 17 | 0.0068398 | 0.0017142 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1373-16_0_3_load_16 | 18 | 0.003235 | 0.00081078 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1373-16_0_3_load_24 | 19 | 0.0074124 | 0.0018577 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1373-16_0_3_load_17 | 20 | 0.029887 | 0.0074903 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1373-16_0_3_load_18 | 21 | 0.0036347 | 0.00091093 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1373-16_0_3_load_19 | 22 | 0.0062127 | 0.001557 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1373-16_0_3_load_20 | 23 | 0.0056899 | 0.001426 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1373-16_0_3_load_21 | 24 | 0.0031522 | 0.00079002 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1373-16_0_3_load_22 | 25 | 0.0048975 | 0.0012274 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1373-16_0_3_load_26 | 26 | 0.0035625 | 0.00089284 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1373-16_0_3_load_27 | 27 | 0.002469 | 0.00061878 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1373-16_0_3_load_25 | 28 | 0.0036603 | 0.00091736 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1373-16_0_3_load_28 | 29 | 0.0028999 | 0.00072677 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1373-16_0_3_load_29 | 30 | 0.0047125 | 0.0011811 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1373-16_0_3_load_30 | 31 | 0.0044101 | 0.0011053 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1373-16_0_3_load_31 | 32 | 0.0033701 | 0.00084463 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1373-16_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1373-16_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.018044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1373-16_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.014822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1373-16_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.014138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1373-16_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.032935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1373-16_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.26684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1373-16_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.057624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1373-16_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.063616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1373-16_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.041528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1373-16_0_3_line_9 | NAYY 4x150 SE | 9 | 15 | 0.015045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1373-16_0_3_line_10 | NAYY 4x150 SE | 10 | 11 | 0.054565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1373-16_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.015986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1373-16_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.024167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1373-16_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.046389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1373-16_0_3_line_14 | NAYY 4x150 SE | 12 | 16 | 0.013617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1373-16_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.014936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1373-16_0_3_line_16 | NAYY 4x150 SE | 14 | 17 | 0.024705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1373-16_0_3_line_17 | NAYY 4x150 SE | 16 | 18 | 0.021502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1373-16_0_3_line_18 | NAYY 4x150 SE | 17 | 19 | 0.01036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1373-16_0_3_line_19 | NAYY 4x150 SE | 18 | 20 | 0.015039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1373-16_0_3_line_20 | NAYY 4x150 SE | 19 | 28 | 0.022906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1373-16_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.018667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1373-16_0_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.0055357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1373-16_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.026784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1373-16_0_3_line_24 | NAYY 4x150 SE | 23 | 24 | 0.017079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1373-16_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.0086626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1373-16_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.013514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1373-16_0_3_line_27 | NAYY 4x150 SE | 26 | 27 | 0.013824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1373-16_0_3_line_28 | NAYY 4x150 SE | 27 | 29 | 0.0076991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1373-16_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.12924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1373-16_0_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.0114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1373-16_0_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.013257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1373-16_0_3_trafo_17 | 0.25 MVA 20/0.4 kV | 33 | 20 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2689119.6596 | 1211770.9121 | 2689118.1216 | 1211765.0074 | 2689113.2985 | 1211761.2884
1 | 2689105.2296 | 1211779.9915 | 2689107.8031 | 1211775.5937 | 2689114.7336 | 1211774.074 | 2689119.6596 | 1211770.9121
2 | 2689113.2985 | 1211761.2884 | 2689113.2985 | 1211761.2884 | 2689119.6651 | 1211757.3253 | 2689126.9643 | 1211757.9127
3 | 2689093.2211 | 1211772.4738 | 2689105.2296 | 1211779.9915
4 | 2689154.5753 | 1211774.6696 | 2689132.0523 | 1211758.3222 | 2689126.9643 | 1211757.9127
5 | 2689154.5753 | 1211774.6696 | 2689182.4502 | 1211759.8875 | 2689181.5886 | 1211754.4933 | 2689201.6252 | 1211742.4848 | 2689216.6417 | 1211732.8251 | 2689212.5088 | 1211688.5671 | 2689209.904 | 1211674.7301 | 2689208.9844 | 1211668.6456 | 2689208.7029 | 1211664.0939 | 2689208.9903 | 1211659.6174 | 2689209.8757 | 1211654.783 | 2689211.2836 | 1211650.5901 | 2689213.6063 | 1211646.1997 | 2689215.5652 | 1211643.2715 | 2689218.2044 | 1211640.0755 | 2689222.3374 | 1211636.0902 | 2689217.4497 | 1211631.603 | 2689194.8479 | 1211613.8866 | 2689165.4164 | 1211600.0819 | 2689164.0266 | 1211611.2018 | 2689159.729 | 1211618.0644
6 | 2689159.729 | 1211618.0644 | 2689150.5272 | 1211632.7256 | 2689137.9227 | 1211648.7924 | 2689125.5901 | 1211664.463
7 | 2689104.8934 | 1211592.4948 | 2689112.3885 | 1211594.3969 | 2689118.3127 | 1211595.6418 | 2689122.3069 | 1211596.3575 | 2689128.1643 | 1211596.9898 | 2689130.6753 | 1211597.2831 | 2689133.4805 | 1211598.2367 | 2689135.2559 | 1211600.4648 | 2689136.5821 | 1211603.2531 | 2689138.9083 | 1211606.7569 | 2689141.6912 | 1211609.7115 | 2689145.9222 | 1211612.888 | 2689148.6696 | 1211614.6524 | 2689152.7128 | 1211616.1583 | 2689157.2376 | 1211616.9709 | 2689159.729 | 1211618.0644
8 | 2689104.8934 | 1211592.4948 | 2689103.1681 | 1211595.0485 | 2689101.1497 | 1211597.3866 | 2689082.0058 | 1211615.7463 | 2689074.1687 | 1211619.8187
9 | 2689074.1687 | 1211619.8187 | 2689071.1072 | 1211621.4095 | 2689060.08 | 1211624.9917
10 | 2688967.905 | 1211608.2608 | 2689003.7363 | 1211616.423 | 2689021.4181 | 1211619.6222
11 | 2689021.4181 | 1211619.6222 | 2689018.9375 | 1211635.4142
12 | 2689021.4181 | 1211619.6222 | 2689044.4782 | 1211623.9804 | 2689045.1756 | 1211624.0256
13 | 2688967.905 | 1211608.2608 | 2688959.3973 | 1211653.8633
14 | 2689018.9375 | 1211635.4142 | 2689016.8244 | 1211648.8661
15 | 2689045.1756 | 1211624.0256 | 2689060.08 | 1211624.9917 | 2689060.08 | 1211624.9917
16 | 2688959.3973 | 1211653.8633 | 2688958.1581 | 1211660.5059 | 2688955.0522 | 1211666.4635 | 2688945.8251 | 1211672.8632
17 | 2689013.3577 | 1211670.0843 | 2689013.9274 | 1211667.3089 | 2689016.8244 | 1211648.8661
18 | 2688945.8251 | 1211672.8632 | 2688937.3126 | 1211678.7672
19 | 2689010.3339 | 1211684.8158 | 2689013.3577 | 1211670.0843
20 | 2688937.3126 | 1211678.7672 | 2688918.4902 | 1211691.8219
21 | 2689010.3339 | 1211684.8158 | 2689007.5841 | 1211698.2127 | 2689004.8269 | 1211702.373
22 | 2689001.7688 | 1211706.9873 | 2689001.7688 | 1211706.9873 | 2689004.8269 | 1211702.373
23 | 2688976.4926 | 1211715.1824 | 2688990.0969 | 1211712.5391 | 2689001.7688 | 1211706.9873
24 | 2688976.4926 | 1211715.1824 | 2688976.4926 | 1211715.1824 | 2688962.3676 | 1211724.7836
25 | 2688955.2034 | 1211729.6534 | 2688962.3676 | 1211724.7836
26 | 2688955.2034 | 1211729.6534 | 2688944.0269 | 1211737.2504
27 | 2688932.5938 | 1211745.0219 | 2688944.0269 | 1211737.2504
28 | 2688932.5938 | 1211745.0219 | 2688926.2264 | 1211749.35
29 | 2688926.2264 | 1211749.35 | 2688910.4843 | 1211760.0504 | 2688902.4637 | 1211771.483 | 2688901.5469 | 1211783.0214 | 2688917.2044 | 1211810.84 | 2688927.6015 | 1211815.8427 | 2688939.5955 | 1211814.1538 | 2688965.4513 | 1211800.8083
30 | 2688965.4513 | 1211800.8083 | 2688975.5811 | 1211795.5797
31 | 2688987.3612 | 1211789.4994 | 2688975.5811 | 1211795.5797

## bus_geodata
| x | y | coords
0 | 2689119.6596 | 1211770.9121
1 | 2689113.2985 | 1211761.2884
2 | 2689105.2296 | 1211779.9915
3 | 2689126.9643 | 1211757.9127
4 | 2689093.2211 | 1211772.4738
5 | 2689154.5753 | 1211774.6696
6 | 2689159.729 | 1211618.0644
7 | 2689125.5901 | 1211664.463
8 | 2689104.8934 | 1211592.4948
9 | 2689074.1687 | 1211619.8187
10 | 2689021.4181 | 1211619.6222
11 | 2688967.905 | 1211608.2608
12 | 2689018.9375 | 1211635.4142
13 | 2689045.1756 | 1211624.0256
14 | 2688959.3973 | 1211653.8633
15 | 2689060.08 | 1211624.9917
16 | 2689016.8244 | 1211648.8661
17 | 2688945.8251 | 1211672.8632
18 | 2689013.3577 | 1211670.0843
19 | 2688937.3126 | 1211678.7672
20 | 2689010.3339 | 1211684.8158
21 | 2689004.8269 | 1211702.373
22 | 2689001.7688 | 1211706.9873
23 | 2688976.4926 | 1211715.1824
24 | 2688962.3676 | 1211724.7836
25 | 2688955.2034 | 1211729.6534
26 | 2688944.0269 | 1211737.2504
27 | 2688932.5938 | 1211745.0219
28 | 2688918.4902 | 1211691.8219
29 | 2688926.2264 | 1211749.35
30 | 2688965.4513 | 1211800.8083
31 | 2688975.5811 | 1211795.5797
32 | 2688987.3612 | 1211789.4994
33 | 2689021.4181 | 1211619.6222

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97221 | -0.19564 | 0.0048791 | 0.0012228
1 | 0.97231 | -0.19491 | 0.01154 | 0.0028921
2 | 0.97218 | -0.19581 | 0 | 0
3 | 0.97268 | -0.1922 | 0.03152 | 0.0078997
4 | 0.97217 | -0.19593 | 0.00085188 | 0.0002135
5 | 0.97504 | -0.17529 | 0 | 0
6 | 0.98458 | -0.10757 | 0 | 0
7 | 0.9835 | -0.11523 | 0.012892 | 0.0032309
8 | 0.98745 | -0.087406 | 0 | 0
9 | 0.98932 | -0.074304 | 0.010844 | 0.0027177
10 | 0.99312 | -0.04775 | 0 | 0
11 | 0.99144 | -0.059609 | 0 | 0
12 | 0.99463 | -0.037214 | 0.0094889 | 0.0023781
13 | 0.99121 | -0.061107 | 0.0085176 | 0.0021347
14 | 0.99 | -0.06972 | 0.003516 | 0.00088118
15 | 0.99012 | -0.068739 | 0.027889 | 0.0069896
16 | 0.99601 | -0.027613 | 0.0095312 | 0.0023887
17 | 0.98937 | -0.07423 | 0.0068398 | 0.0017142
18 | 0.99834 | -0.011481 | 0.003235 | 0.00081078
19 | 0.9892 | -0.0754 | 0.0074124 | 0.0018577
20 | 1 | 0 | -0.20093 | -0.050473
21 | 0.9988 | -0.0084005 | 0.0036347 | 0.00091093
22 | 0.99847 | -0.010694 | 0.0062127 | 0.001557
23 | 0.99712 | -0.020141 | 0.0056899 | 0.001426
24 | 0.9964 | -0.025201 | 0.0031522 | 0.00079002
25 | 0.99607 | -0.027496 | 0.0048975 | 0.0012274
26 | 0.99566 | -0.030412 | 0.0035625 | 0.00089284
27 | 0.9953 | -0.032901 | 0.002469 | 0.00061878
28 | 0.98908 | -0.076256 | 0.0036603 | 0.00091736
29 | 0.99513 | -0.034096 | 0.0028999 | 0.00072677
30 | 0.99281 | -0.050418 | 0.0047125 | 0.0011811
31 | 0.99269 | -0.051316 | 0.0044101 | 0.0011053
32 | 0.99262 | -0.051769 | 0.0033701 | 0.00084463
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.005731 | -0.0014359 | 0.0057316 | 0.001436 | 5.8533e-07 | 7.3927e-08 | 0.0087714 | 0.0087714 | 0.0087714 | 0.97221 | -0.19564 | 0.97231 | -0.19491 | 3.2487
1 | 0.00085192 | 0.00021312 | -0.0008519 | -0.00021333 | 1.914e-08 | -2.1638e-07 | 0.0013038 | 0.0013038 | 0.0013038 | 0.97221 | -0.19564 | 0.97218 | -0.19581 | 0.48291
2 | -0.017271 | -0.0043281 | 0.017278 | 0.0043304 | 6.4617e-06 | 2.3013e-06 | 0.026432 | 0.026432 | 0.026432 | 0.97231 | -0.19491 | 0.97268 | -0.1922 | 9.7895
3 | 0.0008519 | 0.00021333 | -0.00085188 | -0.0002135 | 1.4998e-08 | -1.6953e-07 | 0.0013038 | 0.0013039 | 0.0013039 | 0.97218 | -0.19581 | 0.97217 | -0.19593 | 0.48293
4 | -0.048798 | -0.01223 | 0.048913 | 0.012274 | 0.00011453 | 4.364e-05 | 0.074652 | 0.074651 | 0.074652 | 0.97268 | -0.1922 | 0.97504 | -0.17529 | 27.6487
5 | -0.048913 | -0.012274 | 0.049377 | 0.012446 | 0.00046394 | 0.00017172 | 0.074651 | 0.074649 | 0.074651 | 0.97504 | -0.17529 | 0.98458 | -0.10757 | 13.8243
6 | 0.012905 | 0.0032354 | -0.012892 | -0.0032309 | 1.3679e-05 | 4.5291e-06 | 0.019504 | 0.019505 | 0.019505 | 0.98458 | -0.10757 | 0.9835 | -0.11523 | 7.2239
7 | -0.062282 | -0.015681 | 0.062458 | 0.015747 | 0.00017595 | 6.605e-05 | 0.094153 | 0.094153 | 0.094153 | 0.98458 | -0.10757 | 0.98745 | -0.087406 | 17.4358
8 | -0.062458 | -0.015747 | 0.062573 | 0.01579 | 0.00011486 | 4.3111e-05 | 0.094153 | 0.094152 | 0.094153 | 0.98745 | -0.087406 | 0.98932 | -0.074304 | 17.4357
9 | -0.073416 | -0.018508 | 0.073473 | 0.018529 | 5.7274e-05 | 2.1642e-05 | 0.11046 | 0.11046 | 0.11046 | 0.98932 | -0.074304 | 0.99012 | -0.068739 | 20.4559
10 | 0.021507 | 0.0053988 | -0.021472 | -0.0053859 | 3.5364e-05 | 1.2897e-05 | 0.032228 | 0.032228 | 0.032228 | 0.99312 | -0.04775 | 0.99144 | -0.059609 | 11.9363
11 | -0.1317 | -0.033172 | 0.1319 | 0.033247 | 0.00019433 | 7.4326e-05 | 0.19739 | 0.19739 | 0.19739 | 0.99312 | -0.04775 | 0.99463 | -0.037214 | 36.5535
12 | 0.11019 | 0.027773 | -0.10999 | -0.027695 | 0.00020568 | 7.8484e-05 | 0.16516 | 0.16516 | 0.16516 | 0.99312 | -0.04775 | 0.99121 | -0.061107 | 30.5854
13 | 0.021472 | 0.0053859 | -0.021442 | -0.0053749 | 3.0066e-05 | 1.0966e-05 | 0.032228 | 0.032228 | 0.032228 | 0.99144 | -0.059609 | 0.99 | -0.06972 | 11.9364
14 | -0.14138 | -0.035625 | 0.14157 | 0.035697 | 0.00019019 | 7.2798e-05 | 0.21158 | 0.21158 | 0.21158 | 0.99463 | -0.037214 | 0.99601 | -0.027613 | 39.1824
15 | 0.10147 | 0.02556 | -0.10136 | -0.025519 | 0.00010819 | 4.1229e-05 | 0.15237 | 0.15237 | 0.15237 | 0.99121 | -0.061107 | 0.99012 | -0.068739 | 28.2175
16 | 0.017926 | 0.0044937 | -0.017915 | -0.0044897 | 1.1191e-05 | 3.9869e-06 | 0.026944 | 0.026944 | 0.026944 | 0.99 | -0.06972 | 0.98937 | -0.07423 | 9.9792
17 | -0.15111 | -0.038086 | 0.15145 | 0.038217 | 0.00034212 | 0.00013102 | 0.22582 | 0.22582 | 0.22582 | 0.99601 | -0.027613 | 0.99834 | -0.011481 | 41.8193
18 | 0.011075 | 0.0027755 | -0.011073 | -0.0027749 | 1.7935e-06 | 5.568e-07 | 0.016657 | 0.016657 | 0.016657 | 0.98937 | -0.07423 | 0.9892 | -0.0754 | 6.1692
19 | -0.15468 | -0.039028 | 0.15493 | 0.039124 | 0.00024961 | 9.5608e-05 | 0.23065 | 0.23065 | 0.23065 | 0.99834 | -0.011481 | 1 | 0 | 42.7121
20 | 0.0036607 | 0.00091723 | -0.0036603 | -0.00091736 | 4.3343e-07 | -1.2732e-07 | 0.0055066 | 0.0055067 | 0.0055067 | 0.9892 | -0.0754 | 0.98908 | -0.076256 | 2.0395
21 | 0.045199 | 0.01135 | -0.045146 | -0.01133 | 5.2703e-05 | 2.0026e-05 | 0.067265 | 0.067265 | 0.067265 | 1 | 0 | 0.9988 | -0.0084005 | 24.9128
22 | 0.041512 | 0.010419 | -0.041498 | -0.010414 | 1.3214e-05 | 5.0099e-06 | 0.06185 | 0.06185 | 0.06185 | 0.9988 | -0.0084005 | 0.99847 | -0.010694 | 22.9073
23 | 0.035286 | 0.0088567 | -0.03524 | -0.0088393 | 4.6225e-05 | 1.7429e-05 | 0.052591 | 0.052591 | 0.052591 | 0.99847 | -0.010694 | 0.99712 | -0.020141 | 19.4782
24 | 0.02955 | 0.0074132 | -0.029529 | -0.0074055 | 2.0727e-05 | 7.7492e-06 | 0.0441 | 0.0441 | 0.0441 | 0.99712 | -0.020141 | 0.9964 | -0.025201 | 16.3334
25 | 0.026377 | 0.0066155 | -0.026368 | -0.0066124 | 8.388e-06 | 3.1134e-06 | 0.039393 | 0.039393 | 0.039393 | 0.9964 | -0.025201 | 0.99607 | -0.027496 | 14.5899
26 | 0.021471 | 0.0053849 | -0.021462 | -0.0053818 | 8.6764e-06 | 3.1612e-06 | 0.032076 | 0.032076 | 0.032076 | 0.99607 | -0.027496 | 0.99566 | -0.030412 | 11.8802
27 | 0.0179 | 0.0044889 | -0.017894 | -0.0044867 | 6.1738e-06 | 2.1948e-06 | 0.026752 | 0.026752 | 0.026752 | 0.99566 | -0.030412 | 0.9953 | -0.032901 | 9.9083
28 | 0.015425 | 0.003868 | -0.015422 | -0.0038671 | 2.555e-06 | 8.8264e-07 | 0.023061 | 0.023061 | 0.023061 | 0.9953 | -0.032901 | 0.99513 | -0.034096 | 8.5412
29 | 0.012522 | 0.0031403 | -0.012494 | -0.0031311 | 2.8278e-05 | 9.2011e-06 | 0.018725 | 0.018726 | 0.018726 | 0.99513 | -0.034096 | 0.99281 | -0.050418 | 6.9354
30 | 0.0077814 | 0.00195 | -0.0077804 | -0.0019498 | 9.6753e-07 | 2.2473e-07 | 0.011663 | 0.011663 | 0.011663 | 0.99281 | -0.050418 | 0.99269 | -0.051316 | 4.3195
31 | 0.0033703 | 0.00084454 | -0.0033701 | -0.00084463 | 2.1113e-07 | -9.0168e-08 | 0.005052 | 0.0050521 | 0.0050521 | 0.99269 | -0.051316 | 0.99262 | -0.051769 | 1.8711

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23082 | 0.057964

## res_load
| p_mw | q_mvar
0 | 0.0048791 | 0.0012228
1 | 0.01154 | 0.0028921
2 | 0.03152 | 0.0078997
3 | 0.00085188 | 0.0002135
4 | 0.012892 | 0.0032309
5 | 0.010844 | 0.0027177
6 | 0.0094889 | 0.0023781
7 | 0.0085176 | 0.0021347
8 | 0.003516 | 0.00088118
9 | 0.027889 | 0.0069896
10 | 0.0095312 | 0.0023887
11 | 0.0068398 | 0.0017142
12 | 0.003235 | 0.00081078
13 | 0.0074124 | 0.0018577
14 | 0.029887 | 0.0074903
15 | 0.0036347 | 0.00091093
16 | 0.0062127 | 0.001557
17 | 0.0056899 | 0.001426
18 | 0.0031522 | 0.00079002
19 | 0.0048975 | 0.0012274
20 | 0.0035625 | 0.00089284
21 | 0.002469 | 0.00061878
22 | 0.0036603 | 0.00091736
23 | 0.0028999 | 0.00072677
24 | 0.0047125 | 0.0011811
25 | 0.0044101 | 0.0011053
26 | 0.0033701 | 0.00084463

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1