## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1373-3_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1373-3_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1373-3_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1373-3_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1373-3_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1373-3_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1373-3_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1373-3_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1373-3_0_2_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1373-3_0_2_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1373-3_0_2_node_53 | 0.4 | n |  | TRUE
11 | bus_LV_1373-3_0_2_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1373-3_0_2_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1373-3_0_2_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1373-3_0_2_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_1373-3_0_2_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1373-3_0_2_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_1373-3_0_2_node_43 | 0.4 | n |  | TRUE
18 | bus_LV_1373-3_0_2_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_1373-3_0_2_node_45 | 0.4 | n |  | TRUE
20 | bus_LV_1373-3_0_2_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_1373-3_0_2_node_47 | 0.4 | n |  | TRUE
22 | bus_LV_1373-3_0_2_node_48 | 0.4 | n |  | TRUE
23 | bus_LV_1373-3_0_2_node_49 | 0.4 | n |  | TRUE
24 | bus_LV_1373-3_0_2_node_56 | 0.4 | n |  | TRUE
25 | bus_LV_1373-3_0_2_node_57 | 0.4 | n |  | TRUE
26 | bus_LV_1373-3_0_2_node_50 | 0.4 | n |  | TRUE
27 | bus_LV_1373-3_0_2_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_1373-3_0_2_node_55 | 0.4 | n |  | TRUE
29 | bus_LV_1373-3_0_2_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_1373-3_0_2_node_52 | 0.4 | n |  | TRUE
31 | bus_MV_127_0_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1373-3_0_2_load_0 | 0 | 0.011476 | 0.0028761 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1373-3_0_2_load_4 | 4 | 0.011638 | 0.0029167 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1373-3_0_2_load_5 | 5 | 0.021803 | 0.0054643 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1373-3_0_2_load_7 | 7 | 0.010411 | 0.0026091 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1373-3_0_2_load_13 | 8 | 0.00076891 | 0.00019271 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1373-3_0_2_load_11 | 11 | 0.026301 | 0.0065916 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1373-3_0_2_load_8 | 12 | 0.012733 | 0.0031912 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1373-3_0_2_load_12 | 13 | 0.0015591 | 0.00039074 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1373-3_0_2_load_51 | 14 | 0.00027938 | 7.002e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1373-3_0_2_load_33 | 16 | 0.007946 | 0.0019915 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1373-3_0_2_load_43 | 17 | 0.00038165 | 9.565e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1373-3_0_2_load_46 | 20 | 0.00069924 | 0.00017524 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1373-3_0_2_load_47 | 21 | 0.00043536 | 0.00010911 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1373-3_0_2_load_48 | 22 | 0.00051154 | 0.0001282 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1373-3_0_2_load_49 | 23 | 0.00038813 | 9.7274e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1373-3_0_2_load_56 | 24 | 0.00048558 | 0.0001217 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1373-3_0_2_load_57 | 25 | 0.00085626 | 0.0002146 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1373-3_0_2_load_50 | 26 | 0.00065838 | 0.00016501 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1373-3_0_2_load_58 | 27 | 0.00054832 | 0.00013742 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1373-3_0_2_load_55 | 28 | 0.00024614 | 6.1688e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1373-3_0_2_load_54 | 29 | 0.00020794 | 5.2114e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1373-3_0_2_load_52 | 30 | 0.00018756 | 4.7007e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1373-3_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.013699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1373-3_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.036884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1373-3_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.039272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1373-3_0_2_line_3 | NAYY 4x150 SE | 1 | 4 | 0.028665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1373-3_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.019997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1373-3_0_2_line_5 | NAYY 4x150 SE | 2 | 6 | 0.11658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1373-3_0_2_line_6 | NAYY 4x150 SE | 3 | 7 | 0.0078018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1373-3_0_2_line_7 | NAYY 4x150 SE | 4 | 8 | 0.023083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1373-3_0_2_line_8 | NAYY 4x150 SE | 5 | 9 | 0.030843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1373-3_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.18129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1373-3_0_2_line_10 | NAYY 4x150 SE | 7 | 12 | 0.009132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1373-3_0_2_line_11 | NAYY 4x150 SE | 8 | 13 | 0.050236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1373-3_0_2_line_12 | NAYY 4x150 SE | 9 | 11 | 0.035991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1373-3_0_2_line_13 | NAYY 4x150 SE | 10 | 14 | 0.18133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1373-3_0_2_line_14 | NAYY 4x150 SE | 11 | 15 | 0.043229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1373-3_0_2_line_15 | NAYY 4x150 SE | 14 | 30 | 0.0049417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1373-3_0_2_line_16 | NAYY 4x150 SE | 15 | 16 | 0.22179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1373-3_0_2_line_17 | NAYY 4x150 SE | 17 | 18 | 0.036335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1373-3_0_2_line_18 | NAYY 4x150 SE | 17 | 19 | 0.0051344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1373-3_0_2_line_19 | NAYY 4x150 SE | 18 | 20 | 0.011414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1373-3_0_2_line_20 | NAYY 4x150 SE | 19 | 21 | 0.058274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1373-3_0_2_line_21 | NAYY 4x150 SE | 19 | 22 | 0.051959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1373-3_0_2_line_22 | NAYY 4x150 SE | 20 | 23 | 0.026481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1373-3_0_2_line_23 | NAYY 4x150 SE | 21 | 24 | 0.047669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1373-3_0_2_line_24 | NAYY 4x150 SE | 22 | 25 | 0.0017107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1373-3_0_2_line_25 | NAYY 4x150 SE | 23 | 26 | 0.021853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1373-3_0_2_line_26 | NAYY 4x150 SE | 25 | 27 | 0.067218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1373-3_0_2_line_27 | NAYY 4x150 SE | 26 | 28 | 0.050613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1373-3_0_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.032107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1373-3_0_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.0083215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1373-3_0_2_trafo_11 | 0.25 MVA 20/0.4 kV | 31 | 11 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2688607.2265 | 1210577.7304 | 2688620.0811 | 1210577.1098 | 2688620.5405 | 1210577.8003
1 | 2688640.9725 | 1210608.5076 | 2688620.5405 | 1210577.8003
2 | 2688607.2265 | 1210577.7304 | 2688628.5057 | 1210544.6911
3 | 2688607.2265 | 1210577.7304 | 2688588.8648 | 1210599.7429
4 | 2688640.9725 | 1210608.5076 | 2688651.2221 | 1210591.3376
5 | 2688640.9725 | 1210608.5076 | 2688649.0167 | 1210620.6018 | 2688706.8061 | 1210704.8388
6 | 2688628.5057 | 1210544.6911 | 2688631.7425 | 1210539.6581 | 2688632.5619 | 1210538.0354
7 | 2688588.8648 | 1210599.7429 | 2688576.9222 | 1210614.0601 | 2688573.3394 | 1210616.6811
8 | 2688667.0309 | 1210564.8547 | 2688651.2221 | 1210591.3376
9 | 2688706.8061 | 1210704.8388 | 2688758.9224 | 1210727.8958 | 2688775.3218 | 1210734.711 | 2688793.732 | 1210744.3024 | 2688828.6043 | 1210769.7606 | 2688857.699 | 1210800.8811
10 | 2688632.5619 | 1210538.0354 | 2688636.6782 | 1210529.8837
11 | 2688530.048 | 1210640.9991 | 2688548.3215 | 1210634.9828 | 2688573.3394 | 1210616.6811
12 | 2688667.0309 | 1210564.8547 | 2688683.2749 | 1210573.9799 | 2688692.2029 | 1210559.0928
13 | 2688857.699 | 1210800.8811 | 2688945.6328 | 1210865.8679 | 2689003.2914 | 1210908.9718
14 | 2688714.4359 | 1210522.0197 | 2688692.2029 | 1210559.0928
15 | 2689003.2914 | 1210908.9718 | 2689007.2494 | 1210911.9306
16 | 2688714.4359 | 1210522.0197 | 2688843.1721 | 1210341.4208
17 | 2689109.8772 | 1211020.5326 | 2689114.8299 | 1211016.137 | 2689124.4652 | 1210988.0297
18 | 2689126.1301 | 1210983.1727 | 2689124.4652 | 1210988.0297
19 | 2689109.8772 | 1211020.5326 | 2689102.4034 | 1211011.9061
20 | 2689126.1301 | 1210983.1727 | 2689117.1615 | 1210967.9397 | 2689094.4909 | 1210934.2621
21 | 2689126.1301 | 1210983.1727 | 2689157.2355 | 1210961.4897 | 2689165.8233 | 1210950.3797
22 | 2689102.4034 | 1211011.9061 | 2689085.0636 | 1210991.8919
23 | 2689079.7913 | 1210889.2749 | 2689090.2607 | 1210927.978 | 2689094.4909 | 1210934.2621
24 | 2689166.8694 | 1210949.0263 | 2689165.8233 | 1210950.3797
25 | 2689072.5666 | 1210974.0294 | 2689080.6192 | 1210986.7621 | 2689085.0636 | 1210991.8919
26 | 2689166.8694 | 1210949.0263 | 2689170.1242 | 1210944.8156 | 2689192.1663 | 1210888.8523 | 2689192.7126 | 1210887.1912
27 | 2689039.2187 | 1210936.6464 | 2689060.8986 | 1210955.5803 | 2689072.5666 | 1210974.0294
28 | 2689013.9143 | 1210916.9131 | 2689032.7268 | 1210930.9768 | 2689039.2187 | 1210936.6464
29 | 2689013.9143 | 1210916.9131 | 2689007.2494 | 1210911.9306

## bus_geodata
| x | y | coords
0 | 2688620.5405 | 1210577.8003
1 | 2688607.2265 | 1210577.7304
2 | 2688640.9725 | 1210608.5076
3 | 2688628.5057 | 1210544.6911
4 | 2688588.8648 | 1210599.7429
5 | 2688651.2221 | 1210591.3376
6 | 2688706.8061 | 1210704.8388
7 | 2688632.5619 | 1210538.0354
8 | 2688573.3394 | 1210616.6811
9 | 2688667.0309 | 1210564.8547
10 | 2688857.699 | 1210800.8811
11 | 2688692.2029 | 1210559.0928
12 | 2688636.6782 | 1210529.8837
13 | 2688530.048 | 1210640.9991
14 | 2689003.2914 | 1210908.9718
15 | 2688714.4359 | 1210522.0197
16 | 2688843.1721 | 1210341.4208
17 | 2689124.4652 | 1210988.0297
18 | 2689109.8772 | 1211020.5326
19 | 2689126.1301 | 1210983.1727
20 | 2689102.4034 | 1211011.9061
21 | 2689094.4909 | 1210934.2621
22 | 2689165.8233 | 1210950.3797
23 | 2689085.0636 | 1210991.8919
24 | 2689079.7913 | 1210889.2749
25 | 2689166.8694 | 1210949.0263
26 | 2689072.5666 | 1210974.0294
27 | 2689192.7126 | 1210887.1912
28 | 2689039.2187 | 1210936.6464
29 | 2689013.9143 | 1210916.9131
30 | 2689007.2494 | 1210911.9306
31 | 2688667.0309 | 1210564.8547

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98849 | -0.080661 | 0.011476 | 0.0028761
1 | 0.98775 | -0.085859 | 0 | 0
2 | 0.99108 | -0.062398 | 0 | 0
3 | 0.98644 | -0.09517 | 0 | 0
4 | 0.98718 | -0.089959 | 0.011638 | 0.0029167
5 | 0.99265 | -0.051327 | 0.021803 | 0.0054643
6 | 0.99009 | -0.069473 | 0 | 0
7 | 0.98618 | -0.097023 | 0.010411 | 0.0026091
8 | 0.9871 | -0.090511 | 0.00076891 | 0.00019271
9 | 0.99604 | -0.027547 | 0 | 0
10 | 0.98854 | -0.080475 | 0 | 0
11 | 1 | 0 | -0.085902 | -0.021428
12 | 0.98601 | -0.098217 | 0.012733 | 0.0031912
13 | 0.98699 | -0.091315 | 0.0015591 | 0.00039074
14 | 0.987 | -0.091483 | 0.00027938 | 7.002e-05
15 | 0.99951 | -0.0034401 | 0 | 0
16 | 0.99699 | -0.021114 | 0.007946 | 0.0019915
17 | 0.98578 | -0.10019 | 0.00038165 | 9.565e-05
18 | 0.98595 | -0.09898 | 0 | 0
19 | 0.98576 | -0.10034 | 0 | 0
20 | 0.98601 | -0.0986 | 0.00069924 | 0.00017524
21 | 0.98568 | -0.1009 | 0.00043536 | 0.00010911
22 | 0.98562 | -0.10137 | 0.00051154 | 0.0001282
23 | 0.98616 | -0.097528 | 0.00038813 | 9.7274e-05
24 | 0.98565 | -0.10114 | 0.00048558 | 0.0001217
25 | 0.98561 | -0.10139 | 0.00085626 | 0.0002146
26 | 0.98629 | -0.096555 | 0.00065838 | 0.00016501
27 | 0.98556 | -0.10177 | 0.00054832 | 0.00013742
28 | 0.98665 | -0.093961 | 0.00024614 | 6.1688e-05
29 | 0.9869 | -0.092234 | 0.00020794 | 5.2114e-05
30 | 0.98696 | -0.091768 | 0.00018756 | 4.7007e-05
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.037182 | 0.0093263 | -0.037155 | -0.0093162 | 2.6783e-05 | 1.0126e-05 | 0.055975 | 0.055975 | 0.055975 | 0.98849 | -0.080661 | 0.98775 | -0.085859 | 20.7314
1 | -0.048658 | -0.012202 | 0.048781 | 0.012249 | 0.00012349 | 4.7021e-05 | 0.073249 | 0.073249 | 0.073249 | 0.98849 | -0.080661 | 0.99108 | -0.062398 | 27.1294
2 | 0.023181 | 0.0058142 | -0.023152 | -0.0058032 | 2.9889e-05 | 1.0994e-05 | 0.034924 | 0.034924 | 0.034924 | 0.98775 | -0.085859 | 0.98644 | -0.09517 | 12.9347
3 | 0.013974 | 0.003502 | -0.013966 | -0.0034993 | 7.9268e-06 | 2.6821e-06 | 0.021051 | 0.021051 | 0.021051 | 0.98775 | -0.085859 | 0.98718 | -0.089959 | 7.7968
4 | -0.054696 | -0.013724 | 0.05478 | 0.013756 | 8.4161e-05 | 3.2112e-05 | 0.082127 | 0.082127 | 0.082127 | 0.99108 | -0.062398 | 0.99265 | -0.051327 | 30.4175
5 | 0.0059149 | 0.0014748 | -0.0059092 | -0.0014741 | 5.7343e-06 | 7.047e-07 | 0.0088781 | 0.0088786 | 0.0088786 | 0.99108 | -0.062398 | 0.99009 | -0.069473 | 3.2884
6 | 0.023152 | 0.0058032 | -0.023146 | -0.005801 | 5.9378e-06 | 2.1842e-06 | 0.034924 | 0.034924 | 0.034924 | 0.98644 | -0.09517 | 0.98618 | -0.097023 | 12.9347
7 | 0.0023283 | 0.00058264 | -0.0023281 | -0.00058287 | 1.7739e-07 | -2.2687e-07 | 0.0035093 | 0.0035094 | 0.0035094 | 0.98718 | -0.089959 | 0.9871 | -0.090511 | 1.2998
8 | -0.076583 | -0.019221 | 0.076837 | 0.019318 | 0.00025369 | 9.7171e-05 | 0.11481 | 0.11481 | 0.11481 | 0.99265 | -0.051327 | 0.99604 | -0.027547 | 42.5223
9 | 0.0059092 | 0.0014741 | -0.0059003 | -0.001473 | 8.9182e-06 | 1.1023e-06 | 0.0088786 | 0.0088794 | 0.0088794 | 0.99009 | -0.069473 | 0.98854 | -0.080475 | 3.2887
10 | 0.012735 | 0.0031919 | -0.012733 | -0.0031912 | 2.1041e-06 | 6.9276e-07 | 0.019216 | 0.019216 | 0.019216 | 0.98618 | -0.097023 | 0.98601 | -0.098217 | 7.1169
11 | 0.0015592 | 0.00039016 | -0.0015591 | -0.00039074 | 1.7317e-07 | -5.7549e-07 | 0.0023503 | 0.0023505 | 0.0023505 | 0.9871 | -0.090511 | 0.98699 | -0.091315 | 0.87055
12 | -0.076837 | -0.019318 | 0.077133 | 0.019431 | 0.00029603 | 0.00011339 | 0.11481 | 0.11481 | 0.11481 | 0.99604 | -0.027547 | 1 | 0 | 42.5223
13 | 0.0059003 | 0.001473 | -0.0058914 | -0.0014719 | 8.9221e-06 | 1.1105e-06 | 0.0088794 | 0.0088802 | 0.0088802 | 0.98854 | -0.080475 | 0.987 | -0.091483 | 3.289
14 | 0.0079693 | 0.0019969 | -0.0079655 | -0.001996 | 3.7932e-06 | 8.9207e-07 | 0.011858 | 0.011858 | 0.011858 | 1 | 0 | 0.99951 | -0.0034401 | 4.392
15 | 0.005612 | 0.0014019 | -0.0056118 | -0.0014019 | 2.2065e-07 | 2.1711e-08 | 0.008459 | 0.0084591 | 0.0084591 | 0.987 | -0.091483 | 0.98696 | -0.091768 | 3.133
16 | 0.0079655 | 0.001996 | -0.007946 | -0.0019915 | 1.9463e-05 | 4.5863e-06 | 0.011858 | 0.011859 | 0.011859 | 0.99951 | -0.0034401 | 0.99699 | -0.021114 | 4.3924
17 | -0.0032192 | -0.0008039 | 0.0032197 | 0.00080364 | 5.3512e-07 | -2.575e-07 | 0.0048582 | 0.0048581 | 0.0048582 | 0.98578 | -0.10019 | 0.98595 | -0.09898 | 1.7993
18 | 0.0028375 | 0.00070825 | -0.0028375 | -0.00070829 | 5.8749e-08 | -4.2861e-08 | 0.0042821 | 0.0042822 | 0.0042822 | 0.98578 | -0.10019 | 0.98576 | -0.10034 | 1.586
19 | -0.0032197 | -0.00080364 | 0.0032199 | 0.00080356 | 1.6809e-07 | -8.0922e-08 | 0.0048581 | 0.004858 | 0.0048581 | 0.98595 | -0.09898 | 0.98601 | -0.0986 | 1.7993
20 | 0.00092102 | 0.00022949 | -0.00092095 | -0.00023021 | 7.0252e-08 | -7.1582e-07 | 0.0013898 | 0.0013901 | 0.0013901 | 0.98576 | -0.10034 | 0.98568 | -0.1009 | 0.51485
21 | 0.0019164 | 0.0004788 | -0.0019162 | -0.00047936 | 2.7126e-07 | -5.5797e-07 | 0.0028923 | 0.0028926 | 0.0028926 | 0.98576 | -0.10034 | 0.98562 | -0.10137 | 1.0713
22 | -0.0039191 | -0.00097881 | 0.0039197 | 0.00097869 | 5.7778e-07 | -1.1558e-07 | 0.0059132 | 0.0059131 | 0.0059132 | 0.98601 | -0.0986 | 0.98616 | -0.097528 | 2.1901
23 | 0.0004856 | 0.0001211 | -0.00048558 | -0.0001217 | 1.598e-08 | -6.0144e-07 | 0.00073286 | 0.00073307 | 0.00073307 | 0.98568 | -0.1009 | 0.98565 | -0.10114 | 0.27151
24 | 0.0014046 | 0.00035116 | -0.0014046 | -0.00035118 | 4.7989e-09 | -1.9956e-08 | 0.0021203 | 0.0021203 | 0.0021203 | 0.98562 | -0.10137 | 0.98561 | -0.10139 | 0.78529
25 | -0.0043078 | -0.001076 | 0.0043084 | 0.0010759 | 5.759e-07 | -5.7347e-08 | 0.0064988 | 0.0064987 | 0.0064988 | 0.98616 | -0.097528 | 0.98629 | -0.096555 | 2.407
26 | 0.00054835 | 0.00013658 | -0.00054832 | -0.00013742 | 2.8737e-08 | -8.4557e-07 | 0.00082756 | 0.00082787 | 0.00082787 | 0.98561 | -0.10139 | 0.98556 | -0.10177 | 0.30662
27 | -0.0049668 | -0.0012409 | 0.0049685 | 0.001241 | 1.7727e-06 | 3.5629e-08 | 0.007492 | 0.0074917 | 0.007492 | 0.98629 | -0.096555 | 0.98665 | -0.093961 | 2.7748
28 | -0.0052147 | -0.0013026 | 0.0052159 | 0.0013027 | 1.2387e-06 | 6.625e-08 | 0.007863 | 0.0078628 | 0.007863 | 0.98665 | -0.093961 | 0.9869 | -0.092234 | 2.9122
29 | -0.0054238 | -0.0013548 | 0.0054242 | 0.0013548 | 3.4713e-07 | 2.7177e-08 | 0.0081763 | 0.0081763 | 0.0081763 | 0.9869 | -0.092234 | 0.98696 | -0.091768 | 3.0283

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1122 | 0.02802

## res_load
| p_mw | q_mvar
0 | 0.011476 | 0.0028761
1 | 0.011638 | 0.0029167
2 | 0.021803 | 0.0054643
3 | 0.010411 | 0.0026091
4 | 0.00076891 | 0.00019271
5 | 0.026301 | 0.0065916
6 | 0.012733 | 0.0031912
7 | 0.0015591 | 0.00039074
8 | 0.00027938 | 7.002e-05
9 | 0.007946 | 0.0019915
10 | 0.00038165 | 9.565e-05
11 | 0.00069924 | 0.00017524
12 | 0.00043536 | 0.00010911
13 | 0.00051154 | 0.0001282
14 | 0.00038813 | 9.7274e-05
15 | 0.00048558 | 0.0001217
16 | 0.00085626 | 0.0002146
17 | 0.00065838 | 0.00016501
18 | 0.00054832 | 0.00013742
19 | 0.00024614 | 6.1688e-05
20 | 0.00020794 | 5.2114e-05
21 | 0.00018756 | 4.7007e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1