## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1373-3_1_3_node_15 | 0.4 | n |  | TRUE
1 | bus_LV_1373-3_1_3_node_18 | 0.4 | n |  | TRUE
2 | bus_LV_1373-3_1_3_node_42 | 0.4 | n |  | TRUE
3 | bus_LV_1373-3_1_3_node_16 | 0.4 | n |  | TRUE
4 | bus_LV_1373-3_1_3_node_17 | 0.4 | n |  | TRUE
5 | bus_LV_1373-3_1_3_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1373-3_1_3_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1373-3_1_3_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_1373-3_1_3_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_1373-3_1_3_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1373-3_1_3_node_32 | 0.4 | n |  | TRUE
11 | bus_LV_1373-3_1_3_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_1373-3_1_3_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_1373-3_1_3_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_1373-3_1_3_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_1373-3_1_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1373-3_1_3_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_1373-3_1_3_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_1373-3_1_3_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_1373-3_1_3_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_1373-3_1_3_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_1373-3_1_3_node_37 | 0.4 | n |  | TRUE
22 | bus_LV_1373-3_1_3_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_1373-3_1_3_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_1373-3_1_3_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1373-3_1_3_node_41 | 0.4 | n |  | TRUE
26 | bus_MV_127_0_node_100 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1373-3_1_3_load_42 | 2 | 0.0036947 | 0.00092599 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1373-3_1_3_load_16 | 3 | 0.023337 | 0.0058487 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1373-3_1_3_load_19 | 5 | 0.0055914 | 0.0014013 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1373-3_1_3_load_20 | 6 | 0.00042773 | 0.0001072 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1373-3_1_3_load_21 | 7 | 0.0087068 | 0.0021821 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1373-3_1_3_load_22 | 8 | 0.0054264 | 0.00136 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1373-3_1_3_load_26 | 9 | 0.0064482 | 0.0016161 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1373-3_1_3_load_32 | 10 | 0.0010164 | 0.00025474 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1373-3_1_3_load_25 | 12 | 0.0025853 | 0.00064793 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1373-3_1_3_load_23 | 13 | 0.0025812 | 0.00064691 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1373-3_1_3_load_27 | 14 | 0.0012382 | 0.00031032 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1373-3_1_3_load_28 | 15 | 0.0029135 | 0.0007302 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1373-3_1_3_load_29 | 16 | 0.0068366 | 0.0017134 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1373-3_1_3_load_30 | 17 | 0.0055433 | 0.0013893 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1373-3_1_3_load_31 | 18 | 0.0083153 | 0.002084 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1373-3_1_3_load_36 | 20 | 0.016747 | 0.0041972 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1373-3_1_3_load_37 | 21 | 0.0047881 | 0.0012 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1373-3_1_3_load_38 | 22 | 0.018108 | 0.0045383 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1373-3_1_3_load_39 | 23 | 0.0016451 | 0.00041231 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1373-3_1_3_load_40 | 24 | 0.00084904 | 0.00021279 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1373-3_1_3_load_41 | 25 | 0.0029441 | 0.00073785 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1373-3_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.094378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1373-3_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.17034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1373-3_1_3_line_2 | NAYY 4x150 SE | 1 | 8 | 0.027562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1373-3_1_3_line_3 | NAYY 4x150 SE | 1 | 3 | 0.013392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1373-3_1_3_line_4 | NAYY 4x150 SE | 2 | 25 | 0.011561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1373-3_1_3_line_5 | NAYY 4x150 SE | 3 | 4 | 0.15576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1373-3_1_3_line_6 | NAYY 4x150 SE | 4 | 5 | 0.073109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1373-3_1_3_line_7 | NAYY 4x150 SE | 4 | 6 | 0.049208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1373-3_1_3_line_8 | NAYY 4x150 SE | 4 | 7 | 0.052425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1373-3_1_3_line_9 | NAYY 4x150 SE | 5 | 9 | 0.11098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1373-3_1_3_line_10 | NAYY 4x150 SE | 6 | 10 | 0.0089577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1373-3_1_3_line_11 | NAYY 4x150 SE | 7 | 11 | 0.17183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1373-3_1_3_line_12 | NAYY 4x150 SE | 8 | 12 | 0.17656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1373-3_1_3_line_13 | NAYY 4x150 SE | 10 | 18 | 0.021436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1373-3_1_3_line_14 | NAYY 4x150 SE | 11 | 13 | 0.18522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1373-3_1_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.02073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1373-3_1_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.017532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1373-3_1_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.027339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1373-3_1_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.02539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1373-3_1_3_line_19 | NAYY 4x150 SE | 17 | 19 | 0.0095899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1373-3_1_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.055889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1373-3_1_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.018298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1373-3_1_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.11168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1373-3_1_3_line_23 | NAYY 4x150 SE | 23 | 24 | 0.017826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1373-3_1_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.080897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1373-3_1_3_trafo_19 | 0.25 MVA 20/0.4 kV | 26 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2688273.5449 | 1210772.8251 | 2688327.8327 | 1210695.5328
1 | 2688327.8327 | 1210695.5328 | 2688376.4851 | 1210735.9911 | 2688414.0453 | 1210767.3795 | 2688460.1571 | 1210802.7526
2 | 2688273.5449 | 1210772.8251 | 2688252.9601 | 1210754.4968
3 | 2688273.5449 | 1210772.8251 | 2688281.569 | 1210783.5474
4 | 2688469.3302 | 1210809.7895 | 2688460.1571 | 1210802.7526
5 | 2688380.4966 | 1210903.773 | 2688309.2449 | 1210820.5295 | 2688281.569 | 1210783.5474
6 | 2688380.4966 | 1210903.773 | 2688441.9628 | 1210864.1903
7 | 2688380.4966 | 1210903.773 | 2688386.826 | 1210911.0716 | 2688401.2143 | 1210928.9522 | 2688411.0422 | 1210939.1601 | 2688412.9681 | 1210940.6364
8 | 2688380.4966 | 1210903.773 | 2688339.5977 | 1210936.5694
9 | 2688535.2673 | 1210804.1044 | 2688509.5993 | 1210820.6315 | 2688489.9082 | 1210833.3146 | 2688441.9628 | 1210864.1903
10 | 2688412.9681 | 1210940.6364 | 2688420.0775 | 1210946.0858
11 | 2688205.5435 | 1211044.066 | 2688339.5977 | 1210936.5694
12 | 2688111.1511 | 1210649.4508 | 2688130.7464 | 1210665.8544 | 2688249.0369 | 1210751.0037 | 2688252.9601 | 1210754.4968
13 | 2688420.0775 | 1210946.0858 | 2688427.8305 | 1210952.0286 | 2688438.6136 | 1210956.4839
14 | 2688205.5435 | 1211044.066 | 2688172.2158 | 1210973.2042 | 2688125.3679 | 1210877.1007
15 | 2688479.6974 | 1210968.5438 | 2688483.5098 | 1210969.4767 | 2688499.2751 | 1210975.2952
16 | 2688479.6974 | 1210968.5438 | 2688462.6682 | 1210964.3766
17 | 2688524.9231 | 1210984.761 | 2688499.2751 | 1210975.2952
18 | 2688438.6136 | 1210956.4839 | 2688450.5227 | 1210961.4045 | 2688462.6682 | 1210964.3766
19 | 2688533.9198 | 1210988.0813 | 2688524.9231 | 1210984.761
20 | 2688533.9198 | 1210988.0813 | 2688550.5852 | 1210960.577 | 2688550.2729 | 1210954.4795 | 2688537.9117 | 1210945.9904 | 2688539.4499 | 1210943.8586
21 | 2688539.4499 | 1210943.8586 | 2688550.1566 | 1210929.0202
22 | 2688550.1566 | 1210929.0202 | 2688569.4952 | 1210902.2189 | 2688549.2556 | 1210888.3871 | 2688517.8163 | 1210932.4375
23 | 2688544.3871 | 1210872.5423 | 2688537.8702 | 1210867.4042 | 2688530.6237 | 1210861.2192
24 | 2688530.6237 | 1210861.2192 | 2688520.4503 | 1210852.5359 | 2688517.7945 | 1210846.1033 | 2688489.9241 | 1210825.5874 | 2688469.3302 | 1210809.7895

## bus_geodata
| x | y | coords
0 | 2688327.8327 | 1210695.5328
1 | 2688273.5449 | 1210772.8251
2 | 2688460.1571 | 1210802.7526
3 | 2688281.569 | 1210783.5474
4 | 2688380.4966 | 1210903.773
5 | 2688441.9628 | 1210864.1903
6 | 2688412.9681 | 1210940.6364
7 | 2688339.5977 | 1210936.5694
8 | 2688252.9601 | 1210754.4968
9 | 2688535.2673 | 1210804.1044
10 | 2688420.0775 | 1210946.0858
11 | 2688205.5435 | 1211044.066
12 | 2688111.1511 | 1210649.4508
13 | 2688125.3679 | 1210877.1007
14 | 2688479.6974 | 1210968.5438
15 | 2688499.2751 | 1210975.2952
16 | 2688462.6682 | 1210964.3766
17 | 2688524.9231 | 1210984.761
18 | 2688438.6136 | 1210956.4839
19 | 2688533.9198 | 1210988.0813
20 | 2688539.4499 | 1210943.8586
21 | 2688550.1566 | 1210929.0202
22 | 2688517.8163 | 1210932.4375
23 | 2688544.3871 | 1210872.5423
24 | 2688530.6237 | 1210861.2192
25 | 2688469.3302 | 1210809.7895
26 | 2688380.4966 | 1210903.773

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98303 | -0.11898 | 0 | 0
1 | 0.98428 | -0.11006 | 0 | 0
2 | 0.98076 | -0.13511 | 0.0036947 | 0.00092599
3 | 0.98461 | -0.10768 | 0.023337 | 0.0058487
4 | 0.99375 | -0.043267 | 0 | 0
5 | 1 | 0 | -0.12714 | -0.031936
6 | 0.98902 | -0.076229 | 0.00042773 | 0.0001072
7 | 0.9929 | -0.049272 | 0.0087068 | 0.0021821
8 | 0.98396 | -0.11234 | 0.0054264 | 0.00136
9 | 0.99898 | -0.0071552 | 0.0064482 | 0.0016161
10 | 0.98816 | -0.082224 | 0.0010164 | 0.00025474
11 | 0.99226 | -0.053811 | 0 | 0
12 | 0.9833 | -0.11706 | 0.0025853 | 0.00064793
13 | 0.99157 | -0.058677 | 0.0025812 | 0.00064691
14 | 0.9828 | -0.11999 | 0.0012382 | 0.00031032
15 | 0.98134 | -0.13032 | 0.0029135 | 0.0007302
16 | 0.98407 | -0.11106 | 0.0068366 | 0.0017134
17 | 0.97954 | -0.14315 | 0.0055433 | 0.0013893
18 | 0.98615 | -0.096389 | 0.0083153 | 0.002084
19 | 0.97898 | -0.14711 | 0 | 0
20 | 0.97574 | -0.17026 | 0.016747 | 0.0041972
21 | 0.97512 | -0.17466 | 0.0047881 | 0.0012
22 | 0.97216 | -0.19596 | 0.018108 | 0.0045383
23 | 0.98034 | -0.13817 | 0.0016451 | 0.00041231
24 | 0.98038 | -0.13787 | 0.00084904 | 0.00021279
25 | 0.98067 | -0.13577 | 0.0029441 | 0.00073785
26 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0091547 | -0.0022937 | 0.009166 | 0.0022969 | 1.1308e-05 | 3.1513e-06 | 0.013857 | 0.013857 | 0.013857 | 0.98303 | -0.11898 | 0.98428 | -0.11006 | 5.1323
1 | 0.0091547 | 0.0022937 | -0.0091343 | -0.002288 | 2.0412e-05 | 5.6962e-06 | 0.013857 | 0.013858 | 0.013858 | 0.98303 | -0.11898 | 0.98076 | -0.13511 | 5.1326
2 | 0.0080159 | 0.002007 | -0.0080134 | -0.0020063 | 2.5254e-06 | 6.2112e-07 | 0.012118 | 0.012118 | 0.012118 | 0.98428 | -0.11006 | 0.98396 | -0.11234 | 4.4881
3 | -0.017182 | -0.0043038 | 0.017188 | 0.0043058 | 5.6381e-06 | 1.9982e-06 | 0.025975 | 0.025974 | 0.025975 | 0.98428 | -0.11006 | 0.98461 | -0.10768 | 9.6202
4 | 0.0054395 | 0.0013621 | -0.005439 | -0.001362 | 4.9131e-07 | 4.3082e-08 | 0.0082524 | 0.0082525 | 0.0082525 | 0.98076 | -0.13511 | 0.98067 | -0.13577 | 3.0565
5 | -0.040524 | -0.010155 | 0.040889 | 0.010293 | 0.00036455 | 0.00013821 | 0.061242 | 0.061242 | 0.061242 | 0.98461 | -0.10768 | 0.99375 | -0.043267 | 22.6824
6 | -0.11916 | -0.030041 | 0.11989 | 0.030319 | 0.00072673 | 0.00027761 | 0.17849 | 0.17849 | 0.17849 | 0.99375 | -0.043267 | 1 | 0 | 33.0546
7 | 0.066974 | 0.01692 | -0.066665 | -0.016802 | 0.00030911 | 0.00011825 | 0.10033 | 0.10033 | 0.10033 | 0.99375 | -0.043267 | 0.98902 | -0.076229 | 37.1605
8 | 0.011301 | 0.0028286 | -0.011291 | -0.0028257 | 9.3655e-06 | 2.9235e-06 | 0.01692 | 0.01692 | 0.01692 | 0.99375 | -0.043267 | 0.9929 | -0.049272 | 6.2668
9 | 0.0064545 | 0.0016171 | -0.0064482 | -0.0016161 | 6.3881e-06 | 1.0025e-06 | 0.0096043 | 0.0096048 | 0.0096048 | 1 | 0 | 0.99898 | -0.0071552 | 3.5573
10 | 0.066237 | 0.016695 | -0.066182 | -0.016673 | 5.555e-05 | 2.125e-05 | 0.09969 | 0.09969 | 0.09969 | 0.98902 | -0.076229 | 0.98816 | -0.082224 | 36.9221
11 | 0.0025845 | 0.00064358 | -0.0025829 | -0.00064518 | 1.6077e-06 | -1.6026e-06 | 0.0038719 | 0.0038726 | 0.0038726 | 0.9929 | -0.049272 | 0.99226 | -0.053811 | 1.4343
12 | 0.002587 | 0.00064634 | -0.0025853 | -0.00064793 | 1.686e-06 | -1.5926e-06 | 0.0039115 | 0.0039123 | 0.0039123 | 0.98396 | -0.11234 | 0.9833 | -0.11706 | 1.449
13 | 0.065165 | 0.016419 | -0.065036 | -0.016369 | 0.00012888 | 4.9295e-05 | 0.098159 | 0.098159 | 0.098159 | 0.98816 | -0.082224 | 0.98615 | -0.096389 | 36.3553
14 | 0.0025829 | 0.00064518 | -0.0025812 | -0.00064691 | 1.7337e-06 | -1.724e-06 | 0.0038726 | 0.0038735 | 0.0038735 | 0.99226 | -0.053811 | 0.99157 | -0.058677 | 1.4346
15 | 0.048468 | 0.012194 | -0.048398 | -0.012167 | 6.969e-05 | 2.6541e-05 | 0.0734 | 0.0734 | 0.0734 | 0.9828 | -0.11999 | 0.98134 | -0.13032 | 27.1852
16 | -0.049706 | -0.012504 | 0.049768 | 0.012527 | 6.1988e-05 | 2.3619e-05 | 0.075275 | 0.075275 | 0.075275 | 0.9828 | -0.11999 | 0.98407 | -0.11106 | 27.8795
17 | 0.045485 | 0.011437 | -0.045404 | -0.011406 | 8.1179e-05 | 3.0878e-05 | 0.068982 | 0.068982 | 0.068982 | 0.98134 | -0.13032 | 0.97954 | -0.14315 | 25.549
18 | -0.056605 | -0.014241 | 0.056721 | 0.014285 | 0.00011612 | 4.4339e-05 | 0.085612 | 0.085612 | 0.085612 | 0.98407 | -0.11106 | 0.98615 | -0.096389 | 31.7082
19 | 0.03986 | 0.010017 | -0.039838 | -0.010008 | 2.1948e-05 | 8.3208e-06 | 0.060562 | 0.060562 | 0.060562 | 0.97954 | -0.14315 | 0.97898 | -0.14711 | 22.4302
20 | 0.039838 | 0.010008 | -0.039711 | -0.0099598 | 0.00012791 | 4.8496e-05 | 0.060562 | 0.060562 | 0.060562 | 0.97898 | -0.14711 | 0.97574 | -0.17026 | 22.4303
21 | 0.022964 | 0.0057627 | -0.02295 | -0.0057575 | 1.4005e-05 | 5.1582e-06 | 0.035023 | 0.035023 | 0.035023 | 0.97574 | -0.17026 | 0.97512 | -0.17466 | 12.9714
22 | 0.018162 | 0.0045575 | -0.018108 | -0.0045383 | 5.3536e-05 | 1.9202e-05 | 0.027716 | 0.027717 | 0.027717 | 0.97512 | -0.17466 | 0.97216 | -0.19596 | 10.2655
23 | -0.0016451 | -0.00041231 | 0.0016452 | 0.00041211 | 6.9357e-08 | -1.9809e-07 | 0.0024971 | 0.002497 | 0.0024971 | 0.98034 | -0.13817 | 0.98038 | -0.13787 | 0.92485
24 | -0.0024942 | -0.0006249 | 0.002495 | 0.00062416 | 7.2337e-07 | -7.4216e-07 | 0.0037857 | 0.0037853 | 0.0037857 | 0.98038 | -0.13787 | 0.98067 | -0.13577 | 1.4021

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.13274 | 0.033337

## res_load
| p_mw | q_mvar
0 | 0.0036947 | 0.00092599
1 | 0.023337 | 0.0058487
2 | 0.0055914 | 0.0014013
3 | 0.00042773 | 0.0001072
4 | 0.0087068 | 0.0021821
5 | 0.0054264 | 0.00136
6 | 0.0064482 | 0.0016161
7 | 0.0010164 | 0.00025474
8 | 0.0025853 | 0.00064793
9 | 0.0025812 | 0.00064691
10 | 0.0012382 | 0.00031032
11 | 0.0029135 | 0.0007302
12 | 0.0068366 | 0.0017134
13 | 0.0055433 | 0.0013893
14 | 0.0083153 | 0.002084
15 | 0.016747 | 0.0041972
16 | 0.0047881 | 0.0012
17 | 0.018108 | 0.0045383
18 | 0.0016451 | 0.00041231
19 | 0.00084904 | 0.00021279
20 | 0.0029441 | 0.00073785

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1