## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1374-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1374-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1374-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1374-4_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1374-4_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1374-4_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1374-4_0_2_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1374-4_0_2_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1374-4_0_2_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_1374-4_0_2_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_1374-4_0_2_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1374-4_0_2_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_1374-4_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1374-4_0_2_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1374-4_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1374-4_0_2_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_1374-4_0_2_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_1374-4_0_2_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1374-4_0_2_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1374-4_0_2_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1374-4_0_2_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1374-4_0_2_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1374-4_0_2_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1374-4_0_2_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1374-4_0_2_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1374-4_0_2_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1374-4_0_2_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1374-4_0_2_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1374-4_0_2_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1374-4_0_2_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1374-4_0_2_node_40 | 0.4 | n |  | TRUE
31 | bus_LV_1374-4_0_2_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1374-4_0_2_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1374-4_0_2_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_1374-4_0_2_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_1374-4_0_2_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1374-4_0_2_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_1374-4_0_2_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1374-4_0_2_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_1374-4_0_2_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_1374-4_0_2_node_41 | 0.4 | n |  | TRUE
41 | bus_MV_1_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1374-4_0_2_load_0 | 0 | 0.0058241 | 0.0014597 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1374-4_0_2_load_1 | 1 | 0.0025036 | 0.00062746 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1374-4_0_2_load_3 | 3 | 0.0021064 | 0.0005279 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1374-4_0_2_load_4 | 4 | 0.0015812 | 0.00039629 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1374-4_0_2_load_11 | 6 | 0.0031889 | 0.0007992 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1374-4_0_2_load_32 | 7 | 0.0029382 | 0.00073639 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1374-4_0_2_load_33 | 8 | 0.003412 | 0.00085512 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1374-4_0_2_load_34 | 9 | 0.0040806 | 0.0010227 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1374-4_0_2_load_35 | 10 | 0.0026245 | 0.00065775 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1374-4_0_2_load_37 | 11 | 0.00073474 | 0.00018414 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1374-4_0_2_load_7 | 12 | 0.0012313 | 0.00030859 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1374-4_0_2_load_6 | 13 | 0.0014363 | 0.00035998 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1374-4_0_2_load_9 | 14 | 0.0061649 | 0.0015451 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1374-4_0_2_load_36 | 15 | 0.0035126 | 0.00088034 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1374-4_0_2_load_39 | 16 | 0.0037974 | 0.00095171 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1374-4_0_2_load_8 | 17 | 0.0017682 | 0.00044315 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1374-4_0_2_load_12 | 19 | 0.047053 | 0.011793 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1374-4_0_2_load_16 | 22 | 0.025231 | 0.0063236 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1374-4_0_2_load_15 | 23 | 0.0055105 | 0.0013811 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1374-4_0_2_load_20 | 24 | 0.003044 | 0.00076289 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1374-4_0_2_load_17 | 26 | 0.0084608 | 0.0021205 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1374-4_0_2_load_23 | 28 | 0.0064348 | 0.0016127 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1374-4_0_2_load_21 | 29 | 0.0071871 | 0.0018013 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1374-4_0_2_load_40 | 30 | 0.003896 | 0.00097643 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1374-4_0_2_load_24 | 31 | 0.0087301 | 0.002188 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1374-4_0_2_load_22 | 32 | 0.010245 | 0.0025677 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1374-4_0_2_load_42 | 33 | 0.0027066 | 0.00067833 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1374-4_0_2_load_27 | 34 | 0.0026069 | 0.00065335 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1374-4_0_2_load_28 | 35 | 0.0008364 | 0.00020962 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1374-4_0_2_load_29 | 36 | 0.00083551 | 0.0002094 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1374-4_0_2_load_30 | 37 | 0.0033947 | 0.0008508 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1374-4_0_2_load_31 | 38 | 0.004146 | 0.0010391 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1374-4_0_2_load_38 | 39 | 0.00086942 | 0.0002179 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1374-4_0_2_load_41 | 40 | 0.0030297 | 0.00075931 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1374-4_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1374-4_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.059926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1374-4_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.020594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1374-4_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.052366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1374-4_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.06197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1374-4_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.021993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1374-4_0_2_line_6 | NAYY 4x150 SE | 5 | 12 | 0.011188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1374-4_0_2_line_7 | NAYY 4x150 SE | 5 | 13 | 0.041354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1374-4_0_2_line_8 | NAYY 4x150 SE | 6 | 14 | 0.012054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1374-4_0_2_line_9 | NAYY 4x150 SE | 7 | 8 | 0.0084588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1374-4_0_2_line_10 | NAYY 4x150 SE | 7 | 9 | 0.0071581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1374-4_0_2_line_11 | NAYY 4x150 SE | 8 | 10 | 0.012471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1374-4_0_2_line_12 | NAYY 4x150 SE | 9 | 15 | 0.012923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1374-4_0_2_line_13 | NAYY 4x150 SE | 10 | 11 | 0.010209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1374-4_0_2_line_14 | NAYY 4x150 SE | 11 | 39 | 0.0019021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1374-4_0_2_line_15 | NAYY 4x150 SE | 14 | 17 | 0.0090387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1374-4_0_2_line_16 | NAYY 4x150 SE | 15 | 16 | 0.030947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1374-4_0_2_line_17 | NAYY 4x150 SE | 16 | 30 | 0.017503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1374-4_0_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.021856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1374-4_0_2_line_19 | NAYY 4x150 SE | 18 | 19 | 0.020527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1374-4_0_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.027728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1374-4_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.010072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1374-4_0_2_line_22 | NAYY 4x150 SE | 20 | 22 | 0.0091672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1374-4_0_2_line_23 | NAYY 4x150 SE | 21 | 23 | 0.024393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1374-4_0_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.040181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1374-4_0_2_line_25 | NAYY 4x150 SE | 24 | 25 | 0.023973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1374-4_0_2_line_26 | NAYY 4x150 SE | 25 | 27 | 0.006162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1374-4_0_2_line_27 | NAYY 4x150 SE | 25 | 26 | 0.034139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1374-4_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.0075205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1374-4_0_2_line_29 | NAYY 4x150 SE | 27 | 29 | 0.03567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1374-4_0_2_line_30 | NAYY 4x150 SE | 28 | 31 | 0.015157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1374-4_0_2_line_31 | NAYY 4x150 SE | 29 | 32 | 0.031025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1374-4_0_2_line_32 | NAYY 4x150 SE | 30 | 40 | 0.0033054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1374-4_0_2_line_33 | NAYY 4x150 SE | 31 | 33 | 0.040864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1374-4_0_2_line_34 | NAYY 4x150 SE | 33 | 38 | 0.01627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1374-4_0_2_line_35 | NAYY 4x150 SE | 33 | 40 | 0.020536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1374-4_0_2_line_36 | NAYY 4x150 SE | 34 | 35 | 0.0053691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1374-4_0_2_line_37 | NAYY 4x150 SE | 34 | 36 | 0.021517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1374-4_0_2_line_38 | NAYY 4x150 SE | 35 | 37 | 0.013295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1374-4_0_2_line_39 | NAYY 4x150 SE | 36 | 38 | 0.0047364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1374-4_0_2_trafo_15 | 0.25 MVA 20/0.4 kV | 41 | 23 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2687049.0799 | 1212152.7348 | 2687058.474 | 1212141.5971
1 | 2687012.2472 | 1212199.7869 | 2687017.7566 | 1212189.8718 | 2687049.0799 | 1212152.7348
2 | 2687068.8553 | 1212123.8595 | 2687060.0923 | 1212139.6784 | 2687058.474 | 1212141.5971
3 | 2687012.2472 | 1212199.7869 | 2687004.103 | 1212198.1225 | 2686965.0664 | 1212177.4396
4 | 2687012.2472 | 1212199.7869 | 2687001.3768 | 1212219.3524 | 2686991.1293 | 1212232.6785 | 2686984.4923 | 1212236.0395 | 2686969.688 | 1212240.3598
5 | 2687078.4387 | 1212104.0762 | 2687071.4869 | 1212119.1089 | 2687068.8553 | 1212123.8595
6 | 2686969.688 | 1212240.3598 | 2686978.3066 | 1212247.5235
7 | 2686969.688 | 1212240.3598 | 2686960.8129 | 1212242.9544 | 2686951.4106 | 1212246.2751 | 2686943.0063 | 1212252.023 | 2686935.3881 | 1212261.2346
8 | 2687083.4982 | 1212093.1356 | 2687078.4387 | 1212104.0762
9 | 2687118.919 | 1212169.9764 | 2687123.1271 | 1212177.3142
10 | 2687118.919 | 1212169.9764 | 2687117.6156 | 1212167.7034 | 2687116.7098 | 1212164.6882 | 2687116.6122 | 1212163.302
11 | 2687123.1271 | 1212177.3142 | 2687129.3315 | 1212188.1329
12 | 2687116.6122 | 1212163.302 | 2687116.4895 | 1212161.5607 | 2687116.9527 | 1212158.4654 | 2687118.0821 | 1212155.5355 | 2687119.9538 | 1212152.7721 | 2687121.1097 | 1212151.7097
13 | 2687134.4103 | 1212196.989 | 2687129.3315 | 1212188.1329
14 | 2687134.4103 | 1212196.989 | 2687135.3566 | 1212198.6391
15 | 2687083.4982 | 1212093.1356 | 2687084.8576 | 1212090.196 | 2687087.244 | 1212084.9097
16 | 2687121.1097 | 1212151.7097 | 2687122.4185 | 1212150.5066 | 2687125.3374 | 1212148.8815 | 2687128.5575 | 1212147.9613 | 2687150.9606 | 1212149.8065
17 | 2687150.9606 | 1212149.8065 | 2687157.7698 | 1212150.3674 | 2687163.9843 | 1212159.0417
18 | 2687096.2365 | 1212064.9899 | 2687087.244 | 1212084.9097
19 | 2687096.2365 | 1212064.9899 | 2687103.1516 | 1212068.6154 | 2687115.0227 | 1212073.1821
20 | 2687076.785 | 1212045.6375 | 2687084.2543 | 1212056.0646 | 2687093.0641 | 1212062.642 | 2687096.2365 | 1212064.9899
21 | 2687124.4228 | 1212076.7982 | 2687115.0227 | 1212073.1821
22 | 2687076.785 | 1212045.6375 | 2687071.9971 | 1212037.82
23 | 2687124.4228 | 1212076.7982 | 2687147.0871 | 1212085.8182
24 | 2687147.0871 | 1212085.8182 | 2687155.7452 | 1212089.264 | 2687164.106 | 1212093.8002 | 2687171.5107 | 1212098.2336 | 2687177.7447 | 1212103.228 | 2687181.1289 | 1212106.5351
25 | 2687196.1948 | 1212125.0343 | 2687195.4101 | 1212123.6108 | 2687188.1057 | 1212113.3528 | 2687181.1289 | 1212106.5351
26 | 2687199.1858 | 1212130.4261 | 2687196.1948 | 1212125.0343
27 | 2687196.1948 | 1212125.0343 | 2687203.0927 | 1212122.5557 | 2687213.1082 | 1212114.2189 | 2687223.231 | 1212104.8723
28 | 2687199.1858 | 1212130.4261 | 2687201.5698 | 1212134.7193 | 2687202.4645 | 1212137.1709
29 | 2687199.1858 | 1212130.4261 | 2687215.0556 | 1212124.9878 | 2687221.2075 | 1212126.7567 | 2687226.4376 | 1212134.3938 | 2687227.9245 | 1212137.2685
30 | 2687206.595 | 1212151.7114 | 2687205.0985 | 1212144.3884 | 2687202.4645 | 1212137.1709
31 | 2687227.9245 | 1212137.2685 | 2687237.0935 | 1212154.9966 | 2687241.6777 | 1212165.0684
32 | 2687163.9843 | 1212159.0417 | 2687165.9093 | 1212161.7287
33 | 2687206.595 | 1212151.7114 | 2687176.2693 | 1212179.1008
34 | 2687178.0791 | 1212195.1836 | 2687178.2958 | 1212190.2493 | 2687176.2693 | 1212179.1008
35 | 2687165.9093 | 1212161.7287 | 2687175.56 | 1212175.1994 | 2687176.2693 | 1212179.1008
36 | 2687170.7585 | 1212219.9722 | 2687168.595 | 1212224.8861 | 2687168.595 | 1212224.8861
37 | 2687170.7585 | 1212219.9722 | 2687177.6808 | 1212204.2496 | 2687177.8712 | 1212199.9154
38 | 2687168.595 | 1212224.8861 | 2687167.9352 | 1212229.9909 | 2687168.2478 | 1212235.1211 | 2687168.9868 | 1212238.037
39 | 2687178.0791 | 1212195.1836 | 2687177.8712 | 1212199.9154

## bus_geodata
| x | y | coords
0 | 2687049.0799 | 1212152.7348
1 | 2687058.474 | 1212141.5971
2 | 2687012.2472 | 1212199.7869
3 | 2687068.8553 | 1212123.8595
4 | 2686965.0665 | 1212177.4396
5 | 2686969.688 | 1212240.3598
6 | 2687078.4387 | 1212104.0762
7 | 2687118.919 | 1212169.9764
8 | 2687123.1271 | 1212177.3142
9 | 2687116.6122 | 1212163.302
10 | 2687129.3315 | 1212188.1329
11 | 2687134.4103 | 1212196.989
12 | 2686978.3066 | 1212247.5235
13 | 2686935.3881 | 1212261.2346
14 | 2687083.4982 | 1212093.1356
15 | 2687121.1097 | 1212151.7097
16 | 2687150.9606 | 1212149.8065
17 | 2687087.244 | 1212084.9097
18 | 2687096.2365 | 1212064.9899
19 | 2687115.0227 | 1212073.1821
20 | 2687076.785 | 1212045.6375
21 | 2687124.4228 | 1212076.7982
22 | 2687071.9971 | 1212037.82
23 | 2687147.0871 | 1212085.8182
24 | 2687181.1289 | 1212106.5351
25 | 2687196.1948 | 1212125.0343
26 | 2687223.231 | 1212104.8723
27 | 2687199.1858 | 1212130.4261
28 | 2687202.4645 | 1212137.1709
29 | 2687227.9245 | 1212137.2685
30 | 2687163.9843 | 1212159.0417
31 | 2687206.595 | 1212151.7114
32 | 2687241.6777 | 1212165.0684
33 | 2687176.2693 | 1212179.1008
34 | 2687170.7585 | 1212219.9722
35 | 2687168.595 | 1212224.8861
36 | 2687177.8712 | 1212199.9154
37 | 2687168.9868 | 1212238.037
38 | 2687178.0791 | 1212195.1836
39 | 2687135.3566 | 1212198.6391
40 | 2687165.9093 | 1212161.7287
41 | 2687124.4228 | 1212076.7982

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99116 | -0.06201 | 0.0058241 | 0.0014597
1 | 0.99138 | -0.060516 | 0.0025036 | 0.00062746
2 | 0.9908 | -0.064609 | 0 | 0
3 | 0.99175 | -0.057882 | 0.0021064 | 0.0005279
4 | 0.99068 | -0.065452 | 0.0015812 | 0.00039629
5 | 0.99056 | -0.066295 | 0 | 0
6 | 0.99221 | -0.054601 | 0.0031889 | 0.0007992
7 | 0.98424 | -0.11064 | 0.0029382 | 0.00073639
8 | 0.98415 | -0.11131 | 0.003412 | 0.00085512
9 | 0.98435 | -0.10986 | 0.0040806 | 0.0010227
10 | 0.98407 | -0.11185 | 0.0026245 | 0.00065775
11 | 0.98405 | -0.11202 | 0.00073474 | 0.00018414
12 | 0.99054 | -0.066436 | 0.0012313 | 0.00030859
13 | 0.99047 | -0.0669 | 0.0014363 | 0.00035998
14 | 0.99252 | -0.052414 | 0.0061649 | 0.0015451
15 | 0.98463 | -0.10791 | 0.0035126 | 0.00088034
16 | 0.98544 | -0.10212 | 0.0037974 | 0.00095171
17 | 0.99283 | -0.050211 | 0.0017682 | 0.00044315
18 | 0.99364 | -0.044499 | 0 | 0
19 | 0.99515 | -0.033918 | 0.047053 | 0.011793
20 | 0.99264 | -0.051579 | 0 | 0
21 | 0.99657 | -0.023972 | 0 | 0
22 | 0.99231 | -0.053922 | 0.025231 | 0.0063236
23 | 1 | 0 | -0.18806 | -0.04714
24 | 0.99493 | -0.035293 | 0.003044 | 0.00076289
25 | 0.992 | -0.055781 | 0 | 0
26 | 0.99159 | -0.058712 | 0.0084608 | 0.0021205
27 | 0.99133 | -0.060536 | 0 | 0
28 | 0.99069 | -0.065016 | 0.0064348 | 0.0016127
29 | 0.99043 | -0.066859 | 0.0071871 | 0.0018013
30 | 0.986 | -0.098171 | 0.003896 | 0.00097643
31 | 0.98955 | -0.073067 | 0.0087301 | 0.002188
32 | 0.98998 | -0.070095 | 0.010245 | 0.0025677
33 | 0.98698 | -0.091206 | 0.0027066 | 0.00067833
34 | 0.98644 | -0.09506 | 0.0026069 | 0.00065335
35 | 0.98641 | -0.095293 | 0.0008364 | 0.00020962
36 | 0.98665 | -0.093551 | 0.00083551 | 0.0002094
37 | 0.98634 | -0.095756 | 0.0033947 | 0.0008508
38 | 0.9867 | -0.093178 | 0.004146 | 0.0010391
39 | 0.98405 | -0.11204 | 0.00086942 | 0.0002179
40 | 0.98612 | -0.097294 | 0.0030297 | 0.00075931
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010075 | -0.0025225 | 0.010078 | 0.0025232 | 2.08e-06 | 6.1215e-07 | 0.015125 | 0.015125 | 0.015125 | 0.99116 | -0.06201 | 0.99138 | -0.060516 | 5.6019
1 | 0.0042513 | 0.0010629 | -0.0042498 | -0.0010631 | 1.5228e-06 | -1.8636e-07 | 0.0063815 | 0.0063817 | 0.0063817 | 0.99116 | -0.06201 | 0.9908 | -0.064609 | 2.3636
2 | -0.012581 | -0.0031506 | 0.012586 | 0.0031521 | 4.582e-06 | 1.4967e-06 | 0.018883 | 0.018883 | 0.018883 | 0.99138 | -0.060516 | 0.99175 | -0.057882 | 6.9937
3 | 0.0015814 | 0.00039569 | -0.0015812 | -0.00039629 | 1.843e-07 | -6.0345e-07 | 0.0023748 | 0.002375 | 0.002375 | 0.9908 | -0.064609 | 0.99068 | -0.065452 | 0.87963
4 | 0.0026684 | 0.00066738 | -0.0026677 | -0.00066794 | 6.2091e-07 | -5.5911e-07 | 0.004007 | 0.0040072 | 0.0040072 | 0.9908 | -0.064609 | 0.99056 | -0.066295 | 1.4842
5 | -0.014692 | -0.00368 | 0.014699 | 0.0036823 | 6.6683e-06 | 2.2808e-06 | 0.022043 | 0.022043 | 0.022043 | 0.99175 | -0.057882 | 0.99221 | -0.054601 | 8.1641
6 | 0.0012313 | 0.00030845 | -0.0012313 | -0.00030859 | 2.3884e-08 | -1.3483e-07 | 0.0018496 | 0.0018497 | 0.0018497 | 0.99056 | -0.066295 | 0.99054 | -0.066436 | 0.68506
7 | 0.0014364 | 0.00035949 | -0.0014363 | -0.00035998 | 1.2014e-07 | -4.8608e-07 | 0.0021576 | 0.0021578 | 0.0021578 | 0.99056 | -0.066295 | 0.99047 | -0.0669 | 0.79919
8 | -0.017888 | -0.0044815 | 0.017893 | 0.0044834 | 5.4125e-06 | 1.926e-06 | 0.026825 | 0.026825 | 0.026825 | 0.99221 | -0.054601 | 0.99252 | -0.052414 | 9.9353
9 | 0.0076416 | 0.0019149 | -0.0076409 | -0.0019147 | 7.0448e-07 | 1.6346e-07 | 0.011553 | 0.011553 | 0.011553 | 0.98424 | -0.11064 | 0.98415 | -0.11131 | 4.2788
10 | -0.01058 | -0.0026513 | 0.010581 | 0.0026516 | 1.1427e-06 | 3.4853e-07 | 0.015995 | 0.015995 | 0.015995 | 0.98424 | -0.11064 | 0.98435 | -0.10986 | 5.924
11 | 0.004229 | 0.0010596 | -0.0042286 | -0.0010597 | 3.1817e-07 | -3.6088e-08 | 0.006394 | 0.0063941 | 0.0063941 | 0.98415 | -0.11131 | 0.98407 | -0.11185 | 2.3682
12 | -0.014662 | -0.0036743 | 0.014666 | 0.0036757 | 3.9611e-06 | 1.3592e-06 | 0.022163 | 0.022163 | 0.022163 | 0.98435 | -0.10986 | 0.98463 | -0.10791 | 8.2087
13 | 0.0016042 | 0.0004019 | -0.0016042 | -0.00040202 | 3.7483e-08 | -1.1528e-07 | 0.0024256 | 0.0024257 | 0.0024257 | 0.98407 | -0.11185 | 0.98405 | -0.11202 | 0.89841
14 | 0.00086942 | 0.00021787 | -0.00086942 | -0.0002179 | 2.0515e-09 | -2.3375e-08 | 0.0013147 | 0.0013147 | 0.0013147 | 0.98405 | -0.11202 | 0.98405 | -0.11204 | 0.48692
15 | -0.024058 | -0.0060285 | 0.024065 | 0.0060312 | 7.3373e-06 | 2.7052e-06 | 0.036068 | 0.036068 | 0.036068 | 0.99252 | -0.052414 | 0.99283 | -0.050211 | 13.3585
16 | -0.018178 | -0.004556 | 0.018193 | 0.0045612 | 1.4574e-05 | 5.2113e-06 | 0.027472 | 0.027472 | 0.027472 | 0.98463 | -0.10791 | 0.98544 | -0.10212 | 10.1747
17 | -0.02199 | -0.005513 | 0.022002 | 0.0055174 | 1.2043e-05 | 4.4086e-06 | 0.033206 | 0.033206 | 0.033206 | 0.98544 | -0.10212 | 0.986 | -0.098171 | 12.2984
18 | -0.025833 | -0.0064744 | 0.025854 | 0.006482 | 2.0444e-05 | 7.5803e-06 | 0.038718 | 0.038718 | 0.038718 | 0.99283 | -0.050211 | 0.99364 | -0.044499 | 14.34
19 | -0.051118 | -0.012818 | 0.051193 | 0.012846 | 7.5066e-05 | 2.8605e-05 | 0.076554 | 0.076554 | 0.076554 | 0.99364 | -0.044499 | 0.99515 | -0.033918 | 28.3532
20 | 0.025264 | 0.0063358 | -0.02524 | -0.0063266 | 2.4769e-05 | 9.1677e-06 | 0.037836 | 0.037836 | 0.037836 | 0.99364 | -0.044499 | 0.99264 | -0.051579 | 14.0133
21 | -0.098246 | -0.024639 | 0.098382 | 0.024691 | 0.00013564 | 5.2038e-05 | 0.14691 | 0.14691 | 0.14691 | 0.99515 | -0.033918 | 0.99657 | -0.023972 | 54.4112
22 | 0.02524 | 0.0063266 | -0.025231 | -0.0063236 | 8.189e-06 | 3.0311e-06 | 0.037836 | 0.037836 | 0.037836 | 0.99264 | -0.051579 | 0.99231 | -0.053922 | 14.0133
23 | -0.098382 | -0.024691 | 0.09871 | 0.024817 | 0.00032852 | 0.00012603 | 0.14691 | 0.14691 | 0.14691 | 0.99657 | -0.023972 | 1 | 0 | 54.4111
24 | 0.088545 | 0.022323 | -0.08811 | -0.022156 | 0.00043557 | 0.000167 | 0.1318 | 0.1318 | 0.1318 | 1 | 0 | 0.99493 | -0.035293 | 48.8161
25 | 0.085066 | 0.021393 | -0.084824 | -0.0213 | 0.00024223 | 9.2856e-05 | 0.12725 | 0.12725 | 0.12725 | 0.99493 | -0.035293 | 0.992 | -0.055781 | 47.13
26 | 0.076359 | 0.019179 | -0.076309 | -0.01916 | 5.0458e-05 | 1.9327e-05 | 0.11455 | 0.11455 | 0.11455 | 0.992 | -0.055781 | 0.99133 | -0.060536 | 42.4276
27 | 0.0084642 | 0.0021214 | -0.0084608 | -0.0021205 | 3.434e-06 | 8.8022e-07 | 0.012696 | 0.012697 | 0.012697 | 0.992 | -0.055781 | 0.99159 | -0.058712 | 4.7025
28 | 0.058857 | 0.014784 | -0.05882 | -0.01477 | 3.6637e-05 | 1.3994e-05 | 0.088357 | 0.088357 | 0.088357 | 0.99133 | -0.060536 | 0.99069 | -0.065016 | 32.725
29 | 0.017452 | 0.0043758 | -0.017437 | -0.0043704 | 1.5276e-05 | 5.4157e-06 | 0.026197 | 0.026197 | 0.026197 | 0.99133 | -0.060536 | 0.99043 | -0.066859 | 9.7027
30 | 0.052385 | 0.013157 | -0.052327 | -0.013135 | 5.857e-05 | 2.2332e-05 | 0.078692 | 0.078692 | 0.078692 | 0.99069 | -0.065016 | 0.98955 | -0.073067 | 29.1453
31 | 0.01025 | 0.0025691 | -0.010245 | -0.0025677 | 4.591e-06 | 1.3667e-06 | 0.015399 | 0.0154 | 0.0154 | 0.99043 | -0.066859 | 0.98998 | -0.070095 | 5.7036
32 | -0.025898 | -0.0064938 | 0.025901 | 0.006495 | 3.1509e-06 | 1.1697e-06 | 0.039085 | 0.039085 | 0.039085 | 0.986 | -0.098171 | 0.98612 | -0.097294 | 14.476
33 | 0.043597 | 0.010947 | -0.043487 | -0.010905 | 0.00010961 | 4.1635e-05 | 0.065565 | 0.065565 | 0.065565 | 0.98955 | -0.073067 | 0.98698 | -0.091206 | 24.2833
34 | 0.011825 | 0.0029635 | -0.011822 | -0.0029625 | 3.2268e-06 | 1.0332e-06 | 0.017828 | 0.017828 | 0.017828 | 0.98698 | -0.091206 | 0.9867 | -0.093178 | 6.6029
35 | 0.028955 | 0.0072634 | -0.028931 | -0.0072543 | 2.4424e-05 | 9.1315e-06 | 0.043657 | 0.043657 | 0.043657 | 0.98698 | -0.091206 | 0.98612 | -0.097294 | 16.1692
36 | 0.0042315 | 0.0010603 | -0.0042314 | -0.0010603 | 1.365e-07 | -1.6038e-08 | 0.006383 | 0.006383 | 0.006383 | 0.98644 | -0.09506 | 0.98641 | -0.095293 | 2.3641
37 | -0.0068384 | -0.0017137 | 0.0068398 | 0.0017139 | 1.4287e-06 | 2.7476e-07 | 0.010315 | 0.010315 | 0.010315 | 0.98644 | -0.09506 | 0.98665 | -0.093551 | 3.8205
38 | 0.0033949 | 0.00085071 | -0.0033947 | -0.0008508 | 2.1759e-07 | -8.6012e-08 | 0.0051213 | 0.0051214 | 0.0051214 | 0.98641 | -0.095293 | 0.98634 | -0.095756 | 1.8968
39 | -0.0076753 | -0.0019233 | 0.0076757 | 0.0019234 | 3.9601e-07 | 9.1817e-08 | 0.011575 | 0.011575 | 0.011575 | 0.98665 | -0.093551 | 0.9867 | -0.093178 | 4.2872

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19357 | 0.048521

## res_load
| p_mw | q_mvar
0 | 0.0058241 | 0.0014597
1 | 0.0025036 | 0.00062746
2 | 0.0021064 | 0.0005279
3 | 0.0015812 | 0.00039629
4 | 0.0031889 | 0.0007992
5 | 0.0029382 | 0.00073639
6 | 0.003412 | 0.00085512
7 | 0.0040806 | 0.0010227
8 | 0.0026245 | 0.00065775
9 | 0.00073474 | 0.00018414
10 | 0.0012313 | 0.00030859
11 | 0.0014363 | 0.00035998
12 | 0.0061649 | 0.0015451
13 | 0.0035126 | 0.00088034
14 | 0.0037974 | 0.00095171
15 | 0.0017682 | 0.00044315
16 | 0.047053 | 0.011793
17 | 0.025231 | 0.0063236
18 | 0.0055105 | 0.0013811
19 | 0.003044 | 0.00076289
20 | 0.0084608 | 0.0021205
21 | 0.0064348 | 0.0016127
22 | 0.0071871 | 0.0018013
23 | 0.003896 | 0.00097643
24 | 0.0087301 | 0.002188
25 | 0.010245 | 0.0025677
26 | 0.0027066 | 0.00067833
27 | 0.0026069 | 0.00065335
28 | 0.0008364 | 0.00020962
29 | 0.00083551 | 0.0002094
30 | 0.0033947 | 0.0008508
31 | 0.004146 | 0.0010391
32 | 0.00086942 | 0.0002179
33 | 0.0030297 | 0.00075931

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1