## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1375-4_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1375-4_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1375-4_0_1_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1375-4_0_1_node_20 | 0.4 | n |  | TRUE
4 | bus_LV_1375-4_0_1_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1375-4_0_1_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1375-4_0_1_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1375-4_0_1_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1375-4_0_1_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_1375-4_0_1_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1375-4_0_1_node_152 | 0.4 | n |  | TRUE
11 | bus_LV_1375-4_0_1_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1375-4_0_1_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1375-4_0_1_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1375-4_0_1_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1375-4_0_1_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1375-4_0_1_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1375-4_0_1_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1375-4_0_1_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1375-4_0_1_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1375-4_0_1_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1375-4_0_1_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1375-4_0_1_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_1375-4_0_1_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1375-4_0_1_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1375-4_0_1_node_158 | 0.4 | n |  | TRUE
26 | bus_LV_1375-4_0_1_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1375-4_0_1_node_150 | 0.4 | n |  | TRUE
28 | bus_LV_1375-4_0_1_node_48 | 0.4 | n |  | TRUE
29 | bus_LV_1375-4_0_1_node_151 | 0.4 | n |  | TRUE
30 | bus_LV_1375-4_0_1_node_153 | 0.4 | n |  | TRUE
31 | bus_LV_1375-4_0_1_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_1375-4_0_1_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_1375-4_0_1_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_1375-4_0_1_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_1375-4_0_1_node_47 | 0.4 | n |  | TRUE
36 | bus_MV_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1375-4_0_1_load_0 | 0 | 0.0073195 | 0.0018344 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1375-4_0_1_load_20 | 3 | 0.00072886 | 0.00018267 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1375-4_0_1_load_3 | 4 | 0.00020524 | 5.1438e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1375-4_0_1_load_4 | 5 | 0.00056959 | 0.00014275 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1375-4_0_1_load_22 | 8 | 0.00011107 | 2.7837e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1375-4_0_1_load_7 | 9 | 0.00020609 | 5.1651e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1375-4_0_1_load_8 | 11 | 0.00044777 | 0.00011222 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1375-4_0_1_load_9 | 12 | 0.00075391 | 0.00018895 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1375-4_0_1_load_11 | 14 | 0.00026065 | 6.5326e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1375-4_0_1_load_12 | 15 | 0.00075066 | 0.00018813 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1375-4_0_1_load_17 | 17 | 0.00032271 | 8.0879e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1375-4_0_1_load_18 | 18 | 0.00047844 | 0.00011991 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1375-4_0_1_load_14 | 19 | 0.00018775 | 4.7055e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1375-4_0_1_load_16 | 21 | 0.00030825 | 7.7256e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1375-4_0_1_load_44 | 22 | 0.00013416 | 3.3623e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1375-4_0_1_load_158 | 25 | 0.0003144 | 7.8795e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1375-4_0_1_load_23 | 26 | 0.00014197 | 3.5581e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1375-4_0_1_load_150 | 27 | 0.00017748 | 4.4481e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1375-4_0_1_load_153 | 30 | 0.0031129 | 0.00078017 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1375-4_0_1_load_40 | 31 | 0.00019402 | 4.8625e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1375-4_0_1_load_47 | 35 | 0.00037791 | 9.4714e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1375-4_0_1_line_0 | NAYY 4x150 SE | 0 | 1 | 0.014314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1375-4_0_1_line_1 | NAYY 4x150 SE | 0 | 2 | 0.11248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1375-4_0_1_line_2 | NAYY 4x150 SE | 1 | 3 | 0.41387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1375-4_0_1_line_3 | NAYY 4x150 SE | 2 | 4 | 0.050875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1375-4_0_1_line_4 | NAYY 4x150 SE | 3 | 23 | 0.11051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1375-4_0_1_line_5 | NAYY 4x150 SE | 5 | 6 | 0.0081132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1375-4_0_1_line_6 | NAYY 4x150 SE | 6 | 9 | 0.11418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1375-4_0_1_line_7 | NAYY 4x150 SE | 6 | 7 | 0.071248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1375-4_0_1_line_8 | NAYY 4x150 SE | 7 | 8 | 0.46241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1375-4_0_1_line_9 | NAYY 4x150 SE | 8 | 26 | 0.042897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1375-4_0_1_line_10 | NAYY 4x150 SE | 9 | 10 | 0.27252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1375-4_0_1_line_11 | NAYY 4x150 SE | 10 | 30 | 0.20507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1375-4_0_1_line_12 | NAYY 4x150 SE | 10 | 29 | 0.024065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1375-4_0_1_line_13 | NAYY 4x150 SE | 11 | 12 | 0.024915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1375-4_0_1_line_14 | NAYY 4x150 SE | 11 | 13 | 0.0056865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1375-4_0_1_line_15 | NAYY 4x150 SE | 12 | 14 | 0.033825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1375-4_0_1_line_16 | NAYY 4x150 SE | 13 | 15 | 0.17 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1375-4_0_1_line_17 | NAYY 4x150 SE | 13 | 16 | 0.031805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1375-4_0_1_line_18 | NAYY 4x150 SE | 14 | 17 | 0.010224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1375-4_0_1_line_19 | NAYY 4x150 SE | 16 | 18 | 0.11124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1375-4_0_1_line_20 | NAYY 4x150 SE | 16 | 19 | 0.33712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1375-4_0_1_line_21 | NAYY 4x150 SE | 18 | 23 | 0.17565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1375-4_0_1_line_22 | NAYY 4x150 SE | 19 | 20 | 0.11282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1375-4_0_1_line_23 | NAYY 4x150 SE | 20 | 21 | 0.22234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1375-4_0_1_line_24 | NAYY 4x150 SE | 21 | 22 | 0.42279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1375-4_0_1_line_25 | NAYY 4x150 SE | 22 | 33 | 0.027937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1375-4_0_1_line_26 | NAYY 4x150 SE | 23 | 24 | 0.18417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1375-4_0_1_line_27 | NAYY 4x150 SE | 24 | 25 | 0.053284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1375-4_0_1_line_28 | NAYY 4x150 SE | 27 | 28 | 0.075666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1375-4_0_1_line_29 | NAYY 4x150 SE | 27 | 29 | 0.22178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1375-4_0_1_line_30 | NAYY 4x150 SE | 28 | 34 | 0.21513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1375-4_0_1_line_31 | NAYY 4x150 SE | 31 | 32 | 0.015006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1375-4_0_1_line_32 | NAYY 4x150 SE | 31 | 33 | 0.094383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1375-4_0_1_line_33 | NAYY 4x150 SE | 32 | 34 | 0.047469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1375-4_0_1_line_34 | NAYY 4x150 SE | 34 | 35 | 0.042774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1375-4_0_1_trafo_3 | 0.25 MVA 20/0.4 kV | 36 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28
0 | 2705939.7213 | 1211319.4032 | 2705937.3974 | 1211324.4322 | 2705937.8673 | 1211333.1939
1 | 2705904.4963 | 1211436.0053 | 2705905.0768 | 1211428.5659 | 2705909.9415 | 1211415.7097 | 2705927.9183 | 1211395.0809 | 2705935.6295 | 1211378.5838 | 2705939.1158 | 1211356.4744 | 2705937.8673 | 1211333.1939
2 | 2705618.2139 | 1211058.784 | 2705939.7213 | 1211319.4032
3 | 2705882.5337 | 1211481.2143 | 2705891.7438 | 1211465.9002 | 2705899.3986 | 1211453.8497 | 2705902.1881 | 1211447.8505 | 2705904.0724 | 1211441.4683 | 2705904.4963 | 1211436.0053
4 | 2705532.1765 | 1211000.131 | 2705536.4681 | 1211017.0411 | 2705541.8156 | 1211022.3951 | 2705551.9996 | 1211025.0438 | 2705570.4017 | 1211029.3169 | 2705582.9999 | 1211035.1328 | 2705618.2139 | 1211058.784
5 | 2705565.1104 | 1212193.318 | 2705571.3721 | 1212198.4769
6 | 2705565.1104 | 1212193.318 | 2705569.0029 | 1212191.5078 | 2705588.2717 | 1212184.833 | 2705654.3164 | 1212158.795 | 2705672.1237 | 1212153.7726
7 | 2705566.3781 | 1212250.0364 | 2705567.0288 | 1212239.0401 | 2705562.4311 | 1212231.3199 | 2705550.0233 | 1212219.1917 | 2705548.8908 | 1212213.6232 | 2705549.1857 | 1212210.2705 | 2705550.1016 | 1212206.6174 | 2705552.8121 | 1212200.3165 | 2705555.6163 | 1212197.742 | 2705565.1104 | 1212193.318
8 | 2705566.3781 | 1212250.0364 | 2705295.4225 | 1212624.7474
9 | 2705317.8189 | 1212659.4787 | 2705315.7605 | 1212657.6632 | 2705304.4918 | 1212648.6134 | 2705299.9374 | 1212640.5939 | 2705295.4225 | 1212624.7474
10 | 2705751.4133 | 1211932.2875 | 2705750.0899 | 1211947.3414 | 2705753.6136 | 1211970.1869 | 2705753.7034 | 1211976.6931 | 2705752.7716 | 1211981.2354 | 2705750.8392 | 1211987.3499 | 2705748.6962 | 1211991.6261 | 2705746.125 | 1211995.6278 | 2705739.4744 | 1212002.9596 | 2705734.1892 | 1212008.2919 | 2705731.7743 | 1212012.4743 | 2705730.3344 | 1212017.8193 | 2705729.9931 | 1212024.2067 | 2705730.4356 | 1212030.9638 | 2705732.2117 | 1212038.8008 | 2705743.9025 | 1212076.357 | 2705744.5662 | 1212081.3502 | 2705744.5142 | 1212086.8532 | 2705743.5301 | 1212092.2062 | 2705741.1285 | 1212099.0685 | 2705727.9903 | 1212127.2668 | 2705723.7908 | 1212133.5191 | 2705719.245 | 1212138.3086 | 2705714.0971 | 1212142.765 | 2705710.737 | 1212144.54 | 2705706.9721 | 1212145.574 | 2705700.2871 | 1212146.2894 | 2705692.0389 | 1212148.1557 | 2705672.1237 | 1212153.7726
11 | 2705751.4133 | 1211932.2875 | 2705754.9223 | 1211946.1151 | 2705758.6668 | 1211955.2325 | 2705764.3819 | 1211962.5056 | 2705789.7212 | 1211987.6729 | 2705851.8724 | 1212039.8349 | 2705878.2385 | 1212074.7499 | 2705883.3231 | 1212084.6035
12 | 2705751.4133 | 1211932.2875 | 2705752.2123 | 1211908.2401
13 | 2705283.7938 | 1211050.6901 | 2705283.6779 | 1211053.9899 | 2705283.5728 | 1211075.4366 | 2705283.6111 | 1211075.5982
14 | 2705284.9239 | 1211081.1311 | 2705283.6111 | 1211075.5982
15 | 2705283.7938 | 1211050.6901 | 2705284.1973 | 1211039.2108 | 2705283.7396 | 1211027.6834 | 2705285.7896 | 1211017.0774
16 | 2705369.3875 | 1210942.0458 | 2705370.7677 | 1210947.8187 | 2705367.6938 | 1210954.0133 | 2705362.1468 | 1210959.5081 | 2705348.2961 | 1210968.6366 | 2705341.7468 | 1210974.9366 | 2705337.252 | 1210986.6989 | 2705332.1879 | 1211002.7208 | 2705327.2542 | 1211020.4018 | 2705322.806 | 1211029.5298 | 2705310.6216 | 1211046.7492 | 2705304.1381 | 1211058.7988 | 2705297.4426 | 1211073.8135 | 2705291.9208 | 1211078.3193 | 2705284.9239 | 1211081.1311
17 | 2705291.8489 | 1211112.0864 | 2705290.127 | 1211105.4291 | 2705286.7984 | 1211094.6404 | 2705284.9239 | 1211081.1311
18 | 2705287.7298 | 1211007.0392 | 2705285.7896 | 1211017.0774
19 | 2705291.8489 | 1211112.0864 | 2705295.8865 | 1211118.0174 | 2705301.1348 | 1211122.9691 | 2705309.9519 | 1211127.2611 | 2705321.5051 | 1211124.2518 | 2705351.1771 | 1211109.2762 | 2705378.5775 | 1211096.4065 | 2705389.7884 | 1211093.4305
20 | 2705291.8489 | 1211112.0864 | 2705084.6309 | 1211377.9951
21 | 2705532.1765 | 1211000.131 | 2705526.5433 | 1211012.2066 | 2705510.5653 | 1211024.7106 | 2705485.0968 | 1211035.3234 | 2705452.1291 | 1211046.215 | 2705440.1744 | 1211055.5881 | 2705414.7453 | 1211081.6128 | 2705404.2214 | 1211089.5992 | 2705389.7884 | 1211093.4305
22 | 2705028.6981 | 1211455.7139 | 2705032.4936 | 1211451.6667 | 2705044.9887 | 1211446.0494 | 2705062.8269 | 1211443.8842 | 2705073.1166 | 1211435.7597 | 2705083.934 | 1211423.1412 | 2705085.905 | 1211413.5136 | 2705088.2544 | 1211395.3532 | 2705084.6309 | 1211377.9951
23 | 2705028.6981 | 1211455.7139 | 2705030.1969 | 1211465.5472 | 2705034.1727 | 1211475.8579 | 2705041.7558 | 1211484.164 | 2705062.17 | 1211497.9777 | 2705083.668 | 1211508.9419 | 2705109.2308 | 1211525.1482 | 2705120.0023 | 1211535.8122 | 2705123.5814 | 1211542.3132 | 2705126.6443 | 1211551.7962 | 2705129.2148 | 1211556.4448 | 2705131.492 | 1211558.3307 | 2705137.8138 | 1211559.7097 | 2705142.94 | 1211556.9203 | 2705152.901 | 1211548.4677 | 2705158.2529 | 1211545.8046 | 2705163.6595 | 1211546.934 | 2705167.0721 | 1211549.5182 | 2705174.234 | 1211562.298 | 2705179.7651 | 1211575.6313
24 | 2705156.9673 | 1211997.8031 | 2705179.7651 | 1211575.6313
25 | 2705155.4708 | 1212025.3407 | 2705155.5697 | 1212020.5946 | 2705156.3909 | 1212017.5514 | 2705157.9618 | 1212011.219 | 2705158.1961 | 1212006.5532 | 2705157.4351 | 1212001.8698 | 2705156.9673 | 1211997.8031
26 | 2705532.1765 | 1211000.131 | 2705533.8591 | 1210996.536 | 2705571.805 | 1210942.3466 | 2705600.4473 | 1210915.6456 | 2705612.5337 | 1210904.4516 | 2705623.3345 | 1210916.0511 | 2705620.8587 | 1210931.3737 | 2705615.0777 | 1210957.7901
27 | 2705615.0777 | 1210957.7901 | 2705606.1861 | 1210964.9934 | 2705596.9096 | 1210976.3372 | 2705593.293 | 1210984.8348 | 2705593.8261 | 1210992.0716 | 2705597.44 | 1211002.1761
28 | 2705468.8152 | 1211912.5814 | 2705476.7199 | 1211912.9547 | 2705485.1131 | 1211911.0685 | 2705502.7481 | 1211905.2873 | 2705523.5346 | 1211905.6553 | 2705543.2437 | 1211907.573
29 | 2705752.2123 | 1211908.2401 | 2705739.7886 | 1211906.8411 | 2705733.6079 | 1211910.3896 | 2705721.7933 | 1211921.3547 | 2705718.4944 | 1211923.5311 | 2705703.7661 | 1211926.5278 | 2705689.6566 | 1211928.9128 | 2705647.7818 | 1211934.0636 | 2705623.2971 | 1211935.2531 | 2705601.7409 | 1211932.4361 | 2705577.8355 | 1211924.0848 | 2705551.6131 | 1211908.3873 | 2705543.2437 | 1211907.573
30 | 2705299.2051 | 1212005.4065 | 2705303.5222 | 1212006.2389 | 2705313.1832 | 1212009.1448 | 2705329.159 | 1212014.2305 | 2705333.3835 | 1212015.1391 | 2705336.5894 | 1212015.2069 | 2705340.5128 | 1212014.6647 | 2705348.9036 | 1212012.9005 | 2705355.9359 | 1212010.6008 | 2705363.1116 | 1212007.0695 | 2705392.4858 | 1211990.2209 | 2705413.3672 | 1211977.4696 | 2705421.7512 | 1211972.2252 | 2705426.8296 | 1211968.6902 | 2705430.2603 | 1211964.6368 | 2705433.7892 | 1211958.9062 | 2705436.2351 | 1211952.9564 | 2705437.8428 | 1211945.8464 | 2705440.0295 | 1211936.0781 | 2705442.4749 | 1211930.5952 | 2705444.3729 | 1211927.6933 | 2705447.3682 | 1211924.1994 | 2705450.9738 | 1211921.0053 | 2705455.8787 | 1211918.2567 | 2705468.8152 | 1211912.5814
31 | 2705251.9569 | 1212000.3024 | 2705240.9443 | 1211999.0516 | 2705237.1211 | 1211998.1744
32 | 2705155.4708 | 1212025.3407 | 2705168.5423 | 1212009.3931 | 2705175.4728 | 1212002.5216 | 2705179.4211 | 1211999.2778 | 2705182.7797 | 1211997.5802 | 2705187.086 | 1211996.0106 | 2705195.9295 | 1211994.4321 | 2705205.0734 | 1211993.9152 | 2705212.9186 | 1211994.2093 | 2705221.7484 | 1211995.1324 | 2705230.1812 | 1211996.5822 | 2705237.1211 | 1211998.1744
33 | 2705299.2051 | 1212005.4065 | 2705290.4949 | 1212003.7405 | 2705277.6191 | 1212001.7007 | 2705261.9435 | 1212000.7011 | 2705251.9569 | 1212000.3024
34 | 2705299.2051 | 1212005.4065 | 2705299.3227 | 1212008.2106 | 2705297.0657 | 1212012.5071 | 2705292.5735 | 1212014.7072 | 2705283.5169 | 1212016.304 | 2705275.9153 | 1212018.1378 | 2705272.9656 | 1212020.7765 | 2705271.5587 | 1212023.8428 | 2705272.5063 | 1212029.141 | 2705272.6211 | 1212029.506

## bus_geodata
| x | y | coords
0 | 2705937.8673 | 1211333.1939
1 | 2705939.7213 | 1211319.4032
2 | 2705904.4963 | 1211436.0053
3 | 2705618.2139 | 1211058.784
4 | 2705882.5337 | 1211481.2143
5 | 2705571.3721 | 1212198.4769
6 | 2705565.1104 | 1212193.318
7 | 2705566.3781 | 1212250.0364
8 | 2705295.4225 | 1212624.7474
9 | 2705672.1237 | 1212153.7726
10 | 2705751.4133 | 1211932.2875
11 | 2705283.6111 | 1211075.5982
12 | 2705283.7938 | 1211050.6902
13 | 2705284.9239 | 1211081.1311
14 | 2705285.7896 | 1211017.0774
15 | 2705369.3875 | 1210942.0458
16 | 2705291.8489 | 1211112.0864
17 | 2705287.7298 | 1211007.0392
18 | 2705389.7884 | 1211093.4305
19 | 2705084.6309 | 1211377.9951
20 | 2705028.6981 | 1211455.7139
21 | 2705179.7651 | 1211575.6313
22 | 2705156.9673 | 1211997.8031
23 | 2705532.1765 | 1211000.131
24 | 2705615.0777 | 1210957.7901
25 | 2705597.44 | 1211002.1761
26 | 2705317.8189 | 1212659.4787
27 | 2705543.2437 | 1211907.573
28 | 2705468.8152 | 1211912.5814
29 | 2705752.2123 | 1211908.2401
30 | 2705883.3231 | 1212084.6035
31 | 2705237.1211 | 1211998.1744
32 | 2705251.9569 | 1212000.3024
33 | 2705155.4708 | 1212025.3407
34 | 2705299.2051 | 1212005.4065
35 | 2705272.6211 | 1212029.506
36 | 2705882.5337 | 1211481.2143

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99601 | -0.028345 | 0.0073195 | 0.0018344
1 | 0.99581 | -0.029784 | 0 | 0
2 | 0.99876 | -0.0088065 | 0 | 0
3 | 0.99005 | -0.071548 | 0.00072886 | 0.00018267
4 | 1 | 0 | -0.017931 | -0.0042675
5 | 0.9715 | -0.2086 | 0.00056959 | 0.00014275
6 | 0.9715 | -0.20855 | 0 | 0
7 | 0.97148 | -0.20878 | 0 | 0
8 | 0.97131 | -0.21014 | 0.00011107 | 2.7837e-05
9 | 0.97164 | -0.20749 | 0.00020609 | 5.1651e-05
10 | 0.97205 | -0.20431 | 0 | 0
11 | 0.985 | -0.10837 | 0.00044777 | 0.00011222
12 | 0.98496 | -0.10871 | 0.00075391 | 0.00018895
13 | 0.98502 | -0.10827 | 0 | 0
14 | 0.98493 | -0.10892 | 0.00026065 | 6.5326e-05
15 | 0.98483 | -0.10959 | 0.00075066 | 0.00018813
16 | 0.98514 | -0.10743 | 0 | 0
17 | 0.98492 | -0.10895 | 0.00032271 | 8.0879e-05
18 | 0.98644 | -0.097863 | 0.00047844 | 0.00011991
19 | 0.98241 | -0.12755 | 0.00018775 | 4.7055e-05
20 | 0.98153 | -0.13406 | 0 | 0
21 | 0.9798 | -0.1469 | 0.00030825 | 7.7256e-05
22 | 0.97669 | -0.16994 | 0.00013416 | 3.3623e-05
23 | 0.98863 | -0.081931 | 0 | 0
24 | 0.98854 | -0.082548 | 0 | 0
25 | 0.98852 | -0.082721 | 0.0003144 | 7.8795e-05
26 | 0.9713 | -0.21021 | 0.00014197 | 3.5581e-05
27 | 0.97354 | -0.19326 | 0.00017748 | 4.4481e-05
28 | 0.97402 | -0.18971 | 0 | 0
29 | 0.9722 | -0.20322 | 0 | 0
30 | 0.97111 | -0.21108 | 0.0031129 | 0.00078017
31 | 0.97581 | -0.17643 | 0.00019402 | 4.8625e-05
32 | 0.97571 | -0.17719 | 0 | 0
33 | 0.97649 | -0.17142 | 0 | 0
34 | 0.97538 | -0.17961 | 0 | 0
35 | 0.97536 | -0.17978 | 0.00037791 | 9.4714e-05
36 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0097455 | 0.0024097 | -0.0097436 | -0.0024092 | 1.8904e-06 | 5.4083e-07 | 0.014548 | 0.014548 | 0.014548 | 0.99601 | -0.028345 | 0.99581 | -0.029784 | 5.3882
1 | -0.017065 | -0.0042441 | 0.017111 | 0.0042602 | 4.5577e-05 | 1.6062e-05 | 0.025483 | 0.025483 | 0.025483 | 0.99601 | -0.028345 | 0.99876 | -0.0088065 | 9.4382
2 | 0.0097436 | 0.0024092 | -0.0096889 | -0.0023935 | 5.4666e-05 | 1.5672e-05 | 0.014548 | 0.01455 | 0.01455 | 0.99581 | -0.029784 | 0.99005 | -0.071548 | 5.3889
3 | -0.017111 | -0.0042602 | 0.017131 | 0.0042675 | 2.0614e-05 | 7.262e-06 | 0.025483 | 0.025482 | 0.025483 | 0.99876 | -0.0088065 | 1 | 0 | 9.438
4 | 0.0089601 | 0.0022108 | -0.0089476 | -0.0022074 | 1.2484e-05 | 3.3823e-06 | 0.013454 | 0.013455 | 0.013455 | 0.99005 | -0.071548 | 0.98863 | -0.081931 | 4.9833
5 | -0.00056959 | -0.00014275 | 0.0005696 | 0.00014265 | 3.8532e-09 | -9.8977e-08 | 0.00087243 | 0.00087239 | 0.00087243 | 0.9715 | -0.2086 | 0.9715 | -0.20855 | 0.32312
6 | -0.00082269 | -0.00019895 | 0.0008228 | 0.00019758 | 1.1262e-07 | -1.3707e-06 | 0.0012575 | 0.001257 | 0.0012575 | 0.9715 | -0.20855 | 0.97164 | -0.20749 | 0.46575
7 | 0.00025309 | 5.63e-05 | -0.00025309 | -5.718e-05 | 6.6022e-09 | -8.7965e-07 | 0.00038522 | 0.0003855 | 0.0003855 | 0.9715 | -0.20855 | 0.97148 | -0.20878 | 0.14278
8 | 0.00025309 | 5.718e-05 | -0.00025304 | -6.2888e-05 | 4.3095e-08 | -5.7078e-06 | 0.0003855 | 0.00038747 | 0.00038747 | 0.97148 | -0.20878 | 0.97131 | -0.21014 | 0.14351
9 | 0.00014197 | 3.5051e-05 | -0.00014197 | -3.5581e-05 | 1.2651e-09 | -5.3045e-07 | 0.00021731 | 0.0002175 | 0.0002175 | 0.97131 | -0.21014 | 0.9713 | -0.21021 | 0.080554
10 | -0.0010289 | -0.00024924 | 0.0010293 | 0.00024602 | 4.2024e-07 | -3.2151e-06 | 0.0015726 | 0.0015715 | 0.0015726 | 0.97164 | -0.20749 | 0.97205 | -0.20431 | 0.58245
11 | 0.0031158 | 0.00077875 | -0.0031129 | -0.00078017 | 2.9108e-06 | -1.4201e-06 | 0.004769 | 0.0047699 | 0.0047699 | 0.97205 | -0.20431 | 0.97111 | -0.21108 | 1.7666
12 | -0.0041452 | -0.0010248 | 0.0041458 | 0.0010247 | 6.0366e-07 | -6.6183e-08 | 0.0063404 | 0.0063403 | 0.0063404 | 0.97205 | -0.20431 | 0.9722 | -0.20322 | 2.3483
13 | 0.0013374 | 0.00033431 | -0.0013373 | -0.0003346 | 6.344e-08 | -2.9272e-07 | 0.00202 | 0.0020201 | 0.0020201 | 0.985 | -0.10837 | 0.98496 | -0.10871 | 0.74819
14 | -0.0017851 | -0.00044653 | 0.0017851 | 0.00044646 | 2.5799e-08 | -6.2461e-08 | 0.0026964 | 0.0026964 | 0.0026964 | 0.985 | -0.10837 | 0.98502 | -0.10827 | 0.99868
15 | 0.00058338 | 0.00014565 | -0.00058337 | -0.00014608 | 1.6391e-08 | -4.242e-07 | 0.00088114 | 0.0008813 | 0.0008813 | 0.98496 | -0.10871 | 0.98493 | -0.10892 | 0.32641
16 | 0.0007508 | 0.00018602 | -0.00075066 | -0.00018813 | 1.3637e-07 | -2.1112e-06 | 0.0011334 | 0.0011342 | 0.0011342 | 0.98502 | -0.10827 | 0.98483 | -0.10959 | 0.42007
17 | -0.0025359 | -0.00063249 | 0.0025362 | 0.00063219 | 2.9109e-07 | -2.9294e-07 | 0.0038298 | 0.0038297 | 0.0038298 | 0.98502 | -0.10827 | 0.98514 | -0.10743 | 1.4185
18 | 0.00032271 | 8.075e-05 | -0.00032271 | -8.0879e-05 | 1.5164e-09 | -1.2953e-07 | 0.00048751 | 0.00048755 | 0.00048755 | 0.98493 | -0.10892 | 0.98492 | -0.10895 | 0.18058
19 | -0.0081258 | -0.0020043 | 0.0081362 | 0.0020069 | 1.0437e-05 | 2.5961e-06 | 0.012262 | 0.012262 | 0.012262 | 0.98514 | -0.10743 | 0.98644 | -0.097863 | 4.5416
20 | 0.0055896 | 0.0013721 | -0.0055746 | -0.0013706 | 1.4961e-05 | 1.474e-06 | 0.0084327 | 0.0084342 | 0.0084342 | 0.98514 | -0.10743 | 0.98241 | -0.12755 | 3.1238
21 | -0.0086147 | -0.0021268 | 0.0086331 | 0.0021317 | 1.8475e-05 | 4.8585e-06 | 0.012984 | 0.012983 | 0.012984 | 0.98644 | -0.097863 | 0.98863 | -0.081931 | 4.8087
22 | 0.0053868 | 0.0013236 | -0.0053822 | -0.0013232 | 4.6762e-06 | 3.713e-07 | 0.0081498 | 0.0081503 | 0.0081503 | 0.98241 | -0.12755 | 0.98153 | -0.13406 | 3.0186
23 | 0.0053822 | 0.0013232 | -0.0053729 | -0.0013225 | 9.2174e-06 | 7.3988e-07 | 0.0081503 | 0.0081513 | 0.0081513 | 0.98153 | -0.13406 | 0.9798 | -0.1469 | 3.019
24 | 0.0050647 | 0.0012452 | -0.0050491 | -0.0012445 | 1.5577e-05 | 6.8332e-07 | 0.0076832 | 0.007685 | 0.007685 | 0.9798 | -0.1469 | 0.97669 | -0.16994 | 2.8463
25 | 0.004915 | 0.0012109 | -0.004914 | -0.0012109 | 9.7555e-07 | 2.5658e-08 | 0.0074806 | 0.0074808 | 0.0074808 | 0.97669 | -0.16994 | 0.97649 | -0.17142 | 2.7707
26 | 0.00031443 | 7.5764e-05 | -0.0003144 | -7.8115e-05 | 2.5668e-08 | -2.3514e-06 | 0.0004722 | 0.00047302 | 0.00047302 | 0.98863 | -0.081931 | 0.98854 | -0.082548 | 0.17519
27 | 0.0003144 | 7.8115e-05 | -0.0003144 | -7.8795e-05 | 7.4432e-09 | -6.8024e-07 | 0.00047302 | 0.00047326 | 0.00047326 | 0.98854 | -0.082548 | 0.98852 | -0.082721 | 0.17528
28 | -0.0043288 | -0.0010686 | 0.0043309 | 0.0010684 | 2.0632e-06 | -1.4778e-07 | 0.0066105 | 0.0066102 | 0.0066105 | 0.97354 | -0.19326 | 0.97402 | -0.18971 | 2.4483
29 | 0.0041513 | 0.0010241 | -0.0041458 | -0.0010247 | 5.5622e-06 | -6.1451e-07 | 0.0063393 | 0.0063403 | 0.0063403 | 0.97354 | -0.19326 | 0.9722 | -0.20322 | 2.3482
30 | -0.0043309 | -0.0010684 | 0.0043367 | 0.001068 | 5.8647e-06 | -4.2567e-07 | 0.0066102 | 0.0066093 | 0.0066102 | 0.97402 | -0.18971 | 0.97538 | -0.17961 | 2.4482
31 | 0.0047167 | 0.0011622 | -0.0047162 | -0.0011622 | 4.8345e-07 | -1.4996e-09 | 0.0071853 | 0.0071854 | 0.0071854 | 0.97581 | -0.17643 | 0.97571 | -0.17719 | 2.6613
32 | -0.0049107 | -0.0012108 | 0.004914 | 0.0012109 | 3.2961e-06 | 8.7835e-08 | 0.0074812 | 0.0074808 | 0.0074812 | 0.97581 | -0.17643 | 0.97649 | -0.17142 | 2.7708
33 | 0.0047162 | 0.0011622 | -0.0047147 | -0.0011622 | 1.5294e-06 | -4.4601e-09 | 0.0071854 | 0.0071856 | 0.0071856 | 0.97571 | -0.17719 | 0.97538 | -0.17961 | 2.6613
34 | 0.00037792 | 9.4183e-05 | -0.00037791 | -9.4714e-05 | 8.8693e-09 | -5.3045e-07 | 0.00057635 | 0.00057655 | 0.00057655 | 0.97538 | -0.17961 | 0.97536 | -0.17978 | 0.21354

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.018136 | 0.004319

## res_load
| p_mw | q_mvar
0 | 0.0073195 | 0.0018344
1 | 0.00072886 | 0.00018267
2 | 0.00020524 | 5.1438e-05
3 | 0.00056959 | 0.00014275
4 | 0.00011107 | 2.7837e-05
5 | 0.00020609 | 5.1651e-05
6 | 0.00044777 | 0.00011222
7 | 0.00075391 | 0.00018895
8 | 0.00026065 | 6.5326e-05
9 | 0.00075066 | 0.00018813
10 | 0.00032271 | 8.0879e-05
11 | 0.00047844 | 0.00011991
12 | 0.00018775 | 4.7055e-05
13 | 0.00030825 | 7.7256e-05
14 | 0.00013416 | 3.3623e-05
15 | 0.0003144 | 7.8795e-05
16 | 0.00014197 | 3.5581e-05
17 | 0.00017748 | 4.4481e-05
18 | 0.0031129 | 0.00078017
19 | 0.00019402 | 4.8625e-05
20 | 0.00037791 | 9.4714e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1