## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1375-4_1_3_node_94 | 0.4 | n |  | TRUE
1 | bus_LV_1375-4_1_3_node_92 | 0.4 | n |  | TRUE
2 | bus_LV_1375-4_1_3_node_33 | 0.4 | n |  | TRUE
3 | bus_LV_1375-4_1_3_node_34 | 0.4 | n |  | TRUE
4 | bus_LV_1375-4_1_3_node_90 | 0.4 | n |  | TRUE
5 | bus_LV_1375-4_1_3_node_159 | 0.4 | n |  | TRUE
6 | bus_LV_1375-4_1_3_node_85 | 0.4 | n |  | TRUE
7 | bus_LV_1375-4_1_3_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1375-4_1_3_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_1375-4_1_3_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1375-4_1_3_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1375-4_1_3_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_1375-4_1_3_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_1375-4_1_3_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_1375-4_1_3_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_1375-4_1_3_node_51 | 0.4 | n |  | TRUE
16 | bus_LV_1375-4_1_3_node_49 | 0.4 | n |  | TRUE
17 | bus_LV_1375-4_1_3_node_80 | 0.4 | n |  | TRUE
18 | bus_LV_1375-4_1_3_node_68 | 0.4 | n |  | TRUE
19 | bus_LV_1375-4_1_3_node_66 | 0.4 | n |  | TRUE
20 | bus_LV_1375-4_1_3_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_1375-4_1_3_node_77 | 0.4 | n |  | TRUE
22 | bus_LV_1375-4_1_3_node_75 | 0.4 | n |  | TRUE
23 | bus_LV_1375-4_1_3_node_50 | 0.4 | n |  | TRUE
24 | bus_LV_1375-4_1_3_node_73 | 0.4 | n |  | TRUE
25 | bus_LV_1375-4_1_3_node_67 | 0.4 | n |  | TRUE
26 | bus_LV_1375-4_1_3_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_1375-4_1_3_node_45 | 0.4 | n |  | TRUE
28 | bus_LV_1375-4_1_3_node_46 | 0.4 | n |  | TRUE
29 | bus_LV_1375-4_1_3_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_1375-4_1_3_node_135 | 0.4 | n |  | TRUE
31 | bus_LV_1375-4_1_3_node_136 | 0.4 | n |  | TRUE
32 | bus_LV_1375-4_1_3_node_134 | 0.4 | n |  | TRUE
33 | bus_LV_1375-4_1_3_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_1375-4_1_3_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1375-4_1_3_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_1375-4_1_3_node_93 | 0.4 | n |  | TRUE
37 | bus_LV_1375-4_1_3_node_157 | 0.4 | n |  | TRUE
38 | bus_LV_1375-4_1_3_node_133 | 0.4 | n |  | TRUE
39 | bus_LV_1375-4_1_3_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_1375-4_1_3_node_54 | 0.4 | n |  | TRUE
41 | bus_LV_1375-4_1_3_node_60 | 0.4 | n |  | TRUE
42 | bus_LV_1375-4_1_3_node_53 | 0.4 | n |  | TRUE
43 | bus_LV_1375-4_1_3_node_78 | 0.4 | n |  | TRUE
44 | bus_LV_1375-4_1_3_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_1375-4_1_3_node_61 | 0.4 | n |  | TRUE
46 | bus_LV_1375-4_1_3_node_55 | 0.4 | n |  | TRUE
47 | bus_LV_1375-4_1_3_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_1375-4_1_3_node_57 | 0.4 | n |  | TRUE
49 | bus_LV_1375-4_1_3_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_1375-4_1_3_node_59 | 0.4 | n |  | TRUE
51 | bus_LV_1375-4_1_3_node_65 | 0.4 | n |  | TRUE
52 | bus_LV_1375-4_1_3_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_1375-4_1_3_node_63 | 0.4 | n |  | TRUE
54 | bus_LV_1375-4_1_3_node_64 | 0.4 | n |  | TRUE
55 | bus_LV_1375-4_1_3_node_71 | 0.4 | n |  | TRUE
56 | bus_LV_1375-4_1_3_node_72 | 0.4 | n |  | TRUE
57 | bus_LV_1375-4_1_3_node_74 | 0.4 | n |  | TRUE
58 | bus_LV_1375-4_1_3_node_105 | 0.4 | n |  | TRUE
59 | bus_LV_1375-4_1_3_node_112 | 0.4 | n |  | TRUE
60 | bus_LV_1375-4_1_3_node_99 | 0.4 | n |  | TRUE
61 | bus_LV_1375-4_1_3_node_96 | 0.4 | n |  | TRUE
62 | bus_LV_1375-4_1_3_node_97 | 0.4 | n |  | TRUE
63 | bus_LV_1375-4_1_3_node_79 | 0.4 | n |  | TRUE
64 | bus_LV_1375-4_1_3_node_81 | 0.4 | n |  | TRUE
65 | bus_LV_1375-4_1_3_node_82 | 0.4 | n |  | TRUE
66 | bus_LV_1375-4_1_3_node_83 | 0.4 | n |  | TRUE
67 | bus_LV_1375-4_1_3_node_84 | 0.4 | n |  | TRUE
68 | bus_LV_1375-4_1_3_node_87 | 0.4 | n |  | TRUE
69 | bus_LV_1375-4_1_3_node_88 | 0.4 | n |  | TRUE
70 | bus_LV_1375-4_1_3_node_89 | 0.4 | n |  | TRUE
71 | bus_LV_1375-4_1_3_node_91 | 0.4 | n |  | TRUE
72 | bus_LV_1375-4_1_3_node_95 | 0.4 | n |  | TRUE
73 | bus_LV_1375-4_1_3_node_147 | 0.4 | n |  | TRUE
74 | bus_LV_1375-4_1_3_node_146 | 0.4 | n |  | TRUE
75 | bus_LV_1375-4_1_3_node_98 | 0.4 | n |  | TRUE
76 | bus_LV_1375-4_1_3_node_104 | 0.4 | n |  | TRUE
77 | bus_LV_1375-4_1_3_node_102 | 0.4 | n |  | TRUE
78 | bus_LV_1375-4_1_3_node_100 | 0.4 | n |  | TRUE
79 | bus_LV_1375-4_1_3_node_101 | 0.4 | n |  | TRUE
80 | bus_LV_1375-4_1_3_node_103 | 0.4 | n |  | TRUE
81 | bus_LV_1375-4_1_3_node_106 | 0.4 | n |  | TRUE
82 | bus_LV_1375-4_1_3_node_110 | 0.4 | n |  | TRUE
83 | bus_LV_1375-4_1_3_node_113 | 0.4 | n |  | TRUE
84 | bus_LV_1375-4_1_3_node_108 | 0.4 | n |  | TRUE
85 | bus_LV_1375-4_1_3_node_107 | 0.4 | n |  | TRUE
86 | bus_LV_1375-4_1_3_node_109 | 0.4 | n |  | TRUE
87 | bus_LV_1375-4_1_3_node_111 | 0.4 | n |  | TRUE
88 | bus_LV_1375-4_1_3_node_115 | 0.4 | n |  | TRUE
89 | bus_LV_1375-4_1_3_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_1375-4_1_3_node_114 | 0.4 | n |  | TRUE
91 | bus_LV_1375-4_1_3_node_116 | 0.4 | n |  | TRUE
92 | bus_LV_1375-4_1_3_node_154 | 0.4 | n |  | TRUE
93 | bus_LV_1375-4_1_3_node_155 | 0.4 | n |  | TRUE
94 | bus_LV_1375-4_1_3_node_118 | 0.4 | n |  | TRUE
95 | bus_LV_1375-4_1_3_node_156 | 0.4 | n |  | TRUE
96 | bus_LV_1375-4_1_3_node_119 | 0.4 | n |  | TRUE
97 | bus_LV_1375-4_1_3_node_120 | 0.4 | n |  | TRUE
98 | bus_LV_1375-4_1_3_node_121 | 0.4 | n |  | TRUE
99 | bus_LV_1375-4_1_3_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_1375-4_1_3_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_1375-4_1_3_node_124 | 0.4 | n |  | TRUE
102 | bus_LV_1375-4_1_3_node_125 | 0.4 | n |  | TRUE
103 | bus_LV_1375-4_1_3_node_126 | 0.4 | n |  | TRUE
104 | bus_LV_1375-4_1_3_node_138 | 0.4 | n |  | TRUE
105 | bus_LV_1375-4_1_3_node_143 | 0.4 | n |  | TRUE
106 | bus_LV_1375-4_1_3_node_139 | 0.4 | n |  | TRUE
107 | bus_LV_1375-4_1_3_node_131 | 0.4 | n |  | TRUE
108 | bus_LV_1375-4_1_3_node_141 | 0.4 | n |  | TRUE
109 | bus_LV_1375-4_1_3_node_127 | 0.4 | n |  | TRUE
110 | bus_LV_1375-4_1_3_node_128 | 0.4 | n |  | TRUE
111 | bus_LV_1375-4_1_3_node_129 | 0.4 | n |  | TRUE
112 | bus_LV_1375-4_1_3_node_130 | 0.4 | n |  | TRUE
113 | bus_LV_1375-4_1_3_node_132 | 0.4 | n |  | TRUE
114 | bus_LV_1375-4_1_3_node_148 | 0.4 | n |  | TRUE
115 | bus_LV_1375-4_1_3_node_149 | 0.4 | n |  | TRUE
116 | bus_LV_1375-4_1_3_node_140 | 0.4 | n |  | TRUE
117 | bus_LV_1375-4_1_3_node_142 | 0.4 | n |  | TRUE
118 | bus_LV_1375-4_1_3_node_144 | 0.4 | n |  | TRUE
119 | bus_LV_1375-4_1_3_node_145 | 0.4 | n |  | TRUE
120 | bus_MV_135_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1375-4_1_3_load_94 | 0 | 0.00021408 | 5.3653e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1375-4_1_3_load_92 | 1 | 0.00018186 | 4.5579e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1375-4_1_3_load_33 | 2 | 0.00029524 | 7.3995e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1375-4_1_3_load_159 | 5 | 0.00037057 | 9.2875e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1375-4_1_3_load_24 | 7 | 0.0002291 | 5.7419e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1375-4_1_3_load_29 | 11 | 0.00034022 | 8.5268e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1375-4_1_3_load_32 | 14 | 0.00079963 | 0.00020041 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1375-4_1_3_load_49 | 16 | 6.4815e-05 | 1.6244e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1375-4_1_3_load_80 | 17 | 0.00044638 | 0.00011187 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1375-4_1_3_load_68 | 18 | 0.00035302 | 8.8475e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1375-4_1_3_load_66 | 19 | 0.00049448 | 0.00012393 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1375-4_1_3_load_31 | 20 | 0.00056266 | 0.00014101 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1375-4_1_3_load_77 | 21 | 8.2726e-05 | 2.0733e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1375-4_1_3_load_75 | 22 | 0.0001591 | 3.9875e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1375-4_1_3_load_73 | 24 | 0.00022597 | 5.6634e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1375-4_1_3_load_45 | 27 | 0.00047834 | 0.00011988 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1375-4_1_3_load_37 | 29 | 0.0018882 | 0.00047323 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1375-4_1_3_load_135 | 30 | 0.00047809 | 0.00011982 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1375-4_1_3_load_136 | 31 | 0.00057708 | 0.00014463 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1375-4_1_3_load_134 | 32 | 0.00067509 | 0.00016919 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1375-4_1_3_load_36 | 33 | 0.00086518 | 0.00021683 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1375-4_1_3_load_38 | 34 | 0.00026501 | 6.6419e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1375-4_1_3_load_39 | 35 | 0.0005083 | 0.00012739 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1375-4_1_3_load_93 | 36 | 0.00011048 | 2.7689e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1375-4_1_3_load_157 | 37 | 0.00074177 | 0.0001859 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1375-4_1_3_load_133 | 38 | 0.0026063 | 0.00065319 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1375-4_1_3_load_54 | 40 | 0.00023421 | 5.8698e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1375-4_1_3_load_60 | 41 | 0.0001731 | 4.3384e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1375-4_1_3_load_53 | 42 | 0.00022147 | 5.5505e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1375-4_1_3_load_78 | 43 | 0.00017682 | 4.4316e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1375-4_1_3_load_76 | 44 | 0.0015067 | 0.00037762 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1375-4_1_3_load_61 | 45 | 0.00022512 | 5.642e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1375-4_1_3_load_55 | 46 | 0.00013628 | 3.4155e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1375-4_1_3_load_56 | 47 | 5.6068e-05 | 1.4052e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1375-4_1_3_load_65 | 51 | 0.0003723 | 9.3308e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1375-4_1_3_load_62 | 52 | 0.00014771 | 3.702e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1375-4_1_3_load_63 | 53 | 0.00014985 | 3.7555e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1375-4_1_3_load_64 | 54 | 0.0002039 | 5.1101e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1375-4_1_3_load_71 | 55 | 0.00047102 | 0.00011805 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1375-4_1_3_load_72 | 56 | 0.00019923 | 4.9932e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1375-4_1_3_load_74 | 57 | 0.00014949 | 3.7467e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1375-4_1_3_load_112 | 59 | 0.00019005 | 4.763e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1375-4_1_3_load_96 | 61 | 0.0012265 | 0.00030739 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1375-4_1_3_load_97 | 62 | 0.0048818 | 0.0012235 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1375-4_1_3_load_79 | 63 | 0.00028433 | 7.126e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1375-4_1_3_load_81 | 64 | 0.00066359 | 0.00016631 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1375-4_1_3_load_82 | 65 | 0.00037 | 9.2731e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1375-4_1_3_load_84 | 67 | 0.001418 | 0.00035539 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1375-4_1_3_load_87 | 68 | 0.0051502 | 0.0012908 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1375-4_1_3_load_88 | 69 | 0.0016157 | 0.00040493 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1375-4_1_3_load_89 | 70 | 0.00032349 | 8.1073e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1375-4_1_3_load_91 | 71 | 0.00040598 | 0.00010175 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1375-4_1_3_load_95 | 72 | 0.0004115 | 0.00010313 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1375-4_1_3_load_147 | 73 | 0.00048155 | 0.00012069 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1375-4_1_3_load_146 | 74 | 0.0021958 | 0.00055032 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1375-4_1_3_load_98 | 75 | 0.00033716 | 8.45e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1375-4_1_3_load_104 | 76 | 0.0021916 | 0.00054926 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1375-4_1_3_load_102 | 77 | 0.00046138 | 0.00011563 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1375-4_1_3_load_100 | 78 | 0.0033924 | 0.00085022 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1375-4_1_3_load_101 | 79 | 0.0032775 | 0.00082143 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1375-4_1_3_load_103 | 80 | 0.00026723 | 6.6974e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1375-4_1_3_load_106 | 81 | 0.00095435 | 0.00023918 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1375-4_1_3_load_110 | 82 | 0.0014131 | 0.00035415 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1375-4_1_3_load_113 | 83 | 0.00066625 | 0.00016698 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1375-4_1_3_load_108 | 84 | 0.0010951 | 0.00027445 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1375-4_1_3_load_107 | 85 | 0.0067953 | 0.0017031 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1375-4_1_3_load_109 | 86 | 0.0018713 | 0.000469 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1375-4_1_3_load_111 | 87 | 0.002676 | 0.00067068 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1375-4_1_3_load_115 | 88 | 0.0029699 | 0.00074432 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1375-4_1_3_load_117 | 89 | 0.00059944 | 0.00015023 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1375-4_1_3_load_114 | 90 | 0.00056116 | 0.00014064 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1375-4_1_3_load_154 | 92 | 0.0014407 | 0.00036107 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1375-4_1_3_load_155 | 93 | 0.00060537 | 0.00015172 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1375-4_1_3_load_118 | 94 | 0.0017252 | 0.00043239 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1375-4_1_3_load_156 | 95 | 0.0005391 | 0.00013511 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1375-4_1_3_load_119 | 96 | 0.00081556 | 0.0002044 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1375-4_1_3_load_120 | 97 | 0.0020842 | 0.00052236 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1375-4_1_3_load_121 | 98 | 0.0017628 | 0.0004418 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1375-4_1_3_load_122 | 99 | 0.0020811 | 0.00052158 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1375-4_1_3_load_123 | 100 | 0.0014967 | 0.00037512 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1375-4_1_3_load_124 | 101 | 0.0017236 | 0.00043197 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1375-4_1_3_load_125 | 102 | 0.0023073 | 0.00057827 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1375-4_1_3_load_143 | 105 | 0.0024342 | 0.00061008 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1375-4_1_3_load_139 | 106 | 0.0015581 | 0.0003905 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1375-4_1_3_load_131 | 107 | 0.0017522 | 0.00043913 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1375-4_1_3_load_141 | 108 | 0.0029102 | 0.00072936 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1375-4_1_3_load_127 | 109 | 0.003155 | 0.00079072 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1375-4_1_3_load_128 | 110 | 0.00057315 | 0.00014364 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1375-4_1_3_load_129 | 111 | 0.0015647 | 0.00039215 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1375-4_1_3_load_130 | 112 | 0.0058265 | 0.0014603 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1375-4_1_3_load_132 | 113 | 0.00046436 | 0.00011638 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1375-4_1_3_load_148 | 114 | 0.00030367 | 7.6107e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1375-4_1_3_load_149 | 115 | 0.00056672 | 0.00014203 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1375-4_1_3_load_140 | 116 | 0.0033477 | 0.00083901 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1375-4_1_3_load_142 | 117 | 0.0002841 | 7.1203e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1375-4_1_3_load_144 | 118 | 0.0020654 | 0.00051765 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1375-4_1_3_load_145 | 119 | 0.0010375 | 0.00026003 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 83 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1375-4_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.011831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1375-4_1_3_line_1 | NAYY 4x150 SE | 1 | 36 | 0.016753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1375-4_1_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.12248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1375-4_1_3_line_3 | NAYY 4x150 SE | 3 | 26 | 0.26996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1375-4_1_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.008946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1375-4_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.14363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1375-4_1_3_line_6 | NAYY 4x150 SE | 6 | 68 | 0.077378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1375-4_1_3_line_7 | NAYY 4x150 SE | 6 | 66 | 0.002949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1375-4_1_3_line_8 | NAYY 4x150 SE | 7 | 8 | 0.0038187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1375-4_1_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.3023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1375-4_1_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.011198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1375-4_1_3_line_11 | NAYY 4x150 SE | 9 | 11 | 0.11445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1375-4_1_3_line_12 | NAYY 4x150 SE | 9 | 12 | 0.069744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1375-4_1_3_line_13 | NAYY 4x150 SE | 10 | 13 | 0.065877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1375-4_1_3_line_14 | NAYY 4x150 SE | 10 | 14 | 0.02668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1375-4_1_3_line_15 | NAYY 4x150 SE | 11 | 17 | 0.01962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1375-4_1_3_line_16 | NAYY 4x150 SE | 12 | 18 | 0.083791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1375-4_1_3_line_17 | NAYY 4x150 SE | 12 | 19 | 0.046681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1375-4_1_3_line_18 | NAYY 4x150 SE | 13 | 15 | 0.00491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1375-4_1_3_line_19 | NAYY 4x150 SE | 13 | 16 | 0.20126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1375-4_1_3_line_20 | NAYY 4x150 SE | 14 | 20 | 0.0051885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1375-4_1_3_line_21 | NAYY 4x150 SE | 15 | 21 | 0.083356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1375-4_1_3_line_22 | NAYY 4x150 SE | 15 | 22 | 0.14641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1375-4_1_3_line_23 | NAYY 4x150 SE | 16 | 23 | 0.14758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1375-4_1_3_line_24 | NAYY 4x150 SE | 18 | 24 | 0.095853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1375-4_1_3_line_25 | NAYY 4x150 SE | 19 | 25 | 0.21654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1375-4_1_3_line_26 | NAYY 4x150 SE | 21 | 43 | 0.0060267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1375-4_1_3_line_27 | NAYY 4x150 SE | 22 | 44 | 0.017719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1375-4_1_3_line_28 | NAYY 4x150 SE | 23 | 39 | 0.039136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1375-4_1_3_line_29 | NAYY 4x150 SE | 24 | 57 | 0.039999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1375-4_1_3_line_30 | NAYY 4x150 SE | 25 | 55 | 0.19485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1375-4_1_3_line_31 | NAYY 4x150 SE | 26 | 27 | 0.020779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1375-4_1_3_line_32 | NAYY 4x150 SE | 26 | 28 | 0.30612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1375-4_1_3_line_33 | NAYY 4x150 SE | 26 | 29 | 0.082557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1375-4_1_3_line_34 | NAYY 4x150 SE | 28 | 30 | 0.016627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1375-4_1_3_line_35 | NAYY 4x150 SE | 28 | 31 | 0.071669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1375-4_1_3_line_36 | NAYY 4x150 SE | 28 | 32 | 0.029393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1375-4_1_3_line_37 | NAYY 4x150 SE | 29 | 33 | 0.050621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1375-4_1_3_line_38 | NAYY 4x150 SE | 31 | 37 | 0.023638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1375-4_1_3_line_39 | NAYY 4x150 SE | 32 | 38 | 0.007261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1375-4_1_3_line_40 | NAYY 4x150 SE | 33 | 34 | 0.17399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1375-4_1_3_line_41 | NAYY 4x150 SE | 34 | 35 | 0.0087392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1375-4_1_3_line_42 | NAYY 4x150 SE | 35 | 36 | 0.14484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1375-4_1_3_line_43 | NAYY 4x150 SE | 38 | 113 | 0.014805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1375-4_1_3_line_44 | NAYY 4x150 SE | 39 | 40 | 0.031471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1375-4_1_3_line_45 | NAYY 4x150 SE | 39 | 41 | 0.047312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1375-4_1_3_line_46 | NAYY 4x150 SE | 40 | 42 | 0.009066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1375-4_1_3_line_47 | NAYY 4x150 SE | 41 | 45 | 0.050089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1375-4_1_3_line_48 | NAYY 4x150 SE | 43 | 63 | 0.14061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1375-4_1_3_line_49 | NAYY 4x150 SE | 45 | 49 | 0.042098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1375-4_1_3_line_50 | NAYY 4x150 SE | 46 | 47 | 0.025515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1375-4_1_3_line_51 | NAYY 4x150 SE | 47 | 48 | 0.0061591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1375-4_1_3_line_52 | NAYY 4x150 SE | 48 | 49 | 0.090355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1375-4_1_3_line_53 | NAYY 4x150 SE | 48 | 50 | 0.017588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1375-4_1_3_line_54 | NAYY 4x150 SE | 50 | 51 | 0.040425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1375-4_1_3_line_55 | NAYY 4x150 SE | 50 | 52 | 0.039317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1375-4_1_3_line_56 | NAYY 4x150 SE | 52 | 53 | 0.011323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1375-4_1_3_line_57 | NAYY 4x150 SE | 53 | 54 | 0.11159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1375-4_1_3_line_58 | NAYY 4x150 SE | 55 | 56 | 0.032633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1375-4_1_3_line_59 | NAYY 4x150 SE | 57 | 61 | 0.030612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1375-4_1_3_line_60 | NAYY 4x150 SE | 58 | 59 | 0.044692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_1375-4_1_3_line_61 | NAYY 4x150 SE | 58 | 60 | 0.008757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
62 | LV_1375-4_1_3_line_62 | NAYY 4x150 SE | 59 | 83 | 0.070383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_1375-4_1_3_line_63 | NAYY 4x150 SE | 60 | 76 | 0.010821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
64 | LV_1375-4_1_3_line_64 | NAYY 4x150 SE | 60 | 75 | 0.0089263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1375-4_1_3_line_65 | NAYY 4x150 SE | 61 | 62 | 0.0011516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1375-4_1_3_line_66 | NAYY 4x150 SE | 62 | 75 | 0.05972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1375-4_1_3_line_67 | NAYY 4x150 SE | 64 | 65 | 0.019476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1375-4_1_3_line_68 | NAYY 4x150 SE | 64 | 66 | 0.035559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1375-4_1_3_line_69 | NAYY 4x150 SE | 65 | 67 | 0.052051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1375-4_1_3_line_70 | NAYY 4x150 SE | 68 | 69 | 0.091548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1375-4_1_3_line_71 | NAYY 4x150 SE | 69 | 70 | 0.035498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1375-4_1_3_line_72 | NAYY 4x150 SE | 70 | 71 | 0.04918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1375-4_1_3_line_73 | NAYY 4x150 SE | 71 | 72 | 0.01128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1375-4_1_3_line_74 | NAYY 4x150 SE | 72 | 73 | 0.026802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1375-4_1_3_line_75 | NAYY 4x150 SE | 73 | 74 | 0.0033959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1375-4_1_3_line_76 | NAYY 4x150 SE | 74 | 119 | 0.030563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1375-4_1_3_line_77 | NAYY 4x150 SE | 76 | 77 | 0.0071306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
78 | LV_1375-4_1_3_line_78 | NAYY 4x150 SE | 77 | 78 | 0.0070607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
79 | LV_1375-4_1_3_line_79 | NAYY 4x150 SE | 78 | 79 | 0.0040293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
80 | LV_1375-4_1_3_line_80 | NAYY 4x150 SE | 79 | 80 | 0.00031748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
81 | LV_1375-4_1_3_line_81 | NAYY 4x150 SE | 80 | 81 | 0.019648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
82 | LV_1375-4_1_3_line_82 | NAYY 4x150 SE | 81 | 82 | 0.021567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
83 | LV_1375-4_1_3_line_83 | NAYY 4x150 SE | 82 | 84 | 0.0034696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
84 | LV_1375-4_1_3_line_84 | NAYY 4x150 SE | 83 | 90 | 0.0033467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1375-4_1_3_line_85 | NAYY 4x150 SE | 84 | 85 | 0.0051851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_1375-4_1_3_line_86 | NAYY 4x150 SE | 85 | 86 | 0.023954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
87 | LV_1375-4_1_3_line_87 | NAYY 4x150 SE | 86 | 87 | 0.032847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_1375-4_1_3_line_88 | NAYY 4x150 SE | 87 | 88 | 0.010103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_1375-4_1_3_line_89 | NAYY 4x150 SE | 88 | 89 | 0.014423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_1375-4_1_3_line_90 | NAYY 4x150 SE | 89 | 94 | 0.00083297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
91 | LV_1375-4_1_3_line_91 | NAYY 4x150 SE | 90 | 91 | 0.025328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1375-4_1_3_line_92 | NAYY 4x150 SE | 91 | 92 | 0.011279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1375-4_1_3_line_93 | NAYY 4x150 SE | 91 | 93 | 0.024928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1375-4_1_3_line_94 | NAYY 4x150 SE | 93 | 95 | 0.019543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1375-4_1_3_line_95 | NAYY 4x150 SE | 94 | 96 | 0.009902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_1375-4_1_3_line_96 | NAYY 4x150 SE | 96 | 97 | 0.010454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
97 | LV_1375-4_1_3_line_97 | NAYY 4x150 SE | 97 | 98 | 0.005608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
98 | LV_1375-4_1_3_line_98 | NAYY 4x150 SE | 98 | 99 | 0.016409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
99 | LV_1375-4_1_3_line_99 | NAYY 4x150 SE | 99 | 100 | 0.0080063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
100 | LV_1375-4_1_3_line_100 | NAYY 4x150 SE | 100 | 101 | 0.0045675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
101 | LV_1375-4_1_3_line_101 | NAYY 4x150 SE | 101 | 102 | 0.020758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
102 | LV_1375-4_1_3_line_102 | NAYY 4x150 SE | 102 | 103 | 0.011295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1375-4_1_3_line_103 | NAYY 4x150 SE | 103 | 104 | 0.01679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1375-4_1_3_line_104 | NAYY 4x150 SE | 103 | 105 | 0.0158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1375-4_1_3_line_105 | NAYY 4x150 SE | 104 | 106 | 0.064516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1375-4_1_3_line_106 | NAYY 4x150 SE | 104 | 107 | 0.016518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1375-4_1_3_line_107 | NAYY 4x150 SE | 105 | 108 | 0.016465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1375-4_1_3_line_108 | NAYY 4x150 SE | 106 | 114 | 0.015368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1375-4_1_3_line_109 | NAYY 4x150 SE | 107 | 111 | 0.023277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1375-4_1_3_line_110 | NAYY 4x150 SE | 108 | 116 | 0.0018051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1375-4_1_3_line_111 | NAYY 4x150 SE | 109 | 110 | 0.023796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1375-4_1_3_line_112 | NAYY 4x150 SE | 109 | 111 | 0.0021607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1375-4_1_3_line_113 | NAYY 4x150 SE | 110 | 112 | 0.0057604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1375-4_1_3_line_114 | NAYY 4x150 SE | 112 | 113 | 0.013469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1375-4_1_3_line_115 | NAYY 4x150 SE | 114 | 115 | 0.044644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1375-4_1_3_line_116 | NAYY 4x150 SE | 116 | 117 | 0.0081872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1375-4_1_3_line_117 | NAYY 4x150 SE | 117 | 118 | 0.014722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1375-4_1_3_line_118 | NAYY 4x150 SE | 118 | 119 | 0.00084589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1375-4_1_3_trafo_113 | 0.25 MVA 20/0.4 kV | 120 | 83 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2704043.9118 | 1211041.8207 | 2704032.8077 | 1211045.9027
1 | 2704032.8077 | 1211045.9027 | 2704025.7204 | 1211048.5082 | 2704017.4065 | 1211052.4519
2 | 2703964.8552 | 1211295.9441 | 2703962.8189 | 1211302.4465 | 2703956.8506 | 1211314.7624 | 2703954.3101 | 1211325.7703 | 2703953.2257 | 1211351.3472 | 2703954.1432 | 1211371.9556 | 2703959.0307 | 1211385.0055 | 2703964.7195 | 1211394.3779 | 2703969.1816 | 1211401.7498 | 2703976.1712 | 1211410.1657
3 | 2703845.6832 | 1211412.662 | 2703841.5918 | 1211465.1612 | 2703866.2978 | 1211436.5155 | 2703882.4326 | 1211417.3607 | 2703886.9557 | 1211408.5888 | 2703889.0731 | 1211399.6083 | 2703890.9306 | 1211379.3708 | 2703894.9613 | 1211363.9634 | 2703902.2572 | 1211351.7819 | 2703923.006 | 1211328.26 | 2703939.8785 | 1211311.2864 | 2703949.0515 | 1211303.4852 | 2703961.0629 | 1211297.2345 | 2703964.8552 | 1211295.9441
4 | 2703687.6525 | 1211966.5154 | 2703690.0904 | 1211973.1625 | 2703689.6106 | 1211974.9666
5 | 2703689.6106 | 1211974.9666 | 2703636.2525 | 1212002.5699 | 2703569.0511 | 1212038.3391 | 2703561.3995 | 1212039.585
6 | 2703561.3995 | 1212039.585 | 2703548.2208 | 1211964.4031 | 2703548.0336 | 1211963.3704
7 | 2703561.3995 | 1212039.585 | 2703561.9343 | 1212042.4852
8 | 2703610.1536 | 1210746.7197 | 2703608.4819 | 1210750.153
9 | 2703512.3251 | 1211036.6147 | 2703519.0831 | 1211015.5504 | 2703582.6678 | 1210821.5285 | 2703602.1923 | 1210763.0708 | 2703608.4819 | 1210750.153
10 | 2703610.1536 | 1210746.7197 | 2703616.505 | 1210738.591 | 2703617.0569 | 1210737.8889
11 | 2703512.3251 | 1211036.6147 | 2703440.5875 | 1211032.3007 | 2703411.0286 | 1211023.938 | 2703402.9844 | 1211015.2238
12 | 2703495.9494 | 1211104.2449 | 2703497.609 | 1211093.5884 | 2703498.312 | 1211088.1189 | 2703503.1968 | 1211065.0541 | 2703512.3251 | 1211036.6147
13 | 2703617.0569 | 1210737.8889 | 2703632.2664 | 1210718.2393 | 2703636.4359 | 1210713.197 | 2703638.6299 | 1210709.855 | 2703656.1738 | 1210684.92
14 | 2703617.0569 | 1210737.8889 | 2703609.1716 | 1210727.5558 | 2703615.7668 | 1210715.5688
15 | 2703389.6761 | 1211000.8072 | 2703402.9844 | 1211015.2238
16 | 2703495.9494 | 1211104.2449 | 2703499.4676 | 1211187.9623
17 | 2703495.9494 | 1211104.2449 | 2703477.8848 | 1211089.2209 | 2703460.5975 | 1211084.1509 | 2703455.6923 | 1211082.5184
18 | 2703659.1232 | 1210688.8518 | 2703656.1738 | 1210684.92
19 | 2703656.1738 | 1210684.92 | 2703710.3019 | 1210592.3065 | 2703759.3715 | 1210512.1415
20 | 2703618.2679 | 1210711.0229 | 2703615.7668 | 1210715.5688
21 | 2703659.1232 | 1210688.8518 | 2703663.8335 | 1210695.1158 | 2703674.519 | 1210723.199 | 2703676.6708 | 1210728.8404 | 2703685.8913 | 1210757.6765 | 2703687.9726 | 1210766.5961
22 | 2703659.1232 | 1210688.8518 | 2703690.2262 | 1210684.1222 | 2703698.9892 | 1210682.8848 | 2703716.9677 | 1210678.8611 | 2703735.2464 | 1210676.3771 | 2703739.7225 | 1210676.8775 | 2703754.9038 | 1210675.0402 | 2703793.6801 | 1210663.1285 | 2703796.7287 | 1210665.283 | 2703799.9697 | 1210669.2673
23 | 2703816.9451 | 1210376.8872 | 2703815.0409 | 1210385.8382 | 2703803.564 | 1210420.6741 | 2703796.9796 | 1210438.6611 | 2703776.4714 | 1210481.8459 | 2703762.479 | 1210507.0648 | 2703759.3715 | 1210512.1415
24 | 2703499.4676 | 1211187.9623 | 2703500.0588 | 1211202.0295 | 2703505.4384 | 1211283.626
25 | 2703253.3473 | 1211031.9682 | 2703262.4563 | 1211025.1988 | 2703291.5705 | 1211023.2681 | 2703316.3105 | 1211024.6197 | 2703334.5201 | 1211030.8728 | 2703364.0401 | 1211046.3061 | 2703413.5771 | 1211068.5024 | 2703455.6923 | 1211082.5184
26 | 2703689.342 | 1210772.4652 | 2703687.9726 | 1210766.5961
27 | 2703811.1513 | 1210683.0131 | 2703799.9697 | 1210669.2673
28 | 2703816.9451 | 1210376.8872 | 2703825.0992 | 1210338.6133
29 | 2703508.0698 | 1211323.538 | 2703505.4384 | 1211283.626
30 | 2703253.3473 | 1211031.9682 | 2703257.5681 | 1211047.63 | 2703270.3495 | 1211063.6069 | 2703279.2299 | 1211070.9102 | 2703292.0462 | 1211076.9697 | 2703307.5641 | 1211089.4138 | 2703315.8653 | 1211098.1192 | 2703317.3591 | 1211109.2863 | 2703315.258 | 1211125.7059 | 2703316.079 | 1211138.418 | 2703325.9997 | 1211165.9425 | 2703337.6869 | 1211194.3916
31 | 2703845.6832 | 1211412.662 | 2703830.812 | 1211398.1492
32 | 2703619.5041 | 1211566.1708 | 2703624.7951 | 1211562.1599 | 2703636.4689 | 1211552.9784 | 2703642.3306 | 1211548.933 | 2703655.6536 | 1211538.4459 | 2703678.6012 | 1211520.3764 | 2703702.5184 | 1211507.3051 | 2703723.9695 | 1211499.6949 | 2703739.0423 | 1211497.8557 | 2703760.2579 | 1211496.3569 | 2703794.9177 | 1211496.6378 | 2703812.9438 | 1211489.7466 | 2703828.0715 | 1211480.8369 | 2703837.31 | 1211470.1235 | 2703841.5918 | 1211465.1612 | 2703845.6832 | 1211412.662
33 | 2703845.6832 | 1211412.662 | 2703846.2417 | 1211374.0556 | 2703846.4398 | 1211330.1099
34 | 2703619.5041 | 1211566.1708 | 2703632.1285 | 1211575.3188 | 2703632.9229 | 1211575.9849
35 | 2703619.5041 | 1211566.1708 | 2703609.7247 | 1211552.9361 | 2703603.48 | 1211546.2229 | 2703584.6783 | 1211529.5402 | 2703577.8208 | 1211522.2271 | 2703570.9955 | 1211513.7495
36 | 2703619.5041 | 1211566.1708 | 2703596.3605 | 1211584.29
37 | 2703852.9945 | 1211280.0401 | 2703852.9945 | 1211280.0401 | 2703849.1984 | 1211298.1313 | 2703846.4778 | 1211321.6672 | 2703846.4398 | 1211330.1099
38 | 2703570.9955 | 1211513.7495 | 2703570.8573 | 1211513.5778 | 2703561.1948 | 1211500.1673 | 2703557.588 | 1211494.2985
39 | 2703590.6432 | 1211588.7661 | 2703596.3605 | 1211584.29
40 | 2703852.9945 | 1211280.0401 | 2703860.5848 | 1211267.9749 | 2703866.6664 | 1211253.515 | 2703872.0591 | 1211236.2745 | 2703874.968 | 1211220.2583 | 2703880.0565 | 1211193.8727 | 2703877.736 | 1211180.0447 | 2703873.1191 | 1211166.2769 | 2703865.5086 | 1211154.625 | 2703862.901 | 1211148.9868 | 2703862.9841 | 1211140.2932 | 2703868.564 | 1211131.5064 | 2703882.0951 | 1211124.9012
41 | 2703882.0951 | 1211124.9012 | 2703889.9485 | 1211121.0676
42 | 2704017.4065 | 1211052.4519 | 2703999.1101 | 1211061.1309 | 2703963.7835 | 1211081.5074 | 2703959.0539 | 1211084.6716 | 2703904.6322 | 1211113.8998 | 2703889.9485 | 1211121.0676
43 | 2703590.6432 | 1211588.7661 | 2703578.9858 | 1211597.8928
44 | 2703825.0992 | 1210338.6133 | 2703846.4751 | 1210344.734 | 2703850.3047 | 1210347.447 | 2703851.04 | 1210351.9296
45 | 2703825.0992 | 1210338.6133 | 2703827.4004 | 1210327.8235 | 2703834.7219 | 1210292.2906
46 | 2703849.5793 | 1210360.8772 | 2703851.04 | 1210351.9296
47 | 2703834.7219 | 1210292.2906 | 2703836.7418 | 1210282.4875 | 2703847.2523 | 1210243.8099
48 | 2703689.342 | 1210772.4652 | 2703695.8372 | 1210800.3016 | 2703709.9925 | 1210860.49 | 2703718.1793 | 1210893.6668 | 2703730.4827 | 1210903.9263
49 | 2703862.6208 | 1210204.6609 | 2703853.9435 | 1210225.38 | 2703848.771 | 1210238.2212 | 2703847.2523 | 1210243.8099
50 | 2703968.0902 | 1210232.3352 | 2703960.5171 | 1210235.6653 | 2703952.444 | 1210242.6407 | 2703946.7932 | 1210245.9977
51 | 2703941.498 | 1210249.1435 | 2703946.7932 | 1210245.9977
52 | 2703941.498 | 1210249.1435 | 2703862.6208 | 1210204.6609
53 | 2703941.498 | 1210249.1435 | 2703951.7738 | 1210256.2275 | 2703956.2607 | 1210258.7407
54 | 2703941.3355 | 1210295.0952 | 2703950.3037 | 1210283.8658 | 2703953.5004 | 1210275.7935 | 2703955.6646 | 1210268.515 | 2703956.2607 | 1210258.7407
55 | 2703956.2607 | 1210258.7407 | 2703967.5232 | 1210265.0414 | 2703974.574 | 1210270.0456 | 2703975.8149 | 1210280.8415 | 2703972.1321 | 1210286.6755
56 | 2703972.1321 | 1210286.6755 | 2703970.3581 | 1210289.4858 | 2703970.0464 | 1210297.4797
57 | 2703970.0464 | 1210297.4797 | 2703969.6293 | 1210308.1752 | 2703974.4309 | 1210313.129 | 2703985.4566 | 1210312.5096 | 2703999.6118 | 1210307.6751 | 2704021.7433 | 1210312.7422 | 2704039.2324 | 1210327.2685 | 2704045.7244 | 1210329.0051 | 2704053.7124 | 1210326.9096 | 2704057.7015 | 1210320.4747
58 | 2703348.7832 | 1211224.0002 | 2703349.1921 | 1211215.3234 | 2703343.1132 | 1211206.0227 | 2703337.8507 | 1211194.7903 | 2703337.6869 | 1211194.3916
59 | 2703508.0698 | 1211323.538 | 2703508.1326 | 1211324.4892 | 2703509.9412 | 1211354.0931
60 | 2703520.8836 | 1211424.4253 | 2703526.8528 | 1211429.9439 | 2703530.3006 | 1211438.8545 | 2703533.3006 | 1211455.1736 | 2703534.4263 | 1211465.5288
61 | 2703512.1238 | 1211423.7951 | 2703520.8836 | 1211424.4253
62 | 2703534.4263 | 1211465.5288 | 2703535.26 | 1211473.1981 | 2703533.4508 | 1211485.0306 | 2703529.3928 | 1211510.8228 | 2703526.6117 | 1211532.2341 | 2703526.5862 | 1211535.2319
63 | 2703512.1238 | 1211423.7951 | 2703507.9289 | 1211433.77
64 | 2703512.1238 | 1211423.7951 | 2703512.2877 | 1211414.8703
65 | 2703510.0114 | 1211355.2426 | 2703509.9412 | 1211354.0931
66 | 2703510.0114 | 1211355.2426 | 2703510.346 | 1211360.7198 | 2703512.351 | 1211386.1948 | 2703512.522 | 1211404.3661 | 2703512.4026 | 1211408.6115 | 2703512.2877 | 1211414.8703
67 | 2703525.6916 | 1212067.7139 | 2703524.0779 | 1212056.2267 | 2703524.6933 | 1212052.3012 | 2703527.1849 | 1212049.2979 | 2703527.1849 | 1212049.2979
68 | 2703561.9343 | 1212042.4852 | 2703531.276 | 1212047.4009 | 2703527.1849 | 1212049.2979
69 | 2703525.6916 | 1212067.7139 | 2703528.6702 | 1212088.9183 | 2703533.2074 | 1212119.2194
70 | 2703548.0336 | 1211963.3704 | 2703531.7065 | 1211873.2903
71 | 2703531.7065 | 1211873.2903 | 2703525.3756 | 1211838.3611
72 | 2703516.4586 | 1211790.0387 | 2703519.5032 | 1211812.0304 | 2703525.1129 | 1211836.912 | 2703525.3756 | 1211838.3611
73 | 2703514.9117 | 1211778.8651 | 2703516.4586 | 1211790.0387
74 | 2703511.2362 | 1211752.3164 | 2703514.9117 | 1211778.8651
75 | 2703511.2362 | 1211752.3164 | 2703511.0689 | 1211751.1077 | 2703510.8018 | 1211748.9485
76 | 2703510.8018 | 1211748.9485 | 2703507.0502 | 1211718.6166
77 | 2703507.9289 | 1211433.77 | 2703505.1647 | 1211440.3431
78 | 2703502.4276 | 1211446.8516 | 2703505.1647 | 1211440.3431
79 | 2703502.4276 | 1211446.8516 | 2703500.8656 | 1211450.5658
80 | 2703500.7425 | 1211450.8585 | 2703500.8656 | 1211450.5658
81 | 2703500.7425 | 1211450.8585 | 2703497.0138 | 1211459.725 | 2703492.7644 | 1211468.8102
82 | 2703483.6269 | 1211488.3462 | 2703483.6269 | 1211488.3462 | 2703492.7644 | 1211468.8102
83 | 2703483.6269 | 1211488.3462 | 2703482.5027 | 1211491.6287
84 | 2703526.5577 | 1211538.5784 | 2703526.5862 | 1211535.2319
85 | 2703480.8226 | 1211496.5341 | 2703482.5027 | 1211491.6287
86 | 2703480.8226 | 1211496.5341 | 2703477.5584 | 1211506.0646 | 2703474.9244 | 1211519.6922
87 | 2703474.9244 | 1211519.6922 | 2703473.5337 | 1211526.8872 | 2703473.2577 | 1211550.6659 | 2703473.4975 | 1211552.3878
88 | 2703473.4975 | 1211552.3878 | 2703474.8907 | 1211562.3945
89 | 2703477.242 | 1211576.6078 | 2703476.4406 | 1211573.5261 | 2703474.8907 | 1211562.3945
90 | 2703477.4516 | 1211577.414 | 2703477.242 | 1211576.6078
91 | 2703532.1163 | 1211562.7512 | 2703528.4717 | 1211555.9831 | 2703526.4802 | 1211547.6872 | 2703526.5577 | 1211538.5784
92 | 2703532.1163 | 1211562.7512 | 2703523.1131 | 1211569.5775
93 | 2703532.1163 | 1211562.7512 | 2703551.8583 | 1211547.5312
94 | 2703567.3358 | 1211535.5989 | 2703551.8583 | 1211547.5312
95 | 2703479.9438 | 1211586.9972 | 2703477.4516 | 1211577.414
96 | 2703479.9438 | 1211586.9972 | 2703481.3494 | 1211592.4023 | 2703483.1569 | 1211596.9239
97 | 2703483.1569 | 1211596.9239 | 2703485.2384 | 1211602.1313
98 | 2703490.5858 | 1211617.6138 | 2703488.9537 | 1211611.4255 | 2703485.2384 | 1211602.1313
99 | 2703490.5858 | 1211617.6138 | 2703492.6277 | 1211625.3554
100 | 2703492.6277 | 1211625.3554 | 2703493.7925 | 1211629.7719
101 | 2703497.3242 | 1211650.2203 | 2703494.1947 | 1211631.2971 | 2703493.7925 | 1211629.7719
102 | 2703499.3661 | 1211661.308 | 2703498.5685 | 1211655.1564 | 2703497.3242 | 1211650.2203
103 | 2703512.1938 | 1211650.434 | 2703499.3661 | 1211661.308
104 | 2703499.3661 | 1211661.308 | 2703501.6268 | 1211676.9456
105 | 2703512.1938 | 1211650.434 | 2703517.8677 | 1211655.436 | 2703561.885 | 1211676.1145 | 2703569.1309 | 1211680.2029
106 | 2703512.1938 | 1211650.434 | 2703525.1586 | 1211640.1982
107 | 2703503.9128 | 1211693.2501 | 2703503.4915 | 1211689.8441 | 2703501.6268 | 1211676.9456
108 | 2703569.1309 | 1211680.2029 | 2703582.5155 | 1211687.7551
109 | 2703543.4281 | 1211625.7746 | 2703525.1586 | 1211640.1982
110 | 2703504.1343 | 1211695.0416 | 2703503.9128 | 1211693.2501
111 | 2703545.1239 | 1211624.4357 | 2703550.0211 | 1211620.5694 | 2703563.8448 | 1211609.7468
112 | 2703545.1239 | 1211624.4357 | 2703543.4281 | 1211625.7746
113 | 2703563.8448 | 1211609.7468 | 2703568.3805 | 1211606.1957
114 | 2703578.9858 | 1211597.8928 | 2703568.3805 | 1211606.1957
115 | 2703616.4485 | 1211715.2897 | 2703605.823 | 1211700.9061 | 2703582.5155 | 1211687.7551
116 | 2703505.1393 | 1211703.1669 | 2703504.1343 | 1211695.0416
117 | 2703505.1393 | 1211703.1669 | 2703506.9464 | 1211717.7771
118 | 2703506.9464 | 1211717.7771 | 2703507.0502 | 1211718.6166

## bus_geodata
| x | y | coords
0 | 2704043.9118 | 1211041.8207
1 | 2704032.8077 | 1211045.9027
2 | 2703976.1712 | 1211410.1657
3 | 2703964.8552 | 1211295.9441
4 | 2703689.6106 | 1211974.9666
5 | 2703687.6525 | 1211966.5154
6 | 2703561.3995 | 1212039.585
7 | 2703608.4819 | 1210750.153
8 | 2703610.1536 | 1210746.7197
9 | 2703512.3251 | 1211036.6147
10 | 2703617.0569 | 1210737.8889
11 | 2703402.9844 | 1211015.2238
12 | 2703495.9494 | 1211104.2449
13 | 2703656.1738 | 1210684.92
14 | 2703615.7668 | 1210715.5688
15 | 2703659.1232 | 1210688.8518
16 | 2703759.3715 | 1210512.1415
17 | 2703389.6761 | 1211000.8072
18 | 2703499.4676 | 1211187.9623
19 | 2703455.6923 | 1211082.5184
20 | 2703618.2679 | 1210711.0229
21 | 2703687.9725 | 1210766.5961
22 | 2703799.9697 | 1210669.2672
23 | 2703816.9451 | 1210376.8872
24 | 2703505.4384 | 1211283.626
25 | 2703253.3473 | 1211031.9682
26 | 2703845.6832 | 1211412.662
27 | 2703830.812 | 1211398.1492
28 | 2703619.5041 | 1211566.1708
29 | 2703846.4398 | 1211330.1099
30 | 2703632.9229 | 1211575.9849
31 | 2703570.9955 | 1211513.7495
32 | 2703596.3605 | 1211584.29
33 | 2703852.9945 | 1211280.0401
34 | 2703882.0951 | 1211124.9012
35 | 2703889.9485 | 1211121.0676
36 | 2704017.4065 | 1211052.4519
37 | 2703557.588 | 1211494.2985
38 | 2703590.6432 | 1211588.7661
39 | 2703825.0992 | 1210338.6133
40 | 2703851.04 | 1210351.9296
41 | 2703834.7219 | 1210292.2906
42 | 2703849.5793 | 1210360.8772
43 | 2703689.342 | 1210772.4652
44 | 2703811.1513 | 1210683.0131
45 | 2703847.2523 | 1210243.8099
46 | 2703968.0902 | 1210232.3352
47 | 2703946.7932 | 1210245.9977
48 | 2703941.498 | 1210249.1435
49 | 2703862.6208 | 1210204.6609
50 | 2703956.2607 | 1210258.7407
51 | 2703941.3355 | 1210295.0952
52 | 2703972.1321 | 1210286.6755
53 | 2703970.0464 | 1210297.4797
54 | 2704057.7015 | 1210320.4747
55 | 2703337.6869 | 1211194.3916
56 | 2703348.7832 | 1211224.0002
57 | 2703508.0698 | 1211323.538
58 | 2703520.8836 | 1211424.4253
59 | 2703534.4263 | 1211465.5288
60 | 2703512.1238 | 1211423.7951
61 | 2703509.9412 | 1211354.0931
62 | 2703510.0114 | 1211355.2426
63 | 2703730.4827 | 1210903.9263
64 | 2703527.1849 | 1212049.2979
65 | 2703525.6916 | 1212067.7139
66 | 2703561.9343 | 1212042.4852
67 | 2703533.2074 | 1212119.2194
68 | 2703548.0336 | 1211963.3704
69 | 2703531.7065 | 1211873.2903
70 | 2703525.3756 | 1211838.3611
71 | 2703516.4586 | 1211790.0387
72 | 2703514.9117 | 1211778.8651
73 | 2703511.2362 | 1211752.3164
74 | 2703510.8018 | 1211748.9485
75 | 2703512.2877 | 1211414.8703
76 | 2703507.9289 | 1211433.77
77 | 2703505.1647 | 1211440.3431
78 | 2703502.4276 | 1211446.8516
79 | 2703500.8656 | 1211450.5658
80 | 2703500.7425 | 1211450.8585
81 | 2703492.7644 | 1211468.8102
82 | 2703483.6269 | 1211488.3462
83 | 2703526.5862 | 1211535.2319
84 | 2703482.5027 | 1211491.6287
85 | 2703480.8226 | 1211496.5341
86 | 2703474.9244 | 1211519.6922
87 | 2703473.4975 | 1211552.3878
88 | 2703474.8907 | 1211562.3945
89 | 2703477.242 | 1211576.6078
90 | 2703526.5577 | 1211538.5784
91 | 2703532.1163 | 1211562.7512
92 | 2703523.1131 | 1211569.5775
93 | 2703551.8583 | 1211547.5312
94 | 2703477.4516 | 1211577.414
95 | 2703567.3358 | 1211535.5989
96 | 2703479.9438 | 1211586.9972
97 | 2703483.1569 | 1211596.9239
98 | 2703485.2384 | 1211602.1313
99 | 2703490.5858 | 1211617.6138
100 | 2703492.6277 | 1211625.3554
101 | 2703493.7925 | 1211629.7719
102 | 2703497.3242 | 1211650.2203
103 | 2703499.3661 | 1211661.308
104 | 2703512.1938 | 1211650.434
105 | 2703501.6268 | 1211676.9456
106 | 2703569.1309 | 1211680.2029
107 | 2703525.1586 | 1211640.1983
108 | 2703503.9128 | 1211693.2501
109 | 2703545.1239 | 1211624.4357
110 | 2703563.8448 | 1211609.7468
111 | 2703543.4281 | 1211625.7746
112 | 2703568.3805 | 1211606.1957
113 | 2703578.9858 | 1211597.8928
114 | 2703582.5155 | 1211687.7551
115 | 2703616.4485 | 1211715.2897
116 | 2703504.1343 | 1211695.0416
117 | 2703505.1393 | 1211703.1669
118 | 2703506.9464 | 1211717.7771
119 | 2703507.0502 | 1211718.6166
120 | 2703532.1163 | 1211562.7512

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97026 | -0.21083 | 0.00021408 | 5.3653e-05
1 | 0.97026 | -0.2108 | 0.00018186 | 4.5579e-05
2 | 0.9712 | -0.20401 | 0.00029524 | 7.3995e-05
3 | 0.97125 | -0.20362 | 0 | 0
4 | 0.97131 | -0.20278 | 0 | 0
5 | 0.9713 | -0.20282 | 0.00037057 | 9.2875e-05
6 | 0.97138 | -0.20221 | 0 | 0
7 | 0.98267 | -0.1229 | 0.0002291 | 5.7419e-05
8 | 0.98264 | -0.12313 | 0 | 0
9 | 0.98521 | -0.10441 | 0 | 0
10 | 0.98255 | -0.12379 | 0 | 0
11 | 0.98508 | -0.10534 | 0.00034022 | 8.5268e-05
12 | 0.98587 | -0.099571 | 0 | 0
13 | 0.98215 | -0.12673 | 0 | 0
14 | 0.9825 | -0.12416 | 0.00079963 | 0.00020041
15 | 0.98213 | -0.12684 | 0 | 0
16 | 0.98157 | -0.13102 | 6.4815e-05 | 1.6244e-05
17 | 0.98506 | -0.10543 | 0.00044638 | 0.00011187
18 | 0.98681 | -0.09272 | 0.00035302 | 8.8475e-05
19 | 0.98579 | -0.10015 | 0.00049448 | 0.00012393
20 | 0.98249 | -0.12419 | 0.00056266 | 0.00014101
21 | 0.98207 | -0.12733 | 8.2726e-05 | 2.0733e-05
22 | 0.98178 | -0.12938 | 0.0001591 | 3.9875e-05
23 | 0.98116 | -0.13405 | 0 | 0
24 | 0.98793 | -0.084544 | 0.00022597 | 5.6634e-05
25 | 0.98558 | -0.10171 | 0 | 0
26 | 0.97137 | -0.20271 | 0 | 0
27 | 0.97135 | -0.20281 | 0.00047834 | 0.00011988
28 | 0.97352 | -0.18686 | 0 | 0
29 | 0.97088 | -0.20627 | 0.0018882 | 0.00047323
30 | 0.97351 | -0.18695 | 0.00047809 | 0.00011982
31 | 0.97339 | -0.18786 | 0.00057708 | 0.00014463
32 | 0.97381 | -0.18478 | 0.00067509 | 0.00016919
33 | 0.97072 | -0.20744 | 0.00086518 | 0.00021683
34 | 0.97039 | -0.20984 | 0.00026501 | 6.6419e-05
35 | 0.97038 | -0.20994 | 0.0005083 | 0.00012739
36 | 0.97027 | -0.21073 | 0.00011048 | 2.7689e-05
37 | 0.97336 | -0.18805 | 0.00074177 | 0.0001859
38 | 0.97389 | -0.18422 | 0.0026063 | 0.00065319
39 | 0.98105 | -0.13485 | 0 | 0
40 | 0.98103 | -0.135 | 0.00023421 | 5.8698e-05
41 | 0.98095 | -0.13559 | 0.0001731 | 4.3384e-05
42 | 0.98103 | -0.13502 | 0.00022147 | 5.5505e-05
43 | 0.98206 | -0.12736 | 0.00017682 | 4.4316e-05
44 | 0.98174 | -0.12966 | 0.0015067 | 0.00037762
45 | 0.98085 | -0.13628 | 0.00022512 | 5.642e-05
46 | 0.98064 | -0.13784 | 0.00013628 | 3.4155e-05
47 | 0.98065 | -0.1378 | 5.6068e-05 | 1.4052e-05
48 | 0.98065 | -0.13779 | 0 | 0
49 | 0.98079 | -0.13676 | 0 | 0
50 | 0.98063 | -0.13795 | 0 | 0
51 | 0.98061 | -0.13811 | 0.0003723 | 9.3308e-05
52 | 0.9806 | -0.13816 | 0.00014771 | 3.702e-05
53 | 0.98059 | -0.1382 | 0.00014985 | 3.7555e-05
54 | 0.98056 | -0.13845 | 0.0002039 | 5.1101e-05
55 | 0.98539 | -0.10308 | 0.00047102 | 0.00011805
56 | 0.98539 | -0.10315 | 0.00019923 | 4.9932e-05
57 | 0.98842 | -0.081043 | 0.00014949 | 3.7467e-05
58 | 0.99095 | -0.062961 | 0 | 0
59 | 0.99446 | -0.0384 | 0.00019005 | 4.763e-05
60 | 0.99026 | -0.067794 | 0 | 0
61 | 0.98879 | -0.078318 | 0.0012265 | 0.00030739
62 | 0.98881 | -0.078201 | 0.0048818 | 0.0012235
63 | 0.98201 | -0.12778 | 0.00028433 | 7.126e-05
64 | 0.97125 | -0.20321 | 0.00066359 | 0.00016631
65 | 0.9712 | -0.20358 | 0.00037 | 9.2731e-05
66 | 0.97137 | -0.20228 | 0 | 0
67 | 0.97109 | -0.20436 | 0.001418 | 0.00035539
68 | 0.97171 | -0.19988 | 0.0051502 | 0.0012908
69 | 0.97278 | -0.19213 | 0.0016157 | 0.00040493
70 | 0.97327 | -0.18853 | 0.00032349 | 8.1073e-05
71 | 0.97399 | -0.18338 | 0.00040598 | 0.00010175
72 | 0.97416 | -0.18215 | 0.0004115 | 0.00010313
73 | 0.97458 | -0.17911 | 0.00048155 | 0.00012069
74 | 0.97464 | -0.17871 | 0.0021958 | 0.00055032
75 | 0.99006 | -0.069173 | 0.00033716 | 8.45e-05
76 | 0.98952 | -0.072938 | 0.0021916 | 0.00054926
77 | 0.98905 | -0.076253 | 0.00046138 | 0.00011563
78 | 0.98859 | -0.079521 | 0.0033924 | 0.00085022
79 | 0.98833 | -0.081317 | 0.0032775 | 0.00082143
80 | 0.98831 | -0.081454 | 0.00026723 | 6.6974e-05
81 | 0.98711 | -0.089871 | 0.00095435 | 0.00023918
82 | 0.98582 | -0.099028 | 0.0014131 | 0.00035415
83 | 1 | 0 | -0.11436 | -0.028684
84 | 0.98561 | -0.10048 | 0.0010951 | 0.00027445
85 | 0.98531 | -0.10262 | 0.0067953 | 0.0017031
86 | 0.98403 | -0.11168 | 0.0018713 | 0.000469
87 | 0.98231 | -0.12382 | 0.002676 | 0.00067068
88 | 0.98181 | -0.12742 | 0.0029699 | 0.00074432
89 | 0.98111 | -0.13235 | 0.00059944 | 0.00015023
90 | 0.99998 | -0.00010536 | 0.00056116 | 0.00014064
91 | 0.99989 | -0.0007606 | 0 | 0
92 | 0.99987 | -0.00092288 | 0.0014407 | 0.00036107
93 | 0.99985 | -0.0010462 | 0.00060537 | 0.00015172
94 | 0.98107 | -0.13263 | 0.0017252 | 0.00043239
95 | 0.99984 | -0.0011516 | 0.0005391 | 0.00013511
96 | 0.98062 | -0.1359 | 0.00081556 | 0.0002044
97 | 0.98014 | -0.13931 | 0.0020842 | 0.00052236
98 | 0.97989 | -0.14108 | 0.0017628 | 0.0004418
99 | 0.97918 | -0.14611 | 0.0020811 | 0.00052158
100 | 0.97885 | -0.14848 | 0.0014967 | 0.00037512
101 | 0.97867 | -0.1498 | 0.0017236 | 0.00043197
102 | 0.97786 | -0.15561 | 0.0023073 | 0.00057827
103 | 0.97701 | -0.16167 | 0 | 0
104 | 0.97638 | -0.1662 | 0 | 0
105 | 0.97642 | -0.16589 | 0.0024342 | 0.00061008
106 | 0.97615 | -0.16784 | 0.0015581 | 0.0003905
107 | 0.97582 | -0.17024 | 0.0017522 | 0.00043913
108 | 0.97587 | -0.16987 | 0.0029102 | 0.00072936
109 | 0.97503 | -0.17597 | 0.003155 | 0.00079072
110 | 0.97444 | -0.18019 | 0.00057315 | 0.00014364
111 | 0.97509 | -0.17551 | 0.0015647 | 0.00039215
112 | 0.97431 | -0.18117 | 0.0058265 | 0.0014603
113 | 0.9741 | -0.18266 | 0.00046436 | 0.00011638
114 | 0.97613 | -0.16798 | 0.00030367 | 7.6107e-05
115 | 0.9761 | -0.16825 | 0.00056672 | 0.00014203
116 | 0.97581 | -0.17025 | 0.0033477 | 0.00083901
117 | 0.97561 | -0.1717 | 0.0002841 | 7.1203e-05
118 | 0.97526 | -0.17426 | 0.0020654 | 0.00051765
119 | 0.97524 | -0.17439 | 0.0010375 | 0.00026003
120 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00021408 | -5.3653e-05 | 0.00021408 | 5.3508e-05 | 7.9564e-10 | -1.4581e-07 | 0.00032832 | 0.00032827 | 0.00032832 | 0.97026 | -0.21083 | 0.97026 | -0.2108 | 0.1216
1 | -0.00039594 | -9.9086e-05 | 0.00039595 | 9.8881e-05 | 3.8534e-09 | -2.0543e-07 | 0.00060717 | 0.0006071 | 0.00060717 | 0.97026 | -0.2108 | 0.97027 | -0.21073 | 0.22488
2 | -0.00029524 | -7.3995e-05 | 0.00029526 | 7.2486e-05 | 1.5621e-08 | -1.5097e-06 | 0.00045236 | 0.00045182 | 0.00045236 | 0.9712 | -0.20401 | 0.97125 | -0.20362 | 0.16754
3 | -0.00029526 | -7.2486e-05 | 0.00029529 | 6.9157e-05 | 3.4299e-08 | -3.3282e-06 | 0.00045182 | 0.00045066 | 0.00045182 | 0.97125 | -0.20362 | 0.97137 | -0.20271 | 0.16734
4 | 0.00037058 | 9.2764e-05 | -0.00037057 | -9.2875e-05 | 1.799e-09 | -1.1003e-07 | 0.00056767 | 0.00056771 | 0.00056771 | 0.97131 | -0.20278 | 0.9713 | -0.20282 | 0.21026
5 | -0.00037058 | -9.2764e-05 | 0.0003706 | 9.0998e-05 | 2.885e-08 | -1.7668e-06 | 0.00056767 | 0.00056704 | 0.00056767 | 0.97131 | -0.20278 | 0.97138 | -0.20221 | 0.21025
6 | -0.0028228 | -0.00070429 | 0.0028237 | 0.00070368 | 9.0226e-07 | -6.1117e-07 | 0.004323 | 0.0043226 | 0.004323 | 0.97138 | -0.20221 | 0.97171 | -0.19988 | 1.6011
7 | 0.0024522 | 0.0006133 | -0.0024522 | -0.00061332 | 2.596e-08 | -2.6521e-08 | 0.0037559 | 0.003756 | 0.003756 | 0.97138 | -0.20221 | 0.97137 | -0.20228 | 1.3911
8 | 0.0055626 | 0.0013769 | -0.0055624 | -0.0013769 | 1.6882e-07 | 1.6555e-08 | 0.0084171 | 0.0084171 | 0.0084171 | 0.98267 | -0.1229 | 0.98264 | -0.12313 | 3.1174
9 | -0.0057917 | -0.0014343 | 0.0058062 | 0.0014361 | 1.4486e-05 | 1.7321e-06 | 0.008764 | 0.0087627 | 0.008764 | 0.98267 | -0.1229 | 0.98521 | -0.10441 | 3.2459
10 | 0.0055624 | 0.0013769 | -0.0055619 | -0.0013769 | 4.9505e-07 | 4.8565e-08 | 0.0084171 | 0.0084172 | 0.0084172 | 0.98264 | -0.12313 | 0.98255 | -0.12379 | 3.1175
11 | 0.00078671 | 0.00019547 | -0.00078661 | -0.00019689 | 1.0077e-07 | -1.4184e-06 | 0.0011876 | 0.0011881 | 0.0011881 | 0.98521 | -0.10441 | 0.98508 | -0.10534 | 0.44005
12 | -0.0065929 | -0.0016315 | 0.0065972 | 0.0016323 | 4.3087e-06 | 7.6848e-07 | 0.0099503 | 0.0099499 | 0.0099503 | 0.98521 | -0.10441 | 0.98587 | -0.099571 | 3.6853
13 | 0.0041996 | 0.0010358 | -0.0041979 | -0.001036 | 1.6598e-06 | -1.9565e-07 | 0.0063541 | 0.0063544 | 0.0063544 | 0.98255 | -0.12379 | 0.98215 | -0.12673 | 2.3535
14 | 0.0013624 | 0.00034105 | -0.0013623 | -0.00034136 | 7.0864e-08 | -3.1064e-07 | 0.0020631 | 0.0020632 | 0.0020632 | 0.98255 | -0.12379 | 0.9825 | -0.12416 | 0.76415
15 | 0.00044638 | 0.00011163 | -0.00044638 | -0.00011187 | 5.5657e-09 | -2.4763e-07 | 0.0006742 | 0.00067429 | 0.00067429 | 0.98508 | -0.10534 | 0.98506 | -0.10543 | 0.24974
16 | -0.0077623 | -0.0019181 | 0.0077695 | 0.0019198 | 7.1649e-06 | 1.6863e-06 | 0.011706 | 0.011706 | 0.011706 | 0.98587 | -0.099571 | 0.98681 | -0.09272 | 4.3357
17 | 0.0011651 | 0.00028579 | -0.001165 | -0.00028635 | 8.9865e-08 | -5.6063e-07 | 0.0017563 | 0.0017565 | 0.0017565 | 0.98587 | -0.099571 | 0.98579 | -0.10015 | 0.65057
18 | 0.0022104 | 0.00054903 | -0.0022104 | -0.00054908 | 3.4326e-08 | -4.8933e-08 | 0.0033472 | 0.0033472 | 0.0033472 | 0.98215 | -0.12673 | 0.98213 | -0.12684 | 1.2397
19 | 0.0019875 | 0.00048697 | -0.0019863 | -0.00048908 | 1.1361e-06 | -2.1085e-06 | 0.0030072 | 0.0030081 | 0.0030081 | 0.98215 | -0.12673 | 0.98157 | -0.13102 | 1.1141
20 | 0.00056266 | 0.00014095 | -0.00056266 | -0.00014101 | 2.351e-09 | -6.4803e-08 | 0.00085214 | 0.00085216 | 0.00085216 | 0.9825 | -0.12416 | 0.98249 | -0.12419 | 0.31562
21 | 0.00054393 | 0.00013342 | -0.0005439 | -0.00013446 | 3.5253e-08 | -1.0412e-06 | 0.00082308 | 0.00082345 | 0.00082345 | 0.98213 | -0.12684 | 0.98207 | -0.12733 | 0.30498
22 | 0.0016665 | 0.00041566 | -0.0016659 | -0.00041729 | 5.8222e-07 | -1.6282e-06 | 0.0025241 | 0.0025248 | 0.0025248 | 0.98213 | -0.12684 | 0.98178 | -0.12938 | 0.9351
23 | 0.0019215 | 0.00047284 | -0.0019208 | -0.0004744 | 7.7995e-07 | -1.5647e-06 | 0.0029099 | 0.0029105 | 0.0029105 | 0.98157 | -0.13102 | 0.98116 | -0.13405 | 1.078
24 | -0.0081225 | -0.0020083 | 0.0081314 | 0.0020105 | 8.958e-06 | 2.2194e-06 | 0.012238 | 0.012238 | 0.012238 | 0.98681 | -0.09272 | 0.98793 | -0.084544 | 4.5327
25 | 0.00067052 | 0.00016243 | -0.00067038 | -0.00016513 | 1.3801e-07 | -2.707e-06 | 0.0010102 | 0.0010111 | 0.0010111 | 0.98579 | -0.10015 | 0.98558 | -0.10171 | 0.37449
26 | 0.00046117 | 0.00011373 | -0.00046117 | -0.0001138 | 1.8328e-09 | -7.5551e-08 | 0.0006981 | 0.00069813 | 0.00069813 | 0.98207 | -0.12733 | 0.98206 | -0.12736 | 0.25857
27 | 0.0015068 | 0.00037742 | -0.0015067 | -0.00037762 | 5.7663e-08 | -2.0188e-07 | 0.0022836 | 0.0022837 | 0.0022837 | 0.98178 | -0.12938 | 0.98174 | -0.12966 | 0.84582
28 | 0.0019208 | 0.0004744 | -0.0019205 | -0.00047482 | 2.0688e-07 | -4.1464e-07 | 0.0029105 | 0.0029107 | 0.0029107 | 0.98116 | -0.13405 | 0.98105 | -0.13485 | 1.078
29 | -0.0083574 | -0.0020671 | 0.0083613 | 0.0020681 | 3.9487e-06 | 1.0063e-06 | 0.012578 | 0.012578 | 0.012578 | 0.98793 | -0.084544 | 0.98842 | -0.081043 | 4.6586
30 | 0.00067038 | 0.00016513 | -0.00067026 | -0.00016757 | 1.2441e-07 | -2.4348e-06 | 0.0010111 | 0.001012 | 0.001012 | 0.98558 | -0.10171 | 0.98539 | -0.10308 | 0.37481
31 | 0.00047835 | 0.00011963 | -0.00047834 | -0.00011988 | 6.9613e-09 | -2.5454e-07 | 0.00073268 | 0.00073277 | 0.00073277 | 0.97137 | -0.20271 | 0.97135 | -0.20281 | 0.2714
32 | -0.0048096 | -0.0011946 | 0.0048199 | 0.0011948 | 1.0356e-05 | 1.8536e-07 | 0.0073638 | 0.0073625 | 0.0073638 | 0.97137 | -0.20271 | 0.97352 | -0.18686 | 2.7273
33 | 0.0040359 | 0.0010058 | -0.004034 | -0.0010061 | 1.9679e-06 | -2.6453e-07 | 0.0061805 | 0.0061809 | 0.0061809 | 0.97137 | -0.20271 | 0.97088 | -0.20627 | 2.2892
34 | 0.0004781 | 0.00011962 | -0.00047809 | -0.00011982 | 5.54e-09 | -2.0461e-07 | 0.00073069 | 0.00073076 | 0.00073076 | 0.97352 | -0.18686 | 0.97351 | -0.18695 | 0.27065
35 | 0.001319 | 0.00032943 | -0.0013189 | -0.00033025 | 1.8174e-07 | -8.211e-07 | 0.0020157 | 0.002016 | 0.002016 | 0.97352 | -0.18686 | 0.97339 | -0.18786 | 0.74668
36 | -0.0066171 | -0.0016438 | 0.006619 | 0.0016442 | 1.8742e-06 | 3.5529e-07 | 0.010109 | 0.010109 | 0.010109 | 0.97352 | -0.18686 | 0.97381 | -0.18478 | 3.744
37 | 0.0021457 | 0.00053286 | -0.0021454 | -0.00053336 | 3.4129e-07 | -4.9462e-07 | 0.0032869 | 0.0032871 | 0.0032871 | 0.97088 | -0.20627 | 0.97072 | -0.20744 | 1.2175
38 | 0.00074179 | 0.00018562 | -0.00074177 | -0.0001859 | 1.8965e-08 | -2.8652e-07 | 0.0011339 | 0.001134 | 0.001134 | 0.97339 | -0.18786 | 0.97336 | -0.18805 | 0.41999
39 | -0.007294 | -0.0018134 | 0.0072946 | 0.0018135 | 5.6231e-07 | 1.2593e-07 | 0.01114 | 0.01114 | 0.01114 | 0.97381 | -0.18478 | 0.97389 | -0.18422 | 4.126
40 | 0.0012802 | 0.00031652 | -0.0012798 | -0.00031851 | 4.1763e-07 | -1.9895e-06 | 0.0019609 | 0.0019617 | 0.0019617 | 0.97072 | -0.20744 | 0.97039 | -0.20984 | 0.72655
41 | 0.0010148 | 0.00025209 | -0.0010148 | -0.00025219 | 1.3192e-08 | -1.0289e-07 | 0.0015553 | 0.0015553 | 0.0015553 | 0.97039 | -0.20984 | 0.97038 | -0.20994 | 0.57605
42 | 0.00050648 | 0.0001248 | -0.00050642 | -0.00012657 | 5.4453e-08 | -1.7681e-06 | 0.00077589 | 0.00077653 | 0.00077653 | 0.97038 | -0.20994 | 0.97027 | -0.21073 | 0.2876
43 | -0.0099009 | -0.0024667 | 0.009903 | 0.0024673 | 2.1127e-06 | 6.2831e-07 | 0.015122 | 0.015122 | 0.015122 | 0.97389 | -0.18422 | 0.9741 | -0.18266 | 5.6009
44 | 0.00045568 | 0.00011369 | -0.00045567 | -0.00011409 | 9.378e-09 | -3.9376e-07 | 0.00069098 | 0.00069112 | 0.00069112 | 0.98105 | -0.13485 | 0.98103 | -0.135 | 0.25597
45 | 0.0014649 | 0.00036112 | -0.0014647 | -0.00036166 | 1.4548e-07 | -5.4138e-07 | 0.0022197 | 0.0022199 | 0.0022199 | 0.98105 | -0.13485 | 0.98095 | -0.13559 | 0.82219
46 | 0.00022147 | 5.539e-05 | -0.00022147 | -5.5505e-05 | 6.3827e-10 | -1.1422e-07 | 0.00033588 | 0.00033592 | 0.00033592 | 0.98103 | -0.135 | 0.98103 | -0.13502 | 0.12441
47 | 0.0012916 | 0.00031828 | -0.0012915 | -0.00031887 | 1.1976e-07 | -5.8621e-07 | 0.0019573 | 0.0019576 | 0.0019576 | 0.98095 | -0.13559 | 0.98085 | -0.13628 | 0.72502
48 | 0.00028435 | 6.9487e-05 | -0.00028433 | -7.126e-05 | 1.6262e-08 | -1.7727e-06 | 0.00043021 | 0.00043084 | 0.00043084 | 0.98206 | -0.12736 | 0.98201 | -0.12778 | 0.15957
49 | 0.0010664 | 0.00026244 | -0.0010663 | -0.00026295 | 6.8613e-08 | -5.0493e-07 | 0.001616 | 0.0016162 | 0.0016162 | 0.98085 | -0.13628 | 0.98079 | -0.13676 | 0.59861
50 | -0.00013628 | -3.4155e-05 | 0.00013628 | 3.3833e-05 | 6.8045e-10 | -3.2164e-07 | 0.00020679 | 0.00020668 | 0.00020679 | 0.98064 | -0.13784 | 0.98065 | -0.1378 | 0.076589
51 | -0.00019235 | -4.7886e-05 | 0.00019235 | 4.7808e-05 | 3.2709e-10 | -7.758e-08 | 0.00029175 | 0.00029172 | 0.00029175 | 0.98065 | -0.1378 | 0.98065 | -0.13779 | 0.10806
52 | -0.0010662 | -0.00026403 | 0.0010663 | 0.00026295 | 1.4732e-07 | -1.0835e-06 | 0.0016166 | 0.0016162 | 0.0016166 | 0.98065 | -0.13779 | 0.98079 | -0.13676 | 0.59875
53 | 0.00087381 | 0.00021623 | -0.00087379 | -0.00021644 | 1.9266e-08 | -2.1448e-07 | 0.0013249 | 0.001325 | 0.001325 | 0.98065 | -0.13779 | 0.98063 | -0.13795 | 0.49074
54 | 0.00037231 | 9.2801e-05 | -0.0003723 | -9.3308e-05 | 8.0485e-09 | -5.0689e-07 | 0.00056477 | 0.00056495 | 0.00056495 | 0.98063 | -0.13795 | 0.98061 | -0.13811 | 0.20924
55 | 0.00050148 | 0.00012364 | -0.00050146 | -0.00012413 | 1.4182e-08 | -4.9056e-07 | 0.00076022 | 0.0007604 | 0.0007604 | 0.98063 | -0.13795 | 0.9806 | -0.13816 | 0.28163
56 | 0.00035375 | 8.7109e-05 | -0.00035375 | -8.7251e-05 | 2.0321e-09 | -1.4206e-07 | 0.00053625 | 0.0005363 | 0.0005363 | 0.9806 | -0.13816 | 0.98059 | -0.1382 | 0.19863
57 | 0.0002039 | 4.9696e-05 | -0.0002039 | -5.1101e-05 | 6.6558e-09 | -1.4051e-06 | 0.00030892 | 0.00030942 | 0.00030942 | 0.98059 | -0.1382 | 0.98056 | -0.13845 | 0.1146
58 | 0.00019923 | 4.9517e-05 | -0.00019923 | -4.9932e-05 | 1.8422e-09 | -4.1499e-07 | 0.00030071 | 0.00030086 | 0.00030086 | 0.98539 | -0.10308 | 0.98539 | -0.10315 | 0.11143
59 | -0.0085108 | -0.0021056 | 0.008514 | 0.0021064 | 3.1311e-06 | 8.1177e-07 | 0.012803 | 0.012803 | 0.012803 | 0.98842 | -0.081043 | 0.98879 | -0.078318 | 4.7419
60 | -0.10925 | -0.027479 | 0.10963 | 0.027622 | 0.00037545 | 0.00014325 | 0.16409 | 0.16409 | 0.16409 | 0.99095 | -0.062961 | 0.99446 | -0.0384 | 30.3869
61 | 0.10925 | 0.027479 | -0.10918 | -0.027451 | 7.3565e-05 | 2.8069e-05 | 0.16409 | 0.16409 | 0.16409 | 0.99095 | -0.062961 | 0.99026 | -0.067794 | 30.3869
62 | -0.10982 | -0.02767 | 0.11041 | 0.027896 | 0.00059331 | 0.00022636 | 0.16437 | 0.16437 | 0.16437 | 0.99446 | -0.0384 | 1 | 0 | 30.4395
63 | 0.094198 | 0.023722 | -0.094131 | -0.023696 | 6.7683e-05 | 2.5754e-05 | 0.14159 | 0.14159 | 0.14159 | 0.99026 | -0.067794 | 0.98952 | -0.072938 | 26.22
64 | 0.01498 | 0.003729 | -0.014978 | -0.003728 | 2.8202e-06 | 9.6988e-07 | 0.022501 | 0.022502 | 0.022502 | 0.99026 | -0.067794 | 0.99006 | -0.069173 | 8.3339
65 | -0.0097405 | -0.0024138 | 0.0097406 | 0.0024138 | 1.542e-07 | 4.4536e-08 | 0.014649 | 0.014649 | 0.014649 | 0.98879 | -0.078318 | 0.98881 | -0.078201 | 5.4254
66 | -0.014622 | -0.0036373 | 0.01464 | 0.0036435 | 1.8028e-05 | 6.1669e-06 | 0.021995 | 0.021995 | 0.021995 | 0.98881 | -0.078201 | 0.99006 | -0.069173 | 8.1463
67 | 0.0017883 | 0.00044733 | -0.0017882 | -0.00044754 | 9.1205e-08 | -2.0593e-07 | 0.0027395 | 0.0027395 | 0.0027395 | 0.97125 | -0.20321 | 0.9712 | -0.20358 | 1.0146
68 | -0.0024519 | -0.00061364 | 0.0024522 | 0.00061332 | 3.1304e-07 | -3.1973e-07 | 0.0037561 | 0.003756 | 0.0037561 | 0.97125 | -0.20321 | 0.97137 | -0.20228 | 1.3912
69 | 0.0014182 | 0.00035481 | -0.001418 | -0.00035539 | 1.5333e-07 | -5.8506e-07 | 0.0021726 | 0.0021729 | 0.0021729 | 0.9712 | -0.20358 | 0.97109 | -0.20436 | 0.80477
70 | -0.0079739 | -0.0019944 | 0.0079824 | 0.0019966 | 8.5154e-06 | 2.1399e-06 | 0.012209 | 0.012209 | 0.012209 | 0.97171 | -0.19988 | 0.97278 | -0.19213 | 4.522
71 | -0.0095981 | -0.0024015 | 0.0096029 | 0.0024029 | 4.7738e-06 | 1.3952e-06 | 0.01468 | 0.01468 | 0.01468 | 0.97278 | -0.19213 | 0.97327 | -0.18853 | 5.4372
72 | -0.0099264 | -0.002484 | 0.0099334 | 0.0024861 | 7.0667e-06 | 2.1063e-06 | 0.015175 | 0.015175 | 0.015175 | 0.97327 | -0.18853 | 0.97399 | -0.18338 | 5.6203
73 | -0.010339 | -0.0025878 | 0.010341 | 0.0025884 | 1.756e-06 | 5.3498e-07 | 0.015795 | 0.015795 | 0.015795 | 0.97399 | -0.18338 | 0.97416 | -0.18215 | 5.8499
74 | -0.010753 | -0.0026915 | 0.010757 | 0.0026929 | 4.511e-06 | 1.4012e-06 | 0.016423 | 0.016423 | 0.016423 | 0.97416 | -0.18215 | 0.97458 | -0.17911 | 6.0827
75 | -0.011239 | -0.0028136 | 0.011239 | 0.0028138 | 6.2388e-07 | 1.9763e-07 | 0.017158 | 0.017158 | 0.017158 | 0.97458 | -0.17911 | 0.97464 | -0.17871 | 6.355
76 | -0.013435 | -0.0033641 | 0.013443 | 0.0033668 | 8.0232e-06 | 2.7047e-06 | 0.020511 | 0.020511 | 0.020511 | 0.97464 | -0.17871 | 0.97524 | -0.17439 | 7.5966
77 | 0.091939 | 0.023147 | -0.091896 | -0.023131 | 4.2548e-05 | 1.6181e-05 | 0.13829 | 0.13829 | 0.13829 | 0.98952 | -0.072938 | 0.98905 | -0.076253 | 25.6097
78 | 0.091435 | 0.023015 | -0.091393 | -0.022999 | 4.1709e-05 | 1.5861e-05 | 0.1376 | 0.1376 | 0.1376 | 0.98905 | -0.076253 | 0.98859 | -0.079521 | 25.4812
79 | 0.088001 | 0.022149 | -0.087979 | -0.022141 | 2.2068e-05 | 8.3844e-06 | 0.13249 | 0.13249 | 0.13249 | 0.98859 | -0.079521 | 0.98833 | -0.081317 | 24.5356
80 | 0.084701 | 0.021319 | -0.0847 | -0.021319 | 1.6117e-06 | 6.1175e-07 | 0.12756 | 0.12756 | 0.12756 | 0.98833 | -0.081317 | 0.98831 | -0.081454 | 23.6218
81 | 0.084432 | 0.021252 | -0.084333 | -0.021214 | 9.9118e-05 | 3.7619e-05 | 0.12716 | 0.12716 | 0.12716 | 0.98831 | -0.081454 | 0.98711 | -0.089871 | 23.5473
82 | 0.083379 | 0.020975 | -0.083273 | -0.020935 | 0.00010635 | 4.0353e-05 | 0.12572 | 0.12572 | 0.12572 | 0.98711 | -0.089871 | 0.98582 | -0.099028 | 23.2809
83 | 0.08186 | 0.02058 | -0.081843 | -0.020574 | 1.6533e-05 | 6.2706e-06 | 0.12358 | 0.12358 | 0.12358 | 0.98582 | -0.099028 | 0.98561 | -0.10048 | 22.8859
84 | 0.0031467 | 0.00078757 | -0.0031466 | -0.0007876 | 4.5777e-08 | -2.6299e-08 | 0.0046819 | 0.0046819 | 0.0046819 | 1 | 0 | 0.99998 | -0.00010536 | 1.7341
85 | 0.080748 | 0.0203 | -0.080724 | -0.020291 | 2.4051e-05 | 9.1184e-06 | 0.12193 | 0.12193 | 0.12193 | 0.98561 | -0.10048 | 0.98531 | -0.10262 | 22.5798
86 | 0.073929 | 0.018587 | -0.073835 | -0.018552 | 9.3195e-05 | 3.5235e-05 | 0.11167 | 0.11167 | 0.11167 | 0.98531 | -0.10262 | 0.98403 | -0.11168 | 20.6794
87 | 0.071964 | 0.018083 | -0.071843 | -0.018037 | 0.0001214 | 4.5859e-05 | 0.10884 | 0.10884 | 0.10884 | 0.98403 | -0.11168 | 0.98231 | -0.12382 | 20.1554
88 | 0.069167 | 0.017367 | -0.069132 | -0.017354 | 3.4611e-05 | 1.3056e-05 | 0.10479 | 0.10479 | 0.10479 | 0.98231 | -0.12382 | 0.98181 | -0.12742 | 19.4048
89 | 0.066162 | 0.016609 | -0.066117 | -0.016592 | 4.5257e-05 | 1.7042e-05 | 0.10028 | 0.10028 | 0.10028 | 0.98181 | -0.12742 | 0.98111 | -0.13235 | 18.5712
90 | 0.065517 | 0.016442 | -0.065515 | -0.016441 | 2.5665e-06 | 9.6609e-07 | 0.099376 | 0.099376 | 0.099376 | 0.98111 | -0.13235 | 0.98107 | -0.13263 | 18.4029
91 | 0.0025855 | 0.00064696 | -0.0025852 | -0.0006472 | 2.3389e-07 | -2.4228e-07 | 0.0038469 | 0.003847 | 0.003847 | 0.99998 | -0.00010536 | 0.99989 | -0.0007606 | 1.4248
92 | 0.0014407 | 0.00036093 | -0.0014407 | -0.00036107 | 3.2352e-08 | -1.3549e-07 | 0.002144 | 0.002144 | 0.002144 | 0.99989 | -0.0007606 | 0.99987 | -0.00092288 | 0.79409
93 | 0.0011445 | 0.00028627 | -0.0011445 | -0.00028658 | 4.5118e-08 | -3.096e-07 | 0.0017031 | 0.0017032 | 0.0017032 | 0.99989 | -0.0007606 | 0.99985 | -0.0010462 | 0.6308
94 | 0.00053911 | 0.00013486 | -0.0005391 | -0.00013511 | 7.8492e-09 | -2.5329e-07 | 0.00080223 | 0.00080232 | 0.00080232 | 0.99985 | -0.0010462 | 0.99984 | -0.0011516 | 0.29716
95 | 0.06379 | 0.016009 | -0.063761 | -0.015998 | 2.8924e-05 | 1.0875e-05 | 0.096759 | 0.096759 | 0.096759 | 0.98107 | -0.13263 | 0.98062 | -0.1359 | 17.9183
96 | 0.062945 | 0.015793 | -0.062915 | -0.015782 | 2.9761e-05 | 1.1183e-05 | 0.095521 | 0.095521 | 0.095521 | 0.98062 | -0.1359 | 0.98014 | -0.13931 | 17.6892
97 | 0.060831 | 0.01526 | -0.060816 | -0.015254 | 1.4925e-05 | 5.5989e-06 | 0.092357 | 0.092357 | 0.092357 | 0.98014 | -0.13931 | 0.97989 | -0.14108 | 17.1032
98 | 0.059053 | 0.014812 | -0.059012 | -0.014797 | 4.1175e-05 | 1.5424e-05 | 0.08968 | 0.089681 | 0.089681 | 0.97989 | -0.14108 | 0.97918 | -0.14611 | 16.6075
99 | 0.056931 | 0.014275 | -0.056912 | -0.014268 | 1.8698e-05 | 6.9903e-06 | 0.086518 | 0.086518 | 0.086518 | 0.97918 | -0.14611 | 0.97885 | -0.14848 | 16.0219
100 | 0.055416 | 0.013893 | -0.055406 | -0.01389 | 1.0113e-05 | 3.775e-06 | 0.084243 | 0.084243 | 0.084243 | 0.97885 | -0.14848 | 0.97867 | -0.1498 | 15.6005
101 | 0.053682 | 0.013458 | -0.053639 | -0.013442 | 4.3147e-05 | 1.6074e-05 | 0.081622 | 0.081622 | 0.081622 | 0.97867 | -0.1498 | 0.97786 | -0.15561 | 15.1153
102 | 0.051332 | 0.012863 | -0.051289 | -0.012847 | 4.3003e-05 | 1.6398e-05 | 0.078111 | 0.078111 | 0.078111 | 0.97786 | -0.15561 | 0.97701 | -0.16167 | 28.9301
103 | 0.025728 | 0.0064387 | -0.025712 | -0.0064328 | 1.6084e-05 | 5.976e-06 | 0.039181 | 0.039181 | 0.039181 | 0.97701 | -0.16167 | 0.97638 | -0.1662 | 14.5116
104 | 0.025561 | 0.0064081 | -0.025546 | -0.0064026 | 1.4942e-05 | 5.5493e-06 | 0.03893 | 0.03893 | 0.03893 | 0.97701 | -0.16167 | 0.97642 | -0.16589 | 14.4186
105 | 0.0024291 | 0.00060731 | -0.0024285 | -0.00060791 | 5.5161e-07 | -5.9455e-07 | 0.0037014 | 0.0037017 | 0.0037017 | 0.97638 | -0.1662 | 0.97615 | -0.16784 | 1.371
106 | 0.023283 | 0.0058255 | -0.02327 | -0.0058207 | 1.2975e-05 | 4.784e-06 | 0.03548 | 0.03548 | 0.03548 | 0.97638 | -0.1662 | 0.97582 | -0.17024 | 13.1407
107 | 0.023111 | 0.0057925 | -0.023099 | -0.0057878 | 1.2745e-05 | 4.696e-06 | 0.035221 | 0.035221 | 0.035221 | 0.97642 | -0.16589 | 0.97587 | -0.16987 | 13.0447
108 | 0.00087043 | 0.0002174 | -0.00087041 | -0.00021759 | 1.6877e-08 | -1.8562e-07 | 0.0013266 | 0.0013267 | 0.0013267 | 0.97615 | -0.16784 | 0.97613 | -0.16798 | 0.49135
109 | 0.021518 | 0.0053815 | -0.021502 | -0.0053758 | 1.5634e-05 | 5.7225e-06 | 0.032808 | 0.032808 | 0.032808 | 0.97582 | -0.17024 | 0.97509 | -0.17551 | 12.1511
110 | 0.020188 | 0.0050584 | -0.020187 | -0.0050581 | 1.0674e-06 | 3.8798e-07 | 0.030783 | 0.030783 | 0.030783 | 0.97587 | -0.16987 | 0.97581 | -0.17025 | 11.4012
111 | 0.016781 | 0.0041925 | -0.016771 | -0.004189 | 9.7352e-06 | 3.4477e-06 | 0.025605 | 0.025605 | 0.025605 | 0.97503 | -0.17597 | 0.97444 | -0.18019 | 9.4835
112 | -0.019936 | -0.0049832 | 0.019937 | 0.0049837 | 1.2477e-06 | 4.5292e-07 | 0.03042 | 0.03042 | 0.03042 | 0.97503 | -0.17597 | 0.97509 | -0.17551 | 11.2668
113 | 0.016198 | 0.0040454 | -0.016196 | -0.0040446 | 2.1983e-06 | 7.7377e-07 | 0.02473 | 0.02473 | 0.02473 | 0.97444 | -0.18019 | 0.97431 | -0.18117 | 9.1593
114 | 0.010369 | 0.0025844 | -0.010367 | -0.0025837 | 2.1065e-06 | 6.425e-07 | 0.015832 | 0.015832 | 0.015832 | 0.97431 | -0.18117 | 0.9741 | -0.18266 | 5.8636
115 | 0.00056674 | 0.00014148 | -0.00056672 | -0.00014203 | 2.0788e-08 | -5.5006e-07 | 0.00086373 | 0.00086393 | 0.00086393 | 0.97613 | -0.16798 | 0.9761 | -0.16825 | 0.31998
116 | 0.01684 | 0.004219 | -0.016836 | -0.0042178 | 3.3686e-06 | 1.1934e-06 | 0.025678 | 0.025678 | 0.025678 | 0.97581 | -0.17025 | 0.97561 | -0.1717 | 9.5105
117 | 0.016552 | 0.0041466 | -0.016546 | -0.0041446 | 5.8545e-06 | 2.068e-06 | 0.025245 | 0.025245 | 0.025245 | 0.97561 | -0.1717 | 0.97526 | -0.17426 | 9.3501
118 | 0.014481 | 0.0036269 | -0.014481 | -0.0036268 | 2.5766e-07 | 8.8543e-08 | 0.022094 | 0.022094 | 0.022094 | 0.97526 | -0.17426 | 0.97524 | -0.17439 | 8.1829

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11502 | 0.028851

## res_load
| p_mw | q_mvar
0 | 0.00021408 | 5.3653e-05
1 | 0.00018186 | 4.5579e-05
2 | 0.00029524 | 7.3995e-05
3 | 0.00037057 | 9.2875e-05
4 | 0.0002291 | 5.7419e-05
5 | 0.00034022 | 8.5268e-05
6 | 0.00079963 | 0.00020041
7 | 6.4815e-05 | 1.6244e-05
8 | 0.00044638 | 0.00011187
9 | 0.00035302 | 8.8475e-05
10 | 0.00049448 | 0.00012393
11 | 0.00056266 | 0.00014101
12 | 8.2726e-05 | 2.0733e-05
13 | 0.0001591 | 3.9875e-05
14 | 0.00022597 | 5.6634e-05
15 | 0.00047834 | 0.00011988
16 | 0.0018882 | 0.00047323
17 | 0.00047809 | 0.00011982
18 | 0.00057708 | 0.00014463
19 | 0.00067509 | 0.00016919
20 | 0.00086518 | 0.00021683
21 | 0.00026501 | 6.6419e-05
22 | 0.0005083 | 0.00012739
23 | 0.00011048 | 2.7689e-05
24 | 0.00074177 | 0.0001859
25 | 0.0026063 | 0.00065319
26 | 0.00023421 | 5.8698e-05
27 | 0.0001731 | 4.3384e-05
28 | 0.00022147 | 5.5505e-05
29 | 0.00017682 | 4.4316e-05
30 | 0.0015067 | 0.00037762
31 | 0.00022512 | 5.642e-05
32 | 0.00013628 | 3.4155e-05
33 | 5.6068e-05 | 1.4052e-05
34 | 0.0003723 | 9.3308e-05
35 | 0.00014771 | 3.702e-05
36 | 0.00014985 | 3.7555e-05
37 | 0.0002039 | 5.1101e-05
38 | 0.00047102 | 0.00011805
39 | 0.00019923 | 4.9932e-05
40 | 0.00014949 | 3.7467e-05
41 | 0.00019005 | 4.763e-05
42 | 0.0012265 | 0.00030739
43 | 0.0048818 | 0.0012235
44 | 0.00028433 | 7.126e-05
45 | 0.00066359 | 0.00016631
46 | 0.00037 | 9.2731e-05
47 | 0.001418 | 0.00035539
48 | 0.0051502 | 0.0012908
49 | 0.0016157 | 0.00040493
50 | 0.00032349 | 8.1073e-05
51 | 0.00040598 | 0.00010175
52 | 0.0004115 | 0.00010313
53 | 0.00048155 | 0.00012069
54 | 0.0021958 | 0.00055032
55 | 0.00033716 | 8.45e-05
56 | 0.0021916 | 0.00054926
57 | 0.00046138 | 0.00011563
58 | 0.0033924 | 0.00085022
59 | 0.0032775 | 0.00082143
60 | 0.00026723 | 6.6974e-05
61 | 0.00095435 | 0.00023918
62 | 0.0014131 | 0.00035415
63 | 0.00066625 | 0.00016698
64 | 0.0010951 | 0.00027445
65 | 0.0067953 | 0.0017031
66 | 0.0018713 | 0.000469
67 | 0.002676 | 0.00067068
68 | 0.0029699 | 0.00074432
69 | 0.00059944 | 0.00015023
70 | 0.00056116 | 0.00014064
71 | 0.0014407 | 0.00036107
72 | 0.00060537 | 0.00015172
73 | 0.0017252 | 0.00043239
74 | 0.0005391 | 0.00013511
75 | 0.00081556 | 0.0002044
76 | 0.0020842 | 0.00052236
77 | 0.0017628 | 0.0004418
78 | 0.0020811 | 0.00052158
79 | 0.0014967 | 0.00037512
80 | 0.0017236 | 0.00043197
81 | 0.0023073 | 0.00057827
82 | 0.0024342 | 0.00061008
83 | 0.0015581 | 0.0003905
84 | 0.0017522 | 0.00043913
85 | 0.0029102 | 0.00072936
86 | 0.003155 | 0.00079072
87 | 0.00057315 | 0.00014364
88 | 0.0015647 | 0.00039215
89 | 0.0058265 | 0.0014603
90 | 0.00046436 | 0.00011638
91 | 0.00030367 | 7.6107e-05
92 | 0.00056672 | 0.00014203
93 | 0.0033477 | 0.00083901
94 | 0.0002841 | 7.1203e-05
95 | 0.0020654 | 0.00051765
96 | 0.0010375 | 0.00026003

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1