## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1375-8_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1375-8_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1375-8_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1375-8_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1375-8_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1375-8_0_7_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1375-8_0_7_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1375-8_0_7_node_123 | 0.4 | n |  | TRUE
8 | bus_LV_1375-8_0_7_node_88 | 0.4 | n |  | TRUE
9 | bus_LV_1375-8_0_7_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1375-8_0_7_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1375-8_0_7_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1375-8_0_7_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1375-8_0_7_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1375-8_0_7_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1375-8_0_7_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1375-8_0_7_node_125 | 0.4 | n |  | TRUE
17 | bus_LV_1375-8_0_7_node_77 | 0.4 | n |  | TRUE
18 | bus_LV_1375-8_0_7_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_1375-8_0_7_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_1375-8_0_7_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1375-8_0_7_node_102 | 0.4 | n |  | TRUE
22 | bus_LV_1375-8_0_7_node_76 | 0.4 | n |  | TRUE
23 | bus_LV_1375-8_0_7_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1375-8_0_7_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_1375-8_0_7_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1375-8_0_7_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1375-8_0_7_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1375-8_0_7_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1375-8_0_7_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_1375-8_0_7_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_1375-8_0_7_node_86 | 0.4 | n |  | TRUE
32 | bus_LV_1375-8_0_7_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_1375-8_0_7_node_87 | 0.4 | n |  | TRUE
34 | bus_LV_1375-8_0_7_node_85 | 0.4 | n |  | TRUE
35 | bus_LV_1375-8_0_7_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_1375-8_0_7_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_1375-8_0_7_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1375-8_0_7_node_65 | 0.4 | n |  | TRUE
39 | bus_LV_1375-8_0_7_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1375-8_0_7_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_1375-8_0_7_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_1375-8_0_7_node_50 | 0.4 | n |  | TRUE
43 | bus_LV_1375-8_0_7_node_51 | 0.4 | n |  | TRUE
44 | bus_LV_1375-8_0_7_node_63 | 0.4 | n |  | TRUE
45 | bus_LV_1375-8_0_7_node_75 | 0.4 | n |  | TRUE
46 | bus_LV_1375-8_0_7_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_1375-8_0_7_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_1375-8_0_7_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_1375-8_0_7_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_1375-8_0_7_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_1375-8_0_7_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_1375-8_0_7_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_1375-8_0_7_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_1375-8_0_7_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_1375-8_0_7_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_1375-8_0_7_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_1375-8_0_7_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_1375-8_0_7_node_119 | 0.4 | n |  | TRUE
59 | bus_LV_1375-8_0_7_node_62 | 0.4 | n |  | TRUE
60 | bus_LV_1375-8_0_7_node_83 | 0.4 | n |  | TRUE
61 | bus_LV_1375-8_0_7_node_84 | 0.4 | n |  | TRUE
62 | bus_LV_1375-8_0_7_node_81 | 0.4 | n |  | TRUE
63 | bus_LV_1375-8_0_7_node_117 | 0.4 | n |  | TRUE
64 | bus_LV_1375-8_0_7_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_1375-8_0_7_node_61 | 0.4 | n |  | TRUE
66 | bus_LV_1375-8_0_7_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_1375-8_0_7_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_1375-8_0_7_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_1375-8_0_7_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_1375-8_0_7_node_49 | 0.4 | n |  | TRUE
71 | bus_LV_1375-8_0_7_node_95 | 0.4 | n |  | TRUE
72 | bus_LV_1375-8_0_7_node_107 | 0.4 | n |  | TRUE
73 | bus_LV_1375-8_0_7_node_104 | 0.4 | n |  | TRUE
74 | bus_LV_1375-8_0_7_node_94 | 0.4 | n |  | TRUE
75 | bus_LV_1375-8_0_7_node_112 | 0.4 | n |  | TRUE
76 | bus_LV_1375-8_0_7_node_105 | 0.4 | n |  | TRUE
77 | bus_LV_1375-8_0_7_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_1375-8_0_7_node_52 | 0.4 | n |  | TRUE
79 | bus_LV_1375-8_0_7_node_53 | 0.4 | n |  | TRUE
80 | bus_LV_1375-8_0_7_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_1375-8_0_7_node_115 | 0.4 | n |  | TRUE
82 | bus_LV_1375-8_0_7_node_116 | 0.4 | n |  | TRUE
83 | bus_LV_1375-8_0_7_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_1375-8_0_7_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_1375-8_0_7_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_1375-8_0_7_node_59 | 0.4 | n |  | TRUE
87 | bus_LV_1375-8_0_7_node_60 | 0.4 | n |  | TRUE
88 | bus_LV_1375-8_0_7_node_78 | 0.4 | n |  | TRUE
89 | bus_LV_1375-8_0_7_node_124 | 0.4 | n |  | TRUE
90 | bus_LV_1375-8_0_7_node_103 | 0.4 | n |  | TRUE
91 | bus_LV_1375-8_0_7_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_1375-8_0_7_node_111 | 0.4 | n |  | TRUE
93 | bus_LV_1375-8_0_7_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_1375-8_0_7_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_1375-8_0_7_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_1375-8_0_7_node_68 | 0.4 | n |  | TRUE
97 | bus_LV_1375-8_0_7_node_97 | 0.4 | n |  | TRUE
98 | bus_LV_1375-8_0_7_node_69 | 0.4 | n |  | TRUE
99 | bus_LV_1375-8_0_7_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_1375-8_0_7_node_71 | 0.4 | n |  | TRUE
101 | bus_LV_1375-8_0_7_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_1375-8_0_7_node_73 | 0.4 | n |  | TRUE
103 | bus_LV_1375-8_0_7_node_74 | 0.4 | n |  | TRUE
104 | bus_LV_1375-8_0_7_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_1375-8_0_7_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_1375-8_0_7_node_114 | 0.4 | n |  | TRUE
107 | bus_LV_1375-8_0_7_node_92 | 0.4 | n |  | TRUE
108 | bus_LV_1375-8_0_7_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_1375-8_0_7_node_80 | 0.4 | n |  | TRUE
110 | bus_LV_1375-8_0_7_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_1375-8_0_7_node_122 | 0.4 | n |  | TRUE
112 | bus_LV_1375-8_0_7_node_118 | 0.4 | n |  | TRUE
113 | bus_LV_1375-8_0_7_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_1375-8_0_7_node_91 | 0.4 | n |  | TRUE
115 | bus_LV_1375-8_0_7_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_1375-8_0_7_node_99 | 0.4 | n |  | TRUE
117 | bus_LV_1375-8_0_7_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_1375-8_0_7_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_1375-8_0_7_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_1375-8_0_7_node_108 | 0.4 | n |  | TRUE
121 | bus_LV_1375-8_0_7_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_1375-8_0_7_node_120 | 0.4 | n |  | TRUE
123 | bus_LV_1375-8_0_7_node_121 | 0.4 | n |  | TRUE
124 | bus_MV_135_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1375-8_0_7_load_0 | 0 | 0.0024088 | 0.00060371 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1375-8_0_7_load_2 | 2 | 0.0014719 | 0.00036889 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1375-8_0_7_load_4 | 4 | 0.001986 | 0.00049773 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1375-8_0_7_load_123 | 7 | 0.0011594 | 0.00029057 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1375-8_0_7_load_7 | 9 | 0.0024887 | 0.00062373 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1375-8_0_7_load_11 | 13 | 0.0039635 | 0.00099336 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1375-8_0_7_load_12 | 14 | 0.0054915 | 0.0013763 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1375-8_0_7_load_13 | 15 | 0.0030707 | 0.00076959 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1375-8_0_7_load_125 | 16 | 0.0021556 | 0.00054026 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1375-8_0_7_load_33 | 19 | 0.0031051 | 0.00077821 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1375-8_0_7_load_102 | 21 | 0.0026164 | 0.00065573 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1375-8_0_7_load_76 | 22 | 0.0020358 | 0.00051023 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1375-8_0_7_load_34 | 24 | 0.0031188 | 0.00078165 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1375-8_0_7_load_14 | 26 | 0.0038793 | 0.00097225 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1375-8_0_7_load_15 | 27 | 0.0029787 | 0.00074654 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1375-8_0_7_load_17 | 28 | 0.0028799 | 0.00072178 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1375-8_0_7_load_37 | 29 | 0.0030868 | 0.00077362 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1375-8_0_7_load_39 | 30 | 0.0015632 | 0.00039179 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1375-8_0_7_load_38 | 32 | 0.0012435 | 0.00031164 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1375-8_0_7_load_87 | 33 | 0.0016254 | 0.00040737 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1375-8_0_7_load_85 | 34 | 0.00089107 | 0.00022332 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1375-8_0_7_load_19 | 35 | 0.0048837 | 0.001224 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1375-8_0_7_load_20 | 36 | 0.0061181 | 0.0015333 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1375-8_0_7_load_23 | 37 | 0.0050356 | 0.001262 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1375-8_0_7_load_65 | 38 | 0.014408 | 0.0036111 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1375-8_0_7_load_25 | 39 | 0.0023275 | 0.00058333 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1375-8_0_7_load_26 | 40 | 0.0028157 | 0.00070567 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1375-8_0_7_load_50 | 42 | 0.002391 | 0.00059925 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1375-8_0_7_load_51 | 43 | 0.0017351 | 0.00043486 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1375-8_0_7_load_63 | 44 | 0.0055737 | 0.0013969 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1375-8_0_7_load_75 | 45 | 0.0026487 | 0.00066384 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1375-8_0_7_load_28 | 46 | 0.0027339 | 0.00068517 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1375-8_0_7_load_29 | 47 | 0.004295 | 0.0010764 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1375-8_0_7_load_30 | 48 | 0.0061613 | 0.0015442 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1375-8_0_7_load_31 | 49 | 0.0048936 | 0.0012265 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1375-8_0_7_load_32 | 50 | 0.0027512 | 0.00068952 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1375-8_0_7_load_40 | 51 | 0.013827 | 0.0034653 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1375-8_0_7_load_35 | 52 | 0.0027223 | 0.00068227 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1375-8_0_7_load_36 | 53 | 0.0028115 | 0.00070463 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1375-8_0_7_load_41 | 54 | 0.00032866 | 8.2369e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1375-8_0_7_load_44 | 57 | 0.00041329 | 0.00010358 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1375-8_0_7_load_119 | 58 | 0.00044654 | 0.00011191 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1375-8_0_7_load_81 | 62 | 0.00023617 | 5.9189e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1375-8_0_7_load_117 | 63 | 0.00032579 | 8.1651e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1375-8_0_7_load_61 | 65 | 0.0016884 | 0.00042314 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1375-8_0_7_load_45 | 66 | 0.00061029 | 0.00015295 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1375-8_0_7_load_46 | 67 | 0.00016659 | 4.1751e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1375-8_0_7_load_48 | 69 | 0.00041674 | 0.00010445 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1375-8_0_7_load_95 | 71 | 0.00045173 | 0.00011321 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1375-8_0_7_load_107 | 72 | 0.0054204 | 0.0013585 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1375-8_0_7_load_104 | 73 | 0.0014958 | 0.0003749 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1375-8_0_7_load_94 | 74 | 0.00013928 | 3.4907e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1375-8_0_7_load_112 | 75 | 0.0020164 | 0.00050535 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1375-8_0_7_load_105 | 76 | 0.00032614 | 8.1739e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1375-8_0_7_load_64 | 77 | 0.0039579 | 0.00099195 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1375-8_0_7_load_52 | 78 | 0.00066795 | 0.0001674 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1375-8_0_7_load_53 | 79 | 0.0012521 | 0.0003138 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1375-8_0_7_load_54 | 80 | 0.0022775 | 0.00057079 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1375-8_0_7_load_115 | 81 | 0.00058647 | 0.00014698 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1375-8_0_7_load_116 | 82 | 0.0040904 | 0.0010252 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1375-8_0_7_load_56 | 83 | 0.0019371 | 0.00048548 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1375-8_0_7_load_57 | 84 | 0.00237 | 0.00059398 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1375-8_0_7_load_58 | 85 | 0.0042419 | 0.0010631 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1375-8_0_7_load_59 | 86 | 0.0032851 | 0.00082332 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1375-8_0_7_load_78 | 88 | 0.0024178 | 0.00060596 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1375-8_0_7_load_124 | 89 | 0.0010735 | 0.00026904 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1375-8_0_7_load_79 | 91 | 0.0014666 | 0.00036757 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1375-8_0_7_load_111 | 92 | 0.00046952 | 0.00011767 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1375-8_0_7_load_66 | 94 | 0.0017703 | 0.00044369 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1375-8_0_7_load_67 | 95 | 0.0012445 | 0.0003119 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1375-8_0_7_load_97 | 97 | 0.0014261 | 0.00035743 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1375-8_0_7_load_69 | 98 | 0.00021866 | 5.4802e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1375-8_0_7_load_74 | 103 | 0.00038554 | 9.6626e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1375-8_0_7_load_82 | 104 | 0.00022201 | 5.564e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1375-8_0_7_load_114 | 106 | 0.00040729 | 0.00010208 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1375-8_0_7_load_100 | 108 | 0.0081205 | 0.0020352 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1375-8_0_7_load_80 | 109 | 0.0019004 | 0.00047629 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1375-8_0_7_load_90 | 110 | 0.0014956 | 0.00037482 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1375-8_0_7_load_122 | 111 | 0.0043576 | 0.0010921 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1375-8_0_7_load_118 | 112 | 0.00011399 | 2.857e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1375-8_0_7_load_96 | 113 | 0.0021863 | 0.00054794 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1375-8_0_7_load_91 | 114 | 0.00012257 | 3.072e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1375-8_0_7_load_98 | 115 | 0.0034171 | 0.00085641 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1375-8_0_7_load_99 | 116 | 0.0050507 | 0.0012658 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1375-8_0_7_load_109 | 117 | 0.00067836 | 0.00017001 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1375-8_0_7_load_106 | 118 | 0.00033024 | 8.2765e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1375-8_0_7_load_108 | 120 | 0.00068079 | 0.00017062 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1375-8_0_7_load_113 | 121 | 0.00059825 | 0.00014994 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1375-8_0_7_load_120 | 122 | 0.00081408 | 0.00020403 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1375-8_0_7_load_121 | 123 | 0.00032062 | 8.0354e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1375-8_0_7_line_0 | NAYY 4x150 SE | 0 | 1 | 0.038385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1375-8_0_7_line_1 | NAYY 4x150 SE | 1 | 2 | 0.049169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1375-8_0_7_line_2 | NAYY 4x150 SE | 2 | 3 | 0.003334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1375-8_0_7_line_3 | NAYY 4x150 SE | 3 | 4 | 0.019121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1375-8_0_7_line_4 | NAYY 4x150 SE | 4 | 5 | 0.042076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1375-8_0_7_line_5 | NAYY 4x150 SE | 5 | 6 | 0.045417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1375-8_0_7_line_6 | NAYY 4x150 SE | 6 | 7 | 0.049413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1375-8_0_7_line_7 | NAYY 4x150 SE | 7 | 8 | 0.062486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1375-8_0_7_line_8 | NAYY 4x150 SE | 8 | 82 | 0.077311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1375-8_0_7_line_9 | NAYY 4x150 SE | 9 | 10 | 0.013981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1375-8_0_7_line_10 | NAYY 4x150 SE | 9 | 11 | 0.037467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1375-8_0_7_line_11 | NAYY 4x150 SE | 10 | 12 | 0.014565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1375-8_0_7_line_12 | NAYY 4x150 SE | 10 | 13 | 0.016991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1375-8_0_7_line_13 | NAYY 4x150 SE | 11 | 14 | 0.020993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1375-8_0_7_line_14 | NAYY 4x150 SE | 11 | 15 | 0.019388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1375-8_0_7_line_15 | NAYY 4x150 SE | 12 | 16 | 0.004396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1375-8_0_7_line_16 | NAYY 4x150 SE | 12 | 17 | 0.012636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1375-8_0_7_line_17 | NAYY 4x150 SE | 13 | 18 | 0.088387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1375-8_0_7_line_18 | NAYY 4x150 SE | 14 | 19 | 0.022211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1375-8_0_7_line_19 | NAYY 4x150 SE | 15 | 20 | 0.037576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1375-8_0_7_line_20 | NAYY 4x150 SE | 17 | 21 | 0.011878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1375-8_0_7_line_21 | NAYY 4x150 SE | 17 | 22 | 0.014574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1375-8_0_7_line_22 | NAYY 4x150 SE | 18 | 23 | 0.033262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1375-8_0_7_line_23 | NAYY 4x150 SE | 19 | 24 | 0.00072123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1375-8_0_7_line_24 | NAYY 4x150 SE | 20 | 25 | 0.17165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1375-8_0_7_line_25 | NAYY 4x150 SE | 20 | 26 | 0.016113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1375-8_0_7_line_26 | NAYY 4x150 SE | 21 | 108 | 0.020733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1375-8_0_7_line_27 | NAYY 4x150 SE | 22 | 45 | 0.013564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1375-8_0_7_line_28 | NAYY 4x150 SE | 23 | 37 | 0.011189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1375-8_0_7_line_29 | NAYY 4x150 SE | 23 | 35 | 0.01887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1375-8_0_7_line_30 | NAYY 4x150 SE | 24 | 53 | 0.0019285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1375-8_0_7_line_31 | NAYY 4x150 SE | 25 | 30 | 0.11491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1375-8_0_7_line_32 | NAYY 4x150 SE | 25 | 31 | 0.23212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1375-8_0_7_line_33 | NAYY 4x150 SE | 26 | 27 | 0.011942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1375-8_0_7_line_34 | NAYY 4x150 SE | 27 | 28 | 0.011439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1375-8_0_7_line_35 | NAYY 4x150 SE | 28 | 29 | 0.00053872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1375-8_0_7_line_36 | NAYY 4x150 SE | 30 | 32 | 0.16067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1375-8_0_7_line_37 | NAYY 4x150 SE | 31 | 33 | 0.0555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1375-8_0_7_line_38 | NAYY 4x150 SE | 31 | 34 | 0.032256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1375-8_0_7_line_39 | NAYY 4x150 SE | 34 | 96 | 0.038334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1375-8_0_7_line_40 | NAYY 4x150 SE | 35 | 36 | 0.0011587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1375-8_0_7_line_41 | NAYY 4x150 SE | 37 | 38 | 0.018774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1375-8_0_7_line_42 | NAYY 4x150 SE | 39 | 40 | 0.020596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1375-8_0_7_line_43 | NAYY 4x150 SE | 40 | 41 | 0.018189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1375-8_0_7_line_44 | NAYY 4x150 SE | 41 | 42 | 0.0049869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1375-8_0_7_line_45 | NAYY 4x150 SE | 41 | 43 | 0.0015644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1375-8_0_7_line_46 | NAYY 4x150 SE | 42 | 44 | 0.012372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1375-8_0_7_line_47 | NAYY 4x150 SE | 43 | 45 | 0.015315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1375-8_0_7_line_48 | NAYY 4x150 SE | 44 | 77 | 0.02694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1375-8_0_7_line_49 | NAYY 4x150 SE | 46 | 47 | 0.019529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1375-8_0_7_line_50 | NAYY 4x150 SE | 46 | 48 | 0.0064798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1375-8_0_7_line_51 | NAYY 4x150 SE | 47 | 49 | 0.0089735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1375-8_0_7_line_52 | NAYY 4x150 SE | 48 | 50 | 0.034346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1375-8_0_7_line_53 | NAYY 4x150 SE | 49 | 51 | 0.0013882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1375-8_0_7_line_54 | NAYY 4x150 SE | 50 | 52 | 0.0058265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1375-8_0_7_line_55 | NAYY 4x150 SE | 52 | 53 | 0.016639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1375-8_0_7_line_56 | NAYY 4x150 SE | 54 | 55 | 0.12267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1375-8_0_7_line_57 | NAYY 4x150 SE | 55 | 56 | 0.14615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_1375-8_0_7_line_58 | NAYY 4x150 SE | 55 | 57 | 0.1146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_1375-8_0_7_line_59 | NAYY 4x150 SE | 56 | 58 | 0.0062595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1375-8_0_7_line_60 | NAYY 4x150 SE | 57 | 59 | 0.015234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1375-8_0_7_line_61 | NAYY 4x150 SE | 58 | 61 | 0.036039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_1375-8_0_7_line_62 | NAYY 4x150 SE | 59 | 64 | 0.082733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_1375-8_0_7_line_63 | NAYY 4x150 SE | 59 | 65 | 0.050559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1375-8_0_7_line_64 | NAYY 4x150 SE | 60 | 61 | 0.1041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_1375-8_0_7_line_65 | NAYY 4x150 SE | 60 | 62 | 0.010432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_1375-8_0_7_line_66 | NAYY 4x150 SE | 61 | 63 | 0.024564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1375-8_0_7_line_67 | NAYY 4x150 SE | 62 | 104 | 0.02239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_1375-8_0_7_line_68 | NAYY 4x150 SE | 63 | 112 | 0.013913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1375-8_0_7_line_69 | NAYY 4x150 SE | 64 | 81 | 0.098311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_1375-8_0_7_line_70 | NAYY 4x150 SE | 64 | 79 | 0.01373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1375-8_0_7_line_71 | NAYY 4x150 SE | 66 | 67 | 0.024374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_1375-8_0_7_line_72 | NAYY 4x150 SE | 66 | 68 | 0.037266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_1375-8_0_7_line_73 | NAYY 4x150 SE | 67 | 69 | 0.10727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_1375-8_0_7_line_74 | NAYY 4x150 SE | 68 | 70 | 0.11714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_1375-8_0_7_line_75 | NAYY 4x150 SE | 69 | 71 | 0.062034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_1375-8_0_7_line_76 | NAYY 4x150 SE | 70 | 72 | 0.016124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1375-8_0_7_line_77 | NAYY 4x150 SE | 70 | 73 | 0.13795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_1375-8_0_7_line_78 | NAYY 4x150 SE | 71 | 74 | 0.010398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_1375-8_0_7_line_79 | NAYY 4x150 SE | 72 | 75 | 0.039397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_1375-8_0_7_line_80 | NAYY 4x150 SE | 73 | 76 | 0.068197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1375-8_0_7_line_81 | NAYY 4x150 SE | 74 | 105 | 0.1038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
82 | LV_1375-8_0_7_line_82 | NAYY 4x150 SE | 75 | 119 | 0.024174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1375-8_0_7_line_83 | NAYY 4x150 SE | 76 | 118 | 0.021233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1375-8_0_7_line_84 | NAYY 4x150 SE | 78 | 79 | 0.033274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1375-8_0_7_line_85 | NAYY 4x150 SE | 78 | 80 | 0.0032538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1375-8_0_7_line_86 | NAYY 4x150 SE | 81 | 82 | 0.075229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_1375-8_0_7_line_87 | NAYY 4x150 SE | 83 | 84 | 0.023013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_1375-8_0_7_line_88 | NAYY 4x150 SE | 83 | 85 | 0.034658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_1375-8_0_7_line_89 | NAYY 4x150 SE | 84 | 86 | 0.0056917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1375-8_0_7_line_90 | NAYY 4x150 SE | 85 | 87 | 0.016784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1375-8_0_7_line_91 | NAYY 4x150 SE | 86 | 88 | 0.0015514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1375-8_0_7_line_92 | NAYY 4x150 SE | 87 | 89 | 0.031242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1375-8_0_7_line_93 | NAYY 4x150 SE | 87 | 90 | 0.0101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_1375-8_0_7_line_94 | NAYY 4x150 SE | 88 | 91 | 0.01746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1375-8_0_7_line_95 | NAYY 4x150 SE | 90 | 92 | 0.030854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_1375-8_0_7_line_96 | NAYY 4x150 SE | 90 | 93 | 0.007579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1375-8_0_7_line_97 | NAYY 4x150 SE | 91 | 109 | 0.0051949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1375-8_0_7_line_98 | NAYY 4x150 SE | 92 | 117 | 0.022229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_1375-8_0_7_line_99 | NAYY 4x150 SE | 93 | 97 | 0.019087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
100 | LV_1375-8_0_7_line_100 | NAYY 4x150 SE | 93 | 96 | 0.060197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_1375-8_0_7_line_101 | NAYY 4x150 SE | 94 | 95 | 0.00044256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1375-8_0_7_line_102 | NAYY 4x150 SE | 95 | 96 | 0.019357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1375-8_0_7_line_103 | NAYY 4x150 SE | 97 | 113 | 0.0011803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1375-8_0_7_line_104 | NAYY 4x150 SE | 98 | 99 | 0.052948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1375-8_0_7_line_105 | NAYY 4x150 SE | 98 | 100 | 0.042179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1375-8_0_7_line_106 | NAYY 4x150 SE | 99 | 101 | 0.005863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1375-8_0_7_line_107 | NAYY 4x150 SE | 100 | 102 | 0.008645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1375-8_0_7_line_108 | NAYY 4x150 SE | 100 | 103 | 0.026775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1375-8_0_7_line_109 | NAYY 4x150 SE | 101 | 104 | 0.073453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_1375-8_0_7_line_110 | NAYY 4x150 SE | 101 | 105 | 0.084509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
111 | LV_1375-8_0_7_line_111 | NAYY 4x150 SE | 102 | 106 | 0.0094681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1375-8_0_7_line_112 | NAYY 4x150 SE | 105 | 107 | 0.011316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1375-8_0_7_line_113 | NAYY 4x150 SE | 107 | 114 | 0.044381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1375-8_0_7_line_114 | NAYY 4x150 SE | 108 | 116 | 0.029751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1375-8_0_7_line_115 | NAYY 4x150 SE | 109 | 110 | 0.015722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1375-8_0_7_line_116 | NAYY 4x150 SE | 110 | 111 | 0.009784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1375-8_0_7_line_117 | NAYY 4x150 SE | 113 | 115 | 0.012875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1375-8_0_7_line_118 | NAYY 4x150 SE | 117 | 120 | 0.025651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
119 | LV_1375-8_0_7_line_119 | NAYY 4x150 SE | 119 | 121 | 0.014531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
120 | LV_1375-8_0_7_line_120 | NAYY 4x150 SE | 119 | 120 | 0.076137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
121 | LV_1375-8_0_7_line_121 | NAYY 4x150 SE | 121 | 122 | 0.034355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
122 | LV_1375-8_0_7_line_122 | NAYY 4x150 SE | 122 | 123 | 0.021711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1375-8_0_7_trafo_18 | 0.25 MVA 20/0.4 kV | 124 | 25 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2703423.6922 | 1213809.2482 | 2703397.2921 | 1213837.1135
1 | 2703423.6922 | 1213809.2482 | 2703443.5382 | 1213802.1318 | 2703470.2491 | 1213793.4515
2 | 2703473.4198 | 1213792.4211 | 2703470.2491 | 1213793.4515
3 | 2703473.4198 | 1213792.4211 | 2703491.6057 | 1213786.5149
4 | 2703531.6245 | 1213773.5179 | 2703491.6057 | 1213786.5149
5 | 2703571.6052 | 1213752.3305 | 2703551.9789 | 1213763.8311 | 2703540.2123 | 1213770.7317 | 2703531.6245 | 1213773.5179
6 | 2703571.6052 | 1213752.3305 | 2703615.2808 | 1213729.2211
7 | 2703667.3749 | 1213695.2652 | 2703645.0331 | 1213713.4786 | 2703615.2808 | 1213729.2211
8 | 2703667.3749 | 1213695.2652 | 2703670.2715 | 1213707.8133 | 2703677.2604 | 1213746.2843 | 2703679.052 | 1213753.7875 | 2703681.349 | 1213760.6212 | 2703683.9631 | 1213766.7043 | 2703685.6859 | 1213770.0778
9 | 2703692.8107 | 1213279.1566 | 2703697.3439 | 1213292.3825
10 | 2703709.4922 | 1213327.8256 | 2703697.3439 | 1213292.3825
11 | 2703687.9667 | 1213265.4182 | 2703692.8107 | 1213279.1566
12 | 2703692.8107 | 1213279.1566 | 2703682.3196 | 1213284.3 | 2703678.0999 | 1213287.5178
13 | 2703709.4922 | 1213327.8256 | 2703729.1558 | 1213320.4739
14 | 2703709.4922 | 1213327.8256 | 2703715.8244 | 1213346.15
15 | 2703687.9667 | 1213265.4182 | 2703692.1326 | 1213263.9785
16 | 2703687.9667 | 1213265.4182 | 2703683.9048 | 1213253.4502
17 | 2703647.2622 | 1213365.5816 | 2703651.6683 | 1213321.06 | 2703652.4842 | 1213316.9601 | 2703653.45 | 1213313.8525 | 2703654.8009 | 1213311.3186 | 2703656.9168 | 1213308.4867 | 2703678.0999 | 1213287.5178
18 | 2703749.9606 | 1213312.6956 | 2703729.1558 | 1213320.4739
19 | 2703728.0969 | 1213381.6651 | 2703715.8244 | 1213346.15
20 | 2703683.9048 | 1213253.4502 | 2703680.1138 | 1213242.193
21 | 2703683.9048 | 1213253.4502 | 2703697.4629 | 1213248.1029
22 | 2703647.2622 | 1213365.5816 | 2703680.4891 | 1213368.5502
23 | 2703750.6361 | 1213312.443 | 2703749.9606 | 1213312.6956
24 | 2703728.0969 | 1213381.6651 | 2703754.1577 | 1213457.1498 | 2703758.6401 | 1213470.2593 | 2703759.9414 | 1213474.0624 | 2703763.2453 | 1213483.7268 | 2703764.3012 | 1213486.7918 | 2703765.183 | 1213489.3867 | 2703769.7293 | 1213487.9092 | 2703819.6929 | 1213470.3997
25 | 2703728.0969 | 1213381.6651 | 2703743.6821 | 1213377.5742
26 | 2703680.1138 | 1213242.193 | 2703677.3736 | 1213234.0562 | 2703673.3847 | 1213222.5831
27 | 2703710.081 | 1213243.1264 | 2703697.4629 | 1213248.1029
28 | 2703680.4891 | 1213368.5502 | 2703680.2579 | 1213361.7525 | 2703679.6939 | 1213358.7961 | 2703679.2962 | 1213357.4776
29 | 2703680.4891 | 1213368.5502 | 2703684.6197 | 1213369.5783 | 2703686.9275 | 1213370.9972 | 2703688.8066 | 1213373.0424 | 2703689.9347 | 1213375.019 | 2703690.9567 | 1213377.4162 | 2703692.3278 | 1213381.4335
30 | 2703752.4425 | 1213311.7676 | 2703750.6361 | 1213312.443
31 | 2703819.6929 | 1213470.3997 | 2703835.8762 | 1213464.7219 | 2703894.3572 | 1213440.2453 | 2703923.0347 | 1213421.3092 | 2703923.0347 | 1213421.3092
32 | 2703821.868 | 1213654.3126 | 2703797.1672 | 1213582.8541 | 2703796.4709 | 1213580.5181 | 2703787.5032 | 1213554.0544 | 2703765.183 | 1213489.3867 | 2703769.7293 | 1213487.9092 | 2703819.6929 | 1213470.3997
33 | 2703755.2631 | 1213375.6418 | 2703754.0647 | 1213375.2123 | 2703751.7736 | 1213375.4503 | 2703743.6821 | 1213377.5742
34 | 2703755.2631 | 1213375.6418 | 2703755.4993 | 1213375.7265 | 2703756.7881 | 1213376.7607 | 2703757.5066 | 1213378.2632 | 2703759.8475 | 1213385.7767
35 | 2703760.0077 | 1213386.291 | 2703759.8475 | 1213385.7767
36 | 2704077.6261 | 1213434.708 | 2704037.6419 | 1213417.2713 | 2703993.5446 | 1213408.1068 | 2703955.7687 | 1213412.0065 | 2703923.0347 | 1213421.3092
37 | 2703821.868 | 1213654.3126 | 2703808.0946 | 1213655.5738 | 2703802.214 | 1213656.4498 | 2703797.9938 | 1213657.5327 | 2703793.5697 | 1213659.4125 | 2703789.7509 | 1213661.8701 | 2703786.466 | 1213664.2145 | 2703784.2455 | 1213666.5109 | 2703782.7207 | 1213668.9972 | 2703781.187 | 1213672.4285 | 2703779.5399 | 1213674.5236 | 2703777.99 | 1213675.8308 | 2703774.913 | 1213677.5785
38 | 2703821.868 | 1213654.3126 | 2703832.2228 | 1213684.8611
39 | 2703844.5287 | 1213721.1658 | 2703832.2228 | 1213684.8611
40 | 2703692.702 | 1213382.5301 | 2703692.3278 | 1213381.4335
41 | 2703673.8753 | 1213339.5035 | 2703679.2962 | 1213357.4776
42 | 2703731.0999 | 1213254.3277 | 2703737.1196 | 1213274.0243
43 | 2703725.7837 | 1213236.9333 | 2703731.0999 | 1213254.3277
44 | 2703725.7837 | 1213236.9333 | 2703730.578 | 1213235.5606
45 | 2703725.7837 | 1213236.9333 | 2703724.3284 | 1213237.5073
46 | 2703730.578 | 1213235.5606 | 2703730.7624 | 1213235.5078 | 2703739.9264 | 1213234.1551 | 2703742.8431 | 1213234.2059
47 | 2703710.081 | 1213243.1264 | 2703724.3284 | 1213237.5073
48 | 2703755.4975 | 1213257.5648 | 2703747.0772 | 1213238.894 | 2703745.0291 | 1213235.645 | 2703742.8431 | 1213234.2059
49 | 2703801.7398 | 1213345.6042 | 2703795.9063 | 1213326.9673
50 | 2703793.9707 | 1213320.7833 | 2703795.9063 | 1213326.9673
51 | 2703801.7398 | 1213345.6042 | 2703804.4204 | 1213354.168
52 | 2703773.4854 | 1213303.9003 | 2703781.6711 | 1213300.8398 | 2703788.4753 | 1213303.2266 | 2703793.9707 | 1213320.7833
53 | 2703804.835 | 1213355.4929 | 2703804.4204 | 1213354.168
54 | 2703768.0278 | 1213305.9407 | 2703773.4854 | 1213303.9003
55 | 2703768.0278 | 1213305.9407 | 2703752.4425 | 1213311.7676
56 | 2703778.8085 | 1214130.5015 | 2703778.3709 | 1214132.0728 | 2703777.4641 | 1214134.4143 | 2703775.7243 | 1214137.475 | 2703736.4024 | 1214196.4105 | 2703734.441 | 1214198.678 | 2703732.7234 | 1214200.0269 | 2703730.9976 | 1214200.9753 | 2703728.3774 | 1214201.3744 | 2703725.0973 | 1214201.2729 | 2703716.0784 | 1214199.6148 | 2703710.2863 | 1214198.9358 | 2703704.4403 | 1214198.734 | 2703698.4624 | 1214199.564 | 2703694.5037 | 1214200.9183
57 | 2703778.8085 | 1214130.5015 | 2703785.7143 | 1214135.7254 | 2703816.3409 | 1214167.7814 | 2703848.1776 | 1214213.6461 | 2703869.0393 | 1214237.1262 | 2703872.2539 | 1214242.2859
58 | 2703778.8085 | 1214130.5015 | 2703778.8259 | 1214129.0675 | 2703778.0629 | 1214127.075 | 2703776.7029 | 1214124.9054 | 2703730.027 | 1214068.2085 | 2703725.9729 | 1214062.3782 | 2703723.9371 | 1214058.0064 | 2703722.2429 | 1214052.7732 | 2703718.3018 | 1214035.6149
59 | 2703872.2539 | 1214242.2859 | 2703869.9371 | 1214243.5798 | 2703868.8703 | 1214244.6397 | 2703868.1581 | 1214245.8393 | 2703867.9701 | 1214246.5208
60 | 2703714.8915 | 1214020.767 | 2703718.3018 | 1214035.6149
61 | 2703871.3363 | 1214282.2872 | 2703868.2987 | 1214259.129 | 2703867.5905 | 1214247.8975 | 2703867.9701 | 1214246.5208
62 | 2703699.8106 | 1213939.6138 | 2703699.5327 | 1213942.4887 | 2703699.7569 | 1213946.6289 | 2703700.5389 | 1213952.7691 | 2703708.7901 | 1213994.1976 | 2703714.8915 | 1214020.767
63 | 2703714.8915 | 1214020.767 | 2703711.6357 | 1214024.0683 | 2703708.469 | 1214026.615 | 2703703.6811 | 1214028.9001 | 2703699.8209 | 1214031.1345 | 2703697.6466 | 1214033.4094 | 2703693.9847 | 1214040.8399 | 2703691.0385 | 1214047.3044 | 2703689.1411 | 1214049.8176 | 2703686.7986 | 1214051.278 | 2703679.5017 | 1214053.5703
64 | 2703871.3363 | 1214282.2872 | 2703872.2431 | 1214281.6915 | 2703878.9193 | 1214278.7168 | 2703890.2209 | 1214274.0548 | 2703893.1914 | 1214273.1726 | 2703896.4974 | 1214272.6521 | 2703899.7246 | 1214272.7306 | 2703903.1377 | 1214273.4795 | 2703906.2233 | 1214274.7119 | 2703909.2358 | 1214276.2099 | 2703912.3405 | 1214278.0876 | 2703915.818 | 1214280.8057 | 2703937.1865 | 1214303.0717 | 2703954.8277 | 1214320.3916
65 | 2703954.8277 | 1214320.3916 | 2703962.2721 | 1214327.6992
66 | 2703871.3363 | 1214282.2872 | 2703870.2987 | 1214282.9808 | 2703869.3948 | 1214284.2771 | 2703868.8616 | 1214285.6688 | 2703867.2846 | 1214290.7227 | 2703865.9768 | 1214295.1475 | 2703864.219 | 1214297.4963 | 2703862.9296 | 1214298.6858 | 2703860.4156 | 1214299.9652 | 2703857.6911 | 1214300.7244
67 | 2703962.2721 | 1214327.6992 | 2703963.8574 | 1214329.2553 | 2703976.8881 | 1214344.6496
68 | 2703846.671 | 1214308.3762 | 2703848.9838 | 1214305.1253 | 2703850.9818 | 1214303.3811 | 2703852.5644 | 1214302.3635 | 2703854.3697 | 1214301.6499 | 2703857.6911 | 1214300.7244
69 | 2703699.8106 | 1213939.6138 | 2703700.0528 | 1213937.0495 | 2703701.2468 | 1213930.8659 | 2703702.2794 | 1213925.2242 | 2703702.736 | 1213918.1939 | 2703702.9457 | 1213909.6359 | 2703702.3609 | 1213887.7991 | 2703702.5287 | 1213879.0291 | 2703703.6115 | 1213865.7051 | 2703704.5162 | 1213851.6998 | 2703704.9047 | 1213843.7787 | 2703704.8134 | 1213841.6336
70 | 2703699.8106 | 1213939.6138 | 2703686.1667 | 1213941.1504
71 | 2703990.771 | 1214153.8975 | 2703998.5462 | 1214176.9979
72 | 2703978.883 | 1214118.5784 | 2703990.771 | 1214153.8975
73 | 2704032.7652 | 1214278.662 | 2703998.5462 | 1214176.9979
74 | 2703941.2078 | 1214007.6427 | 2703978.883 | 1214118.5784
75 | 2704032.7652 | 1214278.662 | 2704052.5543 | 1214337.4553
76 | 2703941.2078 | 1214007.6427 | 2703936.1156 | 1213992.3443
77 | 2703941.2078 | 1214007.6427 | 2703922.1008 | 1214031.6267 | 2703891.2995 | 1214060.1214 | 2703885.4081 | 1214077.331 | 2703884.7539 | 1214114.8574 | 2703886.565 | 1214124.2882
78 | 2704055.8714 | 1214347.3102 | 2704052.5543 | 1214337.4553
79 | 2703936.1156 | 1213992.3443 | 2703930.7694 | 1213976.2829 | 2703923.5208 | 1213955.0152
80 | 2703886.565 | 1214124.2882 | 2703889.6152 | 1214140.1712 | 2703883.9591 | 1214143.8864 | 2703862.6707 | 1214149.6642 | 2703856.2767 | 1214145.1607 | 2703850.8443 | 1214130.7747
81 | 2704089.4115 | 1214445.5397 | 2704074.1212 | 1214401.5303 | 2704055.8714 | 1214347.3102
82 | 2703915.7222 | 1213932.1337 | 2703923.5208 | 1213955.0152
83 | 2703843.3436 | 1214110.9111 | 2703850.8443 | 1214130.7747
84 | 2703653.1015 | 1213944.8742 | 2703686.1667 | 1213941.1504
85 | 2703649.8681 | 1213945.2384 | 2703653.1015 | 1213944.8742
86 | 2703704.8134 | 1213841.6336 | 2703704.4302 | 1213832.6292 | 2703702.6726 | 1213813.574 | 2703701.9814 | 1213807.8913 | 2703701.1127 | 1213803.6732 | 2703699.7647 | 1213799.0576 | 2703697.026 | 1213792.2829 | 2703685.6859 | 1213770.0778
87 | 2703925.7715 | 1213769.5177 | 2703948.0092 | 1213763.5942
88 | 2703925.7715 | 1213769.5177 | 2703892.2815 | 1213778.4386
89 | 2703953.5091 | 1213762.1292 | 2703948.0092 | 1213763.5942
90 | 2703876.0631 | 1213782.7588 | 2703892.2815 | 1213778.4386
91 | 2703955.0082 | 1213761.7299 | 2703953.5091 | 1213762.1292
92 | 2703888.7465 | 1213811.3222 | 2703876.0631 | 1213782.7588
93 | 2703866.2779 | 1213785.368 | 2703876.0631 | 1213782.7588
94 | 2703955.0082 | 1213761.7299 | 2703971.8799 | 1213757.2357
95 | 2703866.2779 | 1213785.368 | 2703876.1285 | 1213814.6076
96 | 2703866.2779 | 1213785.368 | 2703863.8503 | 1213778.1872
97 | 2703971.8799 | 1213757.2357 | 2703976.8998 | 1213755.8985
98 | 2703883.2253 | 1213835.6729 | 2703876.1285 | 1213814.6076
99 | 2703863.8503 | 1213778.1872 | 2703845.8443 | 1213784.5205
100 | 2703844.5287 | 1213721.1658 | 2703863.8503 | 1213778.1872
101 | 2703826.2617 | 1213727.5706 | 2703825.844 | 1213727.7171
102 | 2703844.5287 | 1213721.1658 | 2703826.2617 | 1213727.5706
103 | 2703844.7308 | 1213784.9121 | 2703845.8443 | 1213784.5205
104 | 2704013.1074 | 1214404.0453 | 2704011.5208 | 1214403.9842 | 2704007.8581 | 1214404.0537 | 2704003.3098 | 1214404.8082 | 2703997.062 | 1214406.3114 | 2703987.6333 | 1214407.6924 | 2703981.8006 | 1214408.0465 | 2703976.2518 | 1214407.8051 | 2703968.7011 | 1214406.4837 | 2703960.9215 | 1214404.3465
105 | 2703922.3173 | 1214387.7173 | 2703929.1438 | 1214391.7947 | 2703940.6855 | 1214397.3109 | 2703951.1218 | 1214401.3068 | 2703960.9215 | 1214404.3465
106 | 2704018.983 | 1214404.2813 | 2704013.1074 | 1214404.0453
107 | 2703915.9331 | 1214393.5546 | 2703918.3458 | 1214391.1171 | 2703922.3173 | 1214387.7173
108 | 2703922.3173 | 1214387.7173 | 2703909.2127 | 1214379.9055 | 2703905.8113 | 1214377.6224 | 2703902.3094 | 1214375.8713 | 2703900.0408 | 1214375.2758 | 2703898.8814 | 1214375.3509
109 | 2704018.983 | 1214404.2813 | 2704013.8371 | 1214392.2718 | 2704009.0783 | 1214384.1942 | 2704000.1874 | 1214372.175 | 2703976.8881 | 1214344.6496
110 | 2704089.4115 | 1214445.5397 | 2704078.3427 | 1214445.5798 | 2704075.0135 | 1214445.2548 | 2704072.2782 | 1214444.4176 | 2704069.6749 | 1214442.9822 | 2704067.5839 | 1214441.3557 | 2704055.6208 | 1214428.6601 | 2704051.4272 | 1214424.3283 | 2704047.1688 | 1214420.6625 | 2704043.3503 | 1214417.905 | 2704025.1682 | 1214406.8021 | 2704018.983 | 1214404.2813
111 | 2703915.9331 | 1214393.5546 | 2703914.1386 | 1214396.7033 | 2703913.3872 | 1214400.1483 | 2703913.3468 | 1214402.4659
112 | 2704089.4115 | 1214445.5397 | 2704093.643 | 1214445.091 | 2704098.1041 | 1214445.4136 | 2704100.67 | 1214445.9476
113 | 2704100.67 | 1214445.9476 | 2704107.4867 | 1214430.1443 | 2704109.9666 | 1214426.0291 | 2704115.6102 | 1214419.1116 | 2704125.2343 | 1214409.7332
114 | 2703663.6146 | 1213194.4821 | 2703673.3847 | 1213222.5831
115 | 2703992.0922 | 1213751.8516 | 2703976.8998 | 1213755.8985
116 | 2704001.5466 | 1213749.3332 | 2703992.0922 | 1213751.8516
117 | 2703832.5856 | 1213789.1839 | 2703844.7308 | 1213784.9121
118 | 2703891.4146 | 1213859.9815 | 2703883.2253 | 1213835.6729
119 | 2703915.7222 | 1213932.1337 | 2703902.7892 | 1213938.7582
120 | 2703915.7222 | 1213932.1337 | 2703891.4146 | 1213859.9815
121 | 2703871.8835 | 1213953.6741 | 2703875.7435 | 1213952.3293 | 2703878.9427 | 1213950.973 | 2703902.7892 | 1213938.7582
122 | 2703850.4837 | 1213951.422 | 2703863.5057 | 1213954.0062 | 2703867.9222 | 1213954.2945 | 2703871.8835 | 1213953.6741

## bus_geodata
| x | y | coords
0 | 2703397.2921 | 1213837.1135
1 | 2703423.6922 | 1213809.2482
2 | 2703470.2491 | 1213793.4515
3 | 2703473.4198 | 1213792.4211
4 | 2703491.6057 | 1213786.5149
5 | 2703531.6245 | 1213773.5179
6 | 2703571.6052 | 1213752.3305
7 | 2703615.2808 | 1213729.2211
8 | 2703667.3749 | 1213695.2652
9 | 2703697.3439 | 1213292.3825
10 | 2703692.8107 | 1213279.1566
11 | 2703709.4922 | 1213327.8256
12 | 2703687.9667 | 1213265.4182
13 | 2703678.0999 | 1213287.5178
14 | 2703729.1558 | 1213320.4739
15 | 2703715.8244 | 1213346.15
16 | 2703692.1326 | 1213263.9785
17 | 2703683.9048 | 1213253.4502
18 | 2703647.2622 | 1213365.5816
19 | 2703749.9606 | 1213312.6956
20 | 2703728.0969 | 1213381.6651
21 | 2703680.1138 | 1213242.193
22 | 2703697.4629 | 1213248.1029
23 | 2703680.4891 | 1213368.5502
24 | 2703750.6361 | 1213312.443
25 | 2703819.6929 | 1213470.3997
26 | 2703743.6821 | 1213377.5742
27 | 2703755.2631 | 1213375.6418
28 | 2703759.8475 | 1213385.7767
29 | 2703760.0077 | 1213386.291
30 | 2703923.0347 | 1213421.3092
31 | 2703821.868 | 1213654.3126
32 | 2704077.6261 | 1213434.708
33 | 2703774.913 | 1213677.5785
34 | 2703832.2228 | 1213684.8611
35 | 2703692.3278 | 1213381.4335
36 | 2703692.702 | 1213382.5301
37 | 2703679.2962 | 1213357.4776
38 | 2703673.8753 | 1213339.5035
39 | 2703737.1196 | 1213274.0243
40 | 2703731.0999 | 1213254.3277
41 | 2703725.7837 | 1213236.9333
42 | 2703730.578 | 1213235.5606
43 | 2703724.3284 | 1213237.5073
44 | 2703742.8431 | 1213234.2059
45 | 2703710.081 | 1213243.1264
46 | 2703795.9063 | 1213326.9673
47 | 2703801.7398 | 1213345.6042
48 | 2703793.9707 | 1213320.7833
49 | 2703804.4204 | 1213354.168
50 | 2703773.4854 | 1213303.9003
51 | 2703804.835 | 1213355.4929
52 | 2703768.0278 | 1213305.9407
53 | 2703752.4425 | 1213311.7676
54 | 2703694.5037 | 1214200.9183
55 | 2703778.8085 | 1214130.5015
56 | 2703872.2539 | 1214242.2859
57 | 2703718.3018 | 1214035.6149
58 | 2703867.9701 | 1214246.5208
59 | 2703714.8915 | 1214020.767
60 | 2703954.8277 | 1214320.3916
61 | 2703871.3363 | 1214282.2872
62 | 2703962.2721 | 1214327.6992
63 | 2703857.6911 | 1214300.7244
64 | 2703699.8106 | 1213939.6138
65 | 2703679.5017 | 1214053.5703
66 | 2703990.771 | 1214153.8975
67 | 2703998.5462 | 1214176.9979
68 | 2703978.883 | 1214118.5784
69 | 2704032.7652 | 1214278.662
70 | 2703941.2078 | 1214007.6427
71 | 2704052.5543 | 1214337.4553
72 | 2703936.1156 | 1213992.3443
73 | 2703886.565 | 1214124.2882
74 | 2704055.8714 | 1214347.3102
75 | 2703923.5208 | 1213955.0152
76 | 2703850.8443 | 1214130.7747
77 | 2703755.4975 | 1213257.5648
78 | 2703653.1015 | 1213944.8742
79 | 2703686.1667 | 1213941.1504
80 | 2703649.8681 | 1213945.2384
81 | 2703704.8134 | 1213841.6336
82 | 2703685.6859 | 1213770.0778
83 | 2703925.7715 | 1213769.5177
84 | 2703948.0092 | 1213763.5942
85 | 2703892.2815 | 1213778.4386
86 | 2703953.5091 | 1213762.1292
87 | 2703876.0631 | 1213782.7588
88 | 2703955.0082 | 1213761.7298
89 | 2703888.7465 | 1213811.3222
90 | 2703866.2779 | 1213785.368
91 | 2703971.8799 | 1213757.2357
92 | 2703876.1285 | 1213814.6076
93 | 2703863.8503 | 1213778.1872
94 | 2703825.844 | 1213727.7171
95 | 2703826.2617 | 1213727.5706
96 | 2703844.5287 | 1213721.1658
97 | 2703845.8443 | 1213784.5205
98 | 2703960.9215 | 1214404.3465
99 | 2704013.1074 | 1214404.0453
100 | 2703922.3173 | 1214387.7173
101 | 2704018.983 | 1214404.2813
102 | 2703915.9331 | 1214393.5546
103 | 2703898.8814 | 1214375.3509
104 | 2703976.8881 | 1214344.6496
105 | 2704089.4115 | 1214445.5397
106 | 2703913.3468 | 1214402.4659
107 | 2704100.67 | 1214445.9476
108 | 2703673.3847 | 1213222.5831
109 | 2703976.8998 | 1213755.8985
110 | 2703992.0922 | 1213751.8516
111 | 2704001.5466 | 1213749.3332
112 | 2703846.671 | 1214308.3762
113 | 2703844.7308 | 1213784.9121
114 | 2704125.2343 | 1214409.7332
115 | 2703832.5856 | 1213789.1839
116 | 2703663.6146 | 1213194.4821
117 | 2703883.2253 | 1213835.6729
118 | 2703843.3436 | 1214110.9111
119 | 2703915.7222 | 1213932.1337
120 | 2703891.4146 | 1213859.9815
121 | 2703902.7892 | 1213938.7582
122 | 2703871.8835 | 1213953.6741
123 | 2703850.4837 | 1213951.422
124 | 2703822.1854 | 1213497.8515

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97001 | -0.21433 | 0.0024088 | 0.00060371
1 | 0.97015 | -0.21335 | 0 | 0
2 | 0.97032 | -0.21209 | 0.0014719 | 0.00036889
3 | 0.97034 | -0.21195 | 0 | 0
4 | 0.97038 | -0.21169 | 0.001986 | 0.00049773
5 | 0.9705 | -0.21081 | 0 | 0
6 | 0.97063 | -0.20987 | 0 | 0
7 | 0.97077 | -0.20883 | 0.0011594 | 0.00029057
8 | 0.97098 | -0.20727 | 0 | 0
9 | 0.97921 | -0.1451 | 0.0024887 | 0.00062373
10 | 0.97766 | -0.15616 | 0 | 0
11 | 0.98351 | -0.11467 | 0 | 0
12 | 0.97678 | -0.16247 | 0 | 0
13 | 0.9768 | -0.16227 | 0.0039635 | 0.00099336
14 | 0.98192 | -0.12594 | 0.0054915 | 0.0013763
15 | 0.98536 | -0.10167 | 0.0030707 | 0.00076959
16 | 0.97677 | -0.16257 | 0.0021556 | 0.00054026
17 | 0.97605 | -0.16767 | 0 | 0
18 | 0.97285 | -0.19055 | 0 | 0
19 | 0.98042 | -0.13663 | 0.0031051 | 0.00077821
20 | 0.98779 | -0.084536 | 0 | 0
21 | 0.97578 | -0.16963 | 0.0026164 | 0.00065573
22 | 0.97555 | -0.17126 | 0.0020358 | 0.00051023
23 | 0.97137 | -0.20124 | 0 | 0
24 | 0.98037 | -0.13695 | 0.0031188 | 0.00078165
25 | 1 | 0 | -0.22727 | -0.057261
26 | 0.9875 | -0.086651 | 0.0038793 | 0.00097225
27 | 0.98734 | -0.087745 | 0.0029787 | 0.00074654
28 | 0.98724 | -0.088444 | 0.0028799 | 0.00072178
29 | 0.98724 | -0.088461 | 0.0030868 | 0.00077362
30 | 0.99954 | -0.0032449 | 0.0015632 | 0.00039179
31 | 0.99182 | -0.057304 | 0 | 0
32 | 0.99926 | -0.0052538 | 0.0012435 | 0.00031164
33 | 0.99169 | -0.058221 | 0.0016254 | 0.00040737
34 | 0.99071 | -0.06516 | 0.00089107 | 0.00022332
35 | 0.97106 | -0.20344 | 0.0048837 | 0.001224
36 | 0.97105 | -0.20352 | 0.0061181 | 0.0015333
37 | 0.97105 | -0.20355 | 0.0050356 | 0.001262
38 | 0.97065 | -0.20641 | 0.014408 | 0.0036111
39 | 0.97446 | -0.1791 | 0.0023275 | 0.00058333
40 | 0.97453 | -0.1786 | 0.0028157 | 0.00070567
41 | 0.97467 | -0.17762 | 0 | 0
42 | 0.97458 | -0.17824 | 0.002391 | 0.00059925
43 | 0.97471 | -0.17734 | 0.0017351 | 0.00043486
44 | 0.97441 | -0.17948 | 0.0055737 | 0.0013969
45 | 0.97513 | -0.17431 | 0.0026487 | 0.00066384
46 | 0.97721 | -0.15951 | 0.0027339 | 0.00068517
47 | 0.97656 | -0.16421 | 0.004295 | 0.0010764
48 | 0.97746 | -0.15776 | 0.0061613 | 0.0015442
49 | 0.97631 | -0.16596 | 0.0048936 | 0.0012265
50 | 0.97906 | -0.14633 | 0.0027512 | 0.00068952
51 | 0.97629 | -0.16617 | 0.013827 | 0.0034653
52 | 0.97935 | -0.14423 | 0.0027223 | 0.00068227
53 | 0.98026 | -0.13776 | 0.0028115 | 0.00070463
54 | 0.97395 | -0.18575 | 0.00032866 | 8.2369e-05
55 | 0.974 | -0.18532 | 0 | 0
56 | 0.97531 | -0.17582 | 0 | 0
57 | 0.973 | -0.19264 | 0.00041329 | 0.00010358
58 | 0.97537 | -0.17541 | 0.00044654 | 0.00011191
59 | 0.97287 | -0.19359 | 0 | 0
60 | 0.97668 | -0.16592 | 0 | 0
61 | 0.9757 | -0.17301 | 0 | 0
62 | 0.97678 | -0.16521 | 0.00023617 | 5.9189e-05
63 | 0.97569 | -0.17313 | 0.00032579 | 8.1651e-05
64 | 0.97222 | -0.19826 | 0 | 0
65 | 0.97274 | -0.19449 | 0.0016884 | 0.00042314
66 | 0.98176 | -0.12913 | 0.00061029 | 0.00015295
67 | 0.9815 | -0.13102 | 0.00016659 | 4.1751e-05
68 | 0.98217 | -0.12617 | 0 | 0
69 | 0.98036 | -0.13928 | 0.00041674 | 0.00010445
70 | 0.98347 | -0.11685 | 0 | 0
71 | 0.97971 | -0.14396 | 0.00045173 | 0.00011321
72 | 0.98366 | -0.11545 | 0.0054204 | 0.0013585
73 | 0.98332 | -0.11789 | 0.0014958 | 0.0003749
74 | 0.97961 | -0.14473 | 0.00013928 | 3.4907e-05
75 | 0.98424 | -0.11129 | 0.0020164 | 0.00050535
76 | 0.98326 | -0.11836 | 0.00032614 | 8.1739e-05
77 | 0.97425 | -0.1806 | 0.0039579 | 0.00099195
78 | 0.97199 | -0.19991 | 0.00066795 | 0.0001674
79 | 0.97214 | -0.19887 | 0.0012521 | 0.0003138
80 | 0.97198 | -0.19999 | 0.0022775 | 0.00057079
81 | 0.97166 | -0.20236 | 0.00058647 | 0.00014698
82 | 0.97125 | -0.20533 | 0.0040904 | 0.0010252
83 | 0.98659 | -0.094389 | 0.0019371 | 0.00048548
84 | 0.9863 | -0.096431 | 0.00237 | 0.00059398
85 | 0.98691 | -0.09211 | 0.0042419 | 0.0010631
86 | 0.98618 | -0.097302 | 0.0032851 | 0.00082332
87 | 0.9871 | -0.090763 | 0 | 0
88 | 0.98616 | -0.097488 | 0.0024178 | 0.00060596
89 | 0.98705 | -0.091107 | 0.0010735 | 0.00026904
90 | 0.98722 | -0.089916 | 0 | 0
91 | 0.98592 | -0.099141 | 0.0014666 | 0.00036757
92 | 0.98669 | -0.093749 | 0.00046952 | 0.00011767
93 | 0.98744 | -0.088339 | 0 | 0
94 | 0.98932 | -0.075004 | 0.0017703 | 0.00044369
95 | 0.98932 | -0.074996 | 0.0012445 | 0.0003119
96 | 0.98941 | -0.074401 | 0 | 0
97 | 0.98735 | -0.089027 | 0.0014261 | 0.00035743
98 | 0.97761 | -0.15918 | 0.00021866 | 5.4802e-05
99 | 0.97769 | -0.15862 | 0 | 0
100 | 0.97756 | -0.15954 | 0 | 0
101 | 0.9777 | -0.15856 | 0 | 0
102 | 0.97756 | -0.15957 | 0 | 0
103 | 0.97755 | -0.15964 | 0.00038554 | 9.6626e-05
104 | 0.97699 | -0.16367 | 0.00022201 | 5.564e-05
105 | 0.97855 | -0.15237 | 0 | 0
106 | 0.97755 | -0.15961 | 0.00040729 | 0.00010208
107 | 0.97855 | -0.15239 | 0 | 0
108 | 0.97538 | -0.1725 | 0.0081205 | 0.0020352
109 | 0.98586 | -0.099555 | 0.0019004 | 0.00047629
110 | 0.98573 | -0.1005 | 0.0014956 | 0.00037482
111 | 0.98567 | -0.10094 | 0.0043576 | 0.0010921
112 | 0.97568 | -0.17314 | 0.00011399 | 2.857e-05
113 | 0.98734 | -0.089094 | 0.0021863 | 0.00054794
114 | 0.97854 | -0.15244 | 0.00012257 | 3.072e-05
115 | 0.98727 | -0.089545 | 0.0034171 | 0.00085641
116 | 0.97516 | -0.17408 | 0.0050507 | 0.0012658
117 | 0.98631 | -0.096477 | 0.00067836 | 0.00017001
118 | 0.98325 | -0.11843 | 0.00033024 | 8.2765e-05
119 | 0.98462 | -0.10857 | 0 | 0
120 | 0.98587 | -0.099567 | 0.00068079 | 0.00017062
121 | 0.98461 | -0.10866 | 0.00059825 | 0.00014994
122 | 0.98458 | -0.10886 | 0.00081408 | 0.00020403
123 | 0.98457 | -0.10893 | 0.00032062 | 8.0354e-05
124 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0024088 | -0.00060371 | 0.0024092 | 0.00060336 | 3.2705e-07 | -3.4812e-07 | 0.0036952 | 0.003695 | 0.0036952 | 0.97001 | -0.21433 | 0.97015 | -0.21335 | 1.3686
1 | -0.0024092 | -0.00060336 | 0.0024096 | 0.00060292 | 4.1888e-07 | -4.4613e-07 | 0.003695 | 0.0036948 | 0.003695 | 0.97015 | -0.21335 | 0.97032 | -0.21209 | 1.3685
2 | -0.0038815 | -0.00097181 | 0.0038815 | 0.0009718 | 7.3701e-08 | -1.2836e-08 | 0.005952 | 0.005952 | 0.005952 | 0.97032 | -0.21209 | 0.97034 | -0.21195 | 2.2044
3 | -0.0038815 | -0.0009718 | 0.0038817 | 0.00097114 | 1.4089e-07 | -6.5442e-07 | 0.005952 | 0.0059517 | 0.005952 | 0.97034 | -0.21195 | 0.97038 | -0.21169 | 0.73481
4 | -0.0058677 | -0.0014689 | 0.0058684 | 0.0014676 | 7.084e-07 | -1.2871e-06 | 0.0089971 | 0.0089965 | 0.0089971 | 0.97038 | -0.21169 | 0.9705 | -0.21081 | 1.1108
5 | -0.0058684 | -0.0014676 | 0.0058691 | 0.0014662 | 7.6454e-07 | -1.3898e-06 | 0.0089965 | 0.0089959 | 0.0089965 | 0.9705 | -0.21081 | 0.97063 | -0.20987 | 1.1107
6 | -0.0058691 | -0.0014662 | 0.00587 | 0.0014647 | 8.3169e-07 | -1.5126e-06 | 0.0089959 | 0.0089953 | 0.0089959 | 0.97063 | -0.20987 | 0.97077 | -0.20883 | 1.1106
7 | -0.0070294 | -0.0017553 | 0.0070309 | 0.0017535 | 1.5081e-06 | -1.7381e-06 | 0.010772 | 0.010772 | 0.010772 | 0.97077 | -0.20883 | 0.97098 | -0.20727 | 1.3299
8 | -0.0070309 | -0.0017535 | 0.0070327 | 0.0017514 | 1.8656e-06 | -2.152e-06 | 0.010772 | 0.010771 | 0.010772 | 0.97098 | -0.20727 | 0.97125 | -0.20533 | 1.3298
9 | 0.076274 | 0.019169 | -0.076157 | -0.019124 | 0.00011724 | 4.4918e-05 | 0.11593 | 0.11593 | 0.11593 | 0.97921 | -0.1451 | 0.97766 | -0.15616 | 42.9354
10 | -0.078763 | -0.019793 | 0.079098 | 0.019921 | 0.00033502 | 0.00012838 | 0.11971 | 0.11971 | 0.11971 | 0.97921 | -0.1451 | 0.98351 | -0.11467 | 44.336
11 | 0.041538 | 0.010422 | -0.041501 | -0.010408 | 3.6331e-05 | 1.3791e-05 | 0.063225 | 0.063225 | 0.063225 | 0.97766 | -0.15616 | 0.97678 | -0.16247 | 23.4168
12 | 0.034619 | 0.0087022 | -0.03459 | -0.0086911 | 2.9446e-05 | 1.1112e-05 | 0.0527 | 0.0527 | 0.0527 | 0.97766 | -0.15616 | 0.9768 | -0.16227 | 19.5187
13 | 0.052189 | 0.013115 | -0.052107 | -0.013084 | 8.1698e-05 | 3.1156e-05 | 0.078973 | 0.078973 | 0.078973 | 0.98351 | -0.11467 | 0.98192 | -0.12594 | 29.2492
14 | -0.13129 | -0.033037 | 0.13153 | 0.033128 | 0.00023877 | 9.1343e-05 | 0.19868 | 0.19868 | 0.19868 | 0.98351 | -0.11467 | 0.98536 | -0.10167 | 36.7926
15 | 0.0021557 | 0.00054021 | -0.0021556 | -0.00054026 | 2.9582e-08 | -4.3647e-08 | 0.0032839 | 0.0032839 | 0.0032839 | 0.97678 | -0.16247 | 0.97677 | -0.16257 | 1.2163
16 | 0.039346 | 0.0098681 | -0.039317 | -0.0098574 | 2.833e-05 | 1.0738e-05 | 0.059941 | 0.059941 | 0.059941 | 0.97678 | -0.16247 | 0.97605 | -0.16767 | 22.2005
17 | 0.030626 | 0.0076977 | -0.030506 | -0.0076527 | 0.00012009 | 4.5087e-05 | 0.046663 | 0.046663 | 0.046663 | 0.9768 | -0.16227 | 0.97285 | -0.19055 | 17.2826
18 | 0.046616 | 0.011708 | -0.046547 | -0.011682 | 6.9182e-05 | 2.6328e-05 | 0.070651 | 0.070651 | 0.070651 | 0.98192 | -0.12594 | 0.98042 | -0.13663 | 26.1671
19 | -0.1346 | -0.033898 | 0.13492 | 0.03402 | 0.00032309 | 0.00012282 | 0.20332 | 0.20332 | 0.20332 | 0.98536 | -0.10167 | 0.98779 | -0.084536 | 25.1009
20 | 0.015798 | 0.0039601 | -0.015794 | -0.0039586 | 4.2997e-06 | 1.5053e-06 | 0.024085 | 0.024085 | 0.024085 | 0.97605 | -0.16767 | 0.97578 | -0.16963 | 8.9204
21 | 0.023519 | 0.0058973 | -0.023507 | -0.005893 | 1.1693e-05 | 4.3151e-06 | 0.035856 | 0.035856 | 0.035856 | 0.97605 | -0.16767 | 0.97555 | -0.17126 | 13.2801
22 | 0.030506 | 0.0076527 | -0.030461 | -0.0076357 | 4.5194e-05 | 1.697e-05 | 0.046663 | 0.046663 | 0.046663 | 0.97285 | -0.19055 | 0.97137 | -0.20124 | 17.2826
23 | 0.043442 | 0.010903 | -0.04344 | -0.010903 | 1.9568e-06 | 7.435e-07 | 0.065938 | 0.065938 | 0.065938 | 0.98042 | -0.13663 | 0.98037 | -0.13695 | 24.4216
24 | -0.14775 | -0.037236 | 0.14952 | 0.03791 | 0.0017698 | 0.00067402 | 0.22264 | 0.22264 | 0.22264 | 0.98779 | -0.084536 | 1 | 0 | 27.487
25 | 0.01283 | 0.0032159 | -0.012827 | -0.0032146 | 3.7561e-06 | 1.2385e-06 | 0.019328 | 0.019328 | 0.019328 | 0.98779 | -0.084536 | 0.9875 | -0.086651 | 7.1585
26 | 0.013178 | 0.0033028 | -0.013172 | -0.0033011 | 5.2243e-06 | 1.7505e-06 | 0.020095 | 0.020095 | 0.020095 | 0.97578 | -0.16963 | 0.97538 | -0.1725 | 7.4427
27 | 0.021471 | 0.0053828 | -0.021462 | -0.0053794 | 9.0787e-06 | 3.3225e-06 | 0.032751 | 0.032751 | 0.032751 | 0.97555 | -0.17126 | 0.97513 | -0.17431 | 12.1301
28 | 0.019456 | 0.0048773 | -0.01945 | -0.0048751 | 6.2019e-06 | 2.2469e-06 | 0.029805 | 0.029805 | 0.029805 | 0.97137 | -0.20124 | 0.97105 | -0.20355 | 11.0387
29 | 0.011005 | 0.0027584 | -0.011002 | -0.0027573 | 3.3465e-06 | 1.0536e-06 | 0.016859 | 0.016859 | 0.016859 | 0.97137 | -0.20124 | 0.97106 | -0.20344 | 6.244
30 | 0.040321 | 0.010121 | -0.040316 | -0.010119 | 4.5078e-06 | 1.7095e-06 | 0.061205 | 0.061205 | 0.061205 | 0.98037 | -0.13695 | 0.98026 | -0.13776 | 22.6684
31 | 0.0028083 | 0.00070043 | -0.0028071 | -0.00070146 | 1.2516e-06 | -1.0255e-06 | 0.0041776 | 0.0041782 | 0.0041782 | 1 | 0 | 0.99954 | -0.0032449 | 1.5475
32 | 0.074144 | 0.018651 | -0.073557 | -0.018434 | 0.00058797 | 0.00021708 | 0.11035 | 0.11036 | 0.11036 | 1 | 0 | 0.99182 | -0.057304 | 13.6241
33 | 0.0089474 | 0.0022424 | -0.008946 | -0.002242 | 1.3546e-06 | 3.6823e-07 | 0.013482 | 0.013482 | 0.013482 | 0.9875 | -0.086651 | 0.98734 | -0.087745 | 4.9935
34 | 0.0059673 | 0.0014955 | -0.0059667 | -0.0014954 | 5.7729e-07 | 7.5757e-08 | 0.0089933 | 0.0089933 | 0.0089933 | 0.98734 | -0.087745 | 0.98724 | -0.088444 | 3.3309
35 | 0.0030868 | 0.00077362 | -0.0030868 | -0.00077362 | 7.2767e-09 | -4.0897e-09 | 0.0046525 | 0.0046526 | 0.0046526 | 0.98724 | -0.088444 | 0.98724 | -0.088461 | 1.7232
36 | 0.0012438 | 0.00030967 | -0.0012435 | -0.00031164 | 3.4361e-07 | -1.9731e-06 | 0.0018509 | 0.0018517 | 0.0018517 | 0.99954 | -0.0032449 | 0.99926 | -0.0052538 | 0.68581
37 | 0.0016256 | 0.00040674 | -0.0016254 | -0.00040737 | 2.0598e-07 | -6.3694e-07 | 0.0024387 | 0.0024389 | 0.0024389 | 0.99182 | -0.057304 | 0.99169 | -0.058221 | 0.90331
38 | 0.071931 | 0.018027 | -0.071853 | -0.017998 | 7.8136e-05 | 2.8805e-05 | 0.10792 | 0.10792 | 0.10792 | 0.99182 | -0.057304 | 0.99071 | -0.06516 | 13.3231
39 | 0.070962 | 0.017775 | -0.070871 | -0.017741 | 9.0571e-05 | 3.3356e-05 | 0.10658 | 0.10658 | 0.10658 | 0.99071 | -0.06516 | 0.98941 | -0.074401 | 13.1579
40 | 0.0061181 | 0.0015333 | -0.0061181 | -0.0015333 | 6.355e-08 | 1.0108e-08 | 0.0093752 | 0.0093752 | 0.0093752 | 0.97106 | -0.20344 | 0.97105 | -0.20352 | 3.4723
41 | 0.014414 | 0.003613 | -0.014408 | -0.0036111 | 5.7155e-06 | 1.9661e-06 | 0.022088 | 0.022088 | 0.022088 | 0.97105 | -0.20355 | 0.97065 | -0.20641 | 8.1808
42 | -0.0023275 | -0.00058333 | 0.0023277 | 0.00058314 | 1.6234e-07 | -1.9416e-07 | 0.0035542 | 0.0035541 | 0.0035542 | 0.97446 | -0.1791 | 0.97453 | -0.1786 | 1.3164
43 | -0.0051434 | -0.0012888 | 0.0051441 | 0.0012889 | 6.9999e-07 | 4.2573e-08 | 0.0078534 | 0.0078533 | 0.0078534 | 0.97453 | -0.1786 | 0.97467 | -0.17762 | 2.9086
44 | 0.011926 | 0.0029888 | -0.011925 | -0.0029885 | 1.0316e-06 | 3.3462e-07 | 0.018207 | 0.018207 | 0.018207 | 0.97467 | -0.17762 | 0.97458 | -0.17824 | 6.7434
45 | -0.01707 | -0.0042777 | 0.017071 | 0.0042779 | 6.6296e-07 | 2.3549e-07 | 0.026061 | 0.026061 | 0.026061 | 0.97467 | -0.17762 | 0.97471 | -0.17734 | 9.652
46 | 0.0095339 | 0.0023892 | -0.0095323 | -0.0023888 | 1.6359e-06 | 4.7505e-07 | 0.014557 | 0.014557 | 0.014557 | 0.97458 | -0.17824 | 0.97441 | -0.17948 | 5.3913
47 | -0.018806 | -0.0047128 | 0.018814 | 0.0047156 | 7.877e-06 | 2.8386e-06 | 0.028709 | 0.028709 | 0.028709 | 0.97471 | -0.17734 | 0.97513 | -0.17431 | 10.6331
48 | 0.0039586 | 0.00099185 | -0.0039579 | -0.00099195 | 6.1429e-07 | -9.9248e-08 | 0.006045 | 0.0060451 | 0.0060451 | 0.97441 | -0.17948 | 0.97425 | -0.1806 | 2.2389
49 | 0.023035 | 0.0057755 | -0.02302 | -0.00577 | 1.4993e-05 | 5.5222e-06 | 0.035077 | 0.035077 | 0.035077 | 0.97721 | -0.15951 | 0.97656 | -0.16421 | 12.9915
50 | -0.025769 | -0.0064607 | 0.025775 | 0.006463 | 6.226e-06 | 2.3134e-06 | 0.03924 | 0.03924 | 0.03924 | 0.97721 | -0.15951 | 0.97746 | -0.15776 | 14.5333
51 | 0.018725 | 0.0046936 | -0.018721 | -0.0046919 | 4.5586e-06 | 1.6411e-06 | 0.028533 | 0.028533 | 0.028533 | 0.97656 | -0.16421 | 0.97631 | -0.16596 | 10.5677
52 | -0.031937 | -0.0080072 | 0.031987 | 0.0080262 | 5.0663e-05 | 1.9054e-05 | 0.04862 | 0.048619 | 0.04862 | 0.97746 | -0.15776 | 0.97906 | -0.14633 | 18.0072
53 | 0.013827 | 0.0034655 | -0.013827 | -0.0034653 | 3.8472e-07 | 1.3061e-07 | 0.021074 | 0.021074 | 0.021074 | 0.97631 | -0.16596 | 0.97629 | -0.16617 | 7.8053
54 | -0.034739 | -0.0087157 | 0.034749 | 0.0087196 | 1.0136e-05 | 3.8253e-06 | 0.052801 | 0.052801 | 0.052801 | 0.97906 | -0.14633 | 0.97935 | -0.14423 | 19.5559
55 | -0.037471 | -0.0094018 | 0.037505 | 0.0094146 | 3.3659e-05 | 1.2736e-05 | 0.056937 | 0.056937 | 0.056937 | 0.97935 | -0.14423 | 0.98026 | -0.13776 | 21.0878
56 | -0.00032866 | -8.2369e-05 | 0.00032868 | 8.085e-05 | 1.9278e-08 | -1.5192e-06 | 0.00050213 | 0.00050158 | 0.00050213 | 0.97395 | -0.18575 | 0.974 | -0.18532 | 0.18597
57 | -0.01838 | -0.0045839 | 0.018404 | 0.0045876 | 2.3953e-05 | 3.7486e-06 | 0.028072 | 0.02807 | 0.028072 | 0.974 | -0.18532 | 0.97531 | -0.17582 | 3.4657
58 | 0.018052 | 0.004503 | -0.018033 | -0.0045003 | 1.8119e-05 | 2.6945e-06 | 0.02757 | 0.027572 | 0.027572 | 0.974 | -0.18532 | 0.973 | -0.19264 | 3.4039
59 | -0.018404 | -0.0045876 | 0.018405 | 0.0045878 | 1.0258e-06 | 1.602e-07 | 0.02807 | 0.02807 | 0.02807 | 0.97531 | -0.17582 | 0.97537 | -0.17541 | 3.4654
60 | 0.01762 | 0.0043968 | -0.017618 | -0.0043965 | 2.2998e-06 | 3.1695e-07 | 0.02694 | 0.02694 | 0.02694 | 0.973 | -0.19264 | 0.97287 | -0.19359 | 3.3259
61 | -0.018852 | -0.0046997 | 0.018858 | 0.0047007 | 6.1963e-06 | 1.0333e-06 | 0.028751 | 0.028751 | 0.028751 | 0.97537 | -0.17541 | 0.9757 | -0.17301 | 3.5495
62 | 0.015929 | 0.0039739 | -0.015919 | -0.003973 | 1.021e-05 | 8.4709e-07 | 0.024357 | 0.024359 | 0.024359 | 0.97287 | -0.19359 | 0.97222 | -0.19826 | 3.0072
63 | 0.0016886 | 0.00042259 | -0.0016884 | -0.00042314 | 2.1042e-07 | -5.4677e-07 | 0.0025825 | 0.0025827 | 0.0025827 | 0.97287 | -0.19359 | 0.97274 | -0.19449 | 0.95656
64 | 0.019316 | 0.0048138 | -0.019298 | -0.0048105 | 1.8742e-05 | 3.304e-06 | 0.02942 | 0.029421 | 0.029421 | 0.97668 | -0.16592 | 0.9757 | -0.17301 | 3.6322
65 | -0.019316 | -0.0048138 | 0.019318 | 0.0048141 | 1.878e-06 | 3.3062e-07 | 0.02942 | 0.02942 | 0.02942 | 0.97668 | -0.16592 | 0.97678 | -0.16521 | 3.6321
66 | 0.00043979 | 0.00010974 | -0.00043978 | -0.00011005 | 6.893e-09 | -3.0414e-07 | 0.00067054 | 0.00067065 | 0.00067065 | 0.9757 | -0.17301 | 0.97569 | -0.17313 | 0.24839
67 | -0.019554 | -0.0048733 | 0.019559 | 0.0048741 | 4.13e-06 | 7.4749e-07 | 0.029779 | 0.029779 | 0.029779 | 0.97678 | -0.16521 | 0.97699 | -0.16367 | 3.6765
68 | 0.00011399 | 2.8396e-05 | -0.00011399 | -2.857e-05 | 2.623e-10 | -1.7365e-07 | 0.00017379 | 0.00017385 | 0.00017385 | 0.97569 | -0.17313 | 0.97568 | -0.17314 | 0.06439
69 | 0.011721 | 0.0029213 | -0.011714 | -0.0029225 | 6.5767e-06 | -1.1257e-06 | 0.017933 | 0.017934 | 0.017934 | 0.97222 | -0.19826 | 0.97166 | -0.20236 | 2.2141
70 | 0.0041983 | 0.0010517 | -0.0041979 | -0.0010517 | 3.5373e-07 | -3.4198e-08 | 0.0064254 | 0.0064255 | 0.0064255 | 0.97222 | -0.19826 | 0.97214 | -0.19887 | 2.3798
71 | 0.022189 | 0.0055266 | -0.022183 | -0.0055254 | 5.73e-06 | 1.2795e-06 | 0.033619 | 0.033619 | 0.033619 | 0.98176 | -0.12913 | 0.9815 | -0.13102 | 4.1505
72 | -0.022799 | -0.0056796 | 0.022809 | 0.0056817 | 9.2494e-06 | 2.1431e-06 | 0.034544 | 0.034543 | 0.034544 | 0.98176 | -0.12913 | 0.98217 | -0.12617 | 4.2647
73 | 0.022017 | 0.0054836 | -0.021992 | -0.0054781 | 2.4842e-05 | 5.492e-06 | 0.033367 | 0.033368 | 0.033368 | 0.9815 | -0.13102 | 0.98036 | -0.13928 | 4.1195
74 | -0.022809 | -0.0056817 | 0.022838 | 0.0056885 | 2.9072e-05 | 6.7282e-06 | 0.034543 | 0.034542 | 0.034543 | 0.98217 | -0.12617 | 0.98347 | -0.11685 | 4.2646
75 | 0.021575 | 0.0053737 | -0.021561 | -0.0053707 | 1.3828e-05 | 2.9733e-06 | 0.032735 | 0.032736 | 0.032736 | 0.98036 | -0.13928 | 0.97971 | -0.14396 | 4.0415
76 | -0.02499 | -0.0062216 | 0.024995 | 0.0062228 | 4.791e-06 | 1.2288e-06 | 0.037796 | 0.037796 | 0.037796 | 0.98347 | -0.11685 | 0.98366 | -0.11545 | 4.6662
77 | 0.0021526 | 0.00053315 | -0.0021523 | -0.00053828 | 3.0412e-07 | -5.1336e-06 | 0.0032547 | 0.0032565 | 0.0032565 | 0.98347 | -0.11685 | 0.98332 | -0.11789 | 0.40204
78 | 0.02111 | 0.0052575 | -0.021107 | -0.005257 | 2.2217e-06 | 4.6173e-07 | 0.03205 | 0.03205 | 0.03205 | 0.97971 | -0.14396 | 0.97961 | -0.14473 | 3.9568
79 | -0.030416 | -0.0075813 | 0.030433 | 0.0075865 | 1.7336e-05 | 5.1666e-06 | 0.045996 | 0.045995 | 0.045996 | 0.98366 | -0.11545 | 0.98424 | -0.11129 | 5.6785
80 | 0.00065642 | 0.00016339 | -0.00065638 | -0.00016424 | 4.1969e-08 | -8.4891e-07 | 0.00099293 | 0.00099324 | 0.00099324 | 0.98332 | -0.11789 | 0.98326 | -0.11836 | 0.36787
81 | 0.020968 | 0.0052221 | -0.020946 | -0.0052176 | 2.1887e-05 | 4.502e-06 | 0.031839 | 0.03184 | 0.03184 | 0.97961 | -0.14473 | 0.97855 | -0.15237 | 3.9309
82 | -0.032449 | -0.0080918 | 0.032461 | 0.0080956 | 1.2094e-05 | 3.7296e-06 | 0.049044 | 0.049043 | 0.049044 | 0.98424 | -0.11129 | 0.98462 | -0.10857 | 6.0548
83 | 0.00033024 | 8.2497e-05 | -0.00033024 | -8.2765e-05 | 3.3086e-09 | -2.6803e-07 | 0.00049967 | 0.00049977 | 0.00049977 | 0.98326 | -0.11836 | 0.98325 | -0.11843 | 0.1851
84 | -0.0029454 | -0.00073816 | 0.0029459 | 0.00073791 | 4.2215e-07 | -2.5012e-07 | 0.0045091 | 0.004509 | 0.0045091 | 0.97199 | -0.19991 | 0.97214 | -0.19887 | 1.67
85 | 0.0022775 | 0.00057076 | -0.0022775 | -0.00057079 | 2.4682e-08 | -3.0837e-08 | 0.0034866 | 0.0034866 | 0.0034866 | 0.97199 | -0.19991 | 0.97198 | -0.19999 | 1.2913
86 | 0.011128 | 0.0027755 | -0.011123 | -0.0027765 | 4.5418e-06 | -1.0474e-06 | 0.017036 | 0.017037 | 0.017037 | 0.97166 | -0.20236 | 0.97125 | -0.20533 | 2.1034
87 | 0.017304 | 0.0043368 | -0.017299 | -0.0043355 | 4.8905e-06 | 1.2934e-06 | 0.026098 | 0.026098 | 0.026098 | 0.98659 | -0.094389 | 0.9863 | -0.096431 | 4.833
88 | -0.019241 | -0.0048223 | 0.019247 | 0.0048233 | 6.0708e-06 | 1.0067e-06 | 0.02902 | 0.029019 | 0.02902 | 0.98659 | -0.094389 | 0.98691 | -0.09211 | 3.5827
89 | 0.014929 | 0.0037416 | -0.014927 | -0.0037409 | 1.8016e-06 | 6.2031e-07 | 0.022523 | 0.022523 | 0.022523 | 0.9863 | -0.096431 | 0.98618 | -0.097302 | 8.3418
90 | -0.023489 | -0.0058864 | 0.023493 | 0.0058875 | 4.3785e-06 | 1.0405e-06 | 0.035415 | 0.035415 | 0.035415 | 0.98691 | -0.09211 | 0.9871 | -0.090763 | 4.3722
91 | 0.011642 | 0.0029176 | -0.011642 | -0.0029175 | 2.9872e-07 | 9.5097e-08 | 0.017566 | 0.017566 | 0.017566 | 0.98618 | -0.097302 | 0.98616 | -0.097488 | 6.5059
92 | 0.0010735 | 0.00026866 | -0.0010735 | -0.00026904 | 5.1051e-08 | -3.7971e-07 | 0.0016182 | 0.0016183 | 0.0016183 | 0.9871 | -0.090763 | 0.98705 | -0.091107 | 0.59937
93 | -0.024567 | -0.0061561 | 0.02457 | 0.0061569 | 2.8811e-06 | 7.2074e-07 | 0.037033 | 0.037033 | 0.037033 | 0.9871 | -0.090763 | 0.98722 | -0.089916 | 4.572
94 | 0.0092238 | 0.0023116 | -0.0092217 | -0.002311 | 2.1104e-06 | 5.8899e-07 | 0.013918 | 0.013918 | 0.013918 | 0.98616 | -0.097488 | 0.98592 | -0.099141 | 5.1548
95 | 0.036112 | 0.009015 | -0.036093 | -0.0090089 | 1.9006e-05 | 6.1269e-06 | 0.054419 | 0.054419 | 0.054419 | 0.98722 | -0.089916 | 0.98669 | -0.093749 | 6.7184
96 | -0.060682 | -0.015172 | 0.060695 | 0.015177 | 1.3184e-05 | 4.7801e-06 | 0.091451 | 0.091451 | 0.091451 | 0.98722 | -0.089916 | 0.98744 | -0.088339 | 11.2903
97 | 0.0077551 | 0.0019434 | -0.0077546 | -0.0019433 | 4.4407e-07 | 1.0455e-07 | 0.011704 | 0.011704 | 0.011704 | 0.98592 | -0.099141 | 0.98586 | -0.099555 | 4.335
98 | 0.035624 | 0.0088912 | -0.035611 | -0.0088869 | 1.3339e-05 | 4.2788e-06 | 0.053711 | 0.053711 | 0.053711 | 0.98669 | -0.093749 | 0.98631 | -0.096477 | 6.631
99 | 0.0070305 | 0.0017615 | -0.0070298 | -0.0017617 | 6.6843e-07 | -2.3119e-07 | 0.010594 | 0.010594 | 0.010594 | 0.98744 | -0.088339 | 0.98735 | -0.089027 | 1.9619
100 | -0.067726 | -0.016938 | 0.067856 | 0.016986 | 0.00013038 | 4.7833e-05 | 0.10205 | 0.10204 | 0.10205 | 0.98744 | -0.088339 | 0.98941 | -0.074401 | 12.5982
101 | -0.0017703 | -0.00044369 | 0.0017703 | 0.00044368 | 1.958e-09 | -4.9295e-09 | 0.0026627 | 0.0026627 | 0.0026627 | 0.98932 | -0.075004 | 0.98932 | -0.074996 | 0.9862
102 | -0.0030148 | -0.00075558 | 0.0030151 | 0.00075543 | 2.4836e-07 | -1.5306e-07 | 0.0045345 | 0.0045344 | 0.0045345 | 0.98932 | -0.074996 | 0.98941 | -0.074401 | 1.6795
103 | 0.0056037 | 0.0014043 | -0.0056036 | -0.0014043 | 5.2529e-08 | 5.1081e-09 | 0.0084452 | 0.0084452 | 0.0084452 | 0.98735 | -0.089027 | 0.98734 | -0.089094 | 3.1278
104 | -0.0010115 | -0.00025243 | 0.0010116 | 0.0002518 | 7.827e-08 | -6.3383e-07 | 0.0015393 | 0.001539 | 0.0015393 | 0.97761 | -0.15918 | 0.97769 | -0.15862 | 0.5701
105 | 0.00079288 | 0.00019763 | -0.00079284 | -0.00019814 | 3.8315e-08 | -5.141e-07 | 0.0012064 | 0.0012066 | 0.0012066 | 0.97761 | -0.15918 | 0.97756 | -0.15954 | 0.4469
106 | -0.0010116 | -0.0002518 | 0.0010116 | 0.00025173 | 8.6655e-09 | -7.0192e-08 | 0.001539 | 0.001539 | 0.001539 | 0.97769 | -0.15862 | 0.9777 | -0.15856 | 0.57001
107 | 0.00040729 | 0.00010185 | -0.00040729 | -0.00010196 | 2.073e-09 | -1.0759e-07 | 0.00061989 | 0.00061992 | 0.00061992 | 0.97756 | -0.15954 | 0.97756 | -0.15957 | 0.2296
108 | 0.00038555 | 9.6293e-05 | -0.00038554 | -9.6626e-05 | 5.7533e-09 | -3.3347e-07 | 0.00058675 | 0.00058687 | 0.00058687 | 0.97756 | -0.15954 | 0.97755 | -0.15964 | 0.21736
109 | 0.019794 | 0.0049323 | -0.019781 | -0.0049297 | 1.3858e-05 | 2.5684e-06 | 0.030116 | 0.030117 | 0.030117 | 0.9777 | -0.15856 | 0.97699 | -0.16367 | 3.7182
110 | -0.020806 | -0.005184 | 0.020824 | 0.0051876 | 1.7613e-05 | 3.5922e-06 | 0.031655 | 0.031654 | 0.031655 | 0.9777 | -0.15856 | 0.97855 | -0.15237 | 3.908
111 | 0.00040729 | 0.00010196 | -0.00040729 | -0.00010208 | 2.2707e-09 | -1.1783e-07 | 0.00061992 | 0.00061997 | 0.00061997 | 0.97756 | -0.15957 | 0.97755 | -0.15961 | 0.22962
112 | 0.00012258 | 3.0021e-05 | -0.00012258 | -3.0163e-05 | 2.4474e-10 | -1.4206e-07 | 0.00018615 | 0.0001862 | 0.0001862 | 0.97855 | -0.15237 | 0.97855 | -0.15239 | 0.068961
113 | 0.00012258 | 3.0163e-05 | -0.00012257 | -3.072e-05 | 9.6112e-10 | -5.5716e-07 | 0.0001862 | 0.00018639 | 0.00018639 | 0.97855 | -0.15239 | 0.97854 | -0.15244 | 0.069035
114 | 0.0050518 | 0.0012659 | -0.0050507 | -0.0012658 | 1.1027e-06 | 5.2858e-08 | 0.0077068 | 0.007707 | 0.007707 | 0.97538 | -0.1725 | 0.97516 | -0.17408 | 2.8544
115 | 0.0058542 | 0.001467 | -0.0058534 | -0.0014669 | 7.6597e-07 | 9.4156e-08 | 0.008836 | 0.008836 | 0.008836 | 0.98586 | -0.099555 | 0.98573 | -0.1005 | 3.2726
116 | 0.0043579 | 0.0010921 | -0.0043576 | -0.0010921 | 2.6421e-07 | -2.3096e-08 | 0.0065784 | 0.0065785 | 0.0065785 | 0.98573 | -0.1005 | 0.98567 | -0.10094 | 2.4365
117 | 0.0034173 | 0.00085632 | -0.0034171 | -0.00085641 | 2.1309e-07 | -8.2685e-08 | 0.0051502 | 0.0051502 | 0.0051502 | 0.98734 | -0.089094 | 0.98727 | -0.089545 | 1.9075
118 | 0.034932 | 0.0087169 | -0.034917 | -0.0087122 | 1.4811e-05 | 4.715e-06 | 0.052688 | 0.052688 | 0.052688 | 0.98631 | -0.096477 | 0.98587 | -0.099567 | 6.5047
119 | 0.001733 | 0.00043264 | -0.001733 | -0.00043318 | 2.0724e-08 | -5.4647e-07 | 0.0026184 | 0.0026186 | 0.0026186 | 0.98462 | -0.10857 | 0.98461 | -0.10866 | 0.32329
120 | -0.034194 | -0.0085282 | 0.034237 | 0.0085416 | 4.2266e-05 | 1.3347e-05 | 0.051662 | 0.051661 | 0.051662 | 0.98462 | -0.10857 | 0.98587 | -0.099567 | 6.378
121 | 0.0011347 | 0.00028325 | -0.0011347 | -0.00028411 | 3.1514e-08 | -8.6175e-07 | 0.0017145 | 0.0017148 | 0.0017148 | 0.98461 | -0.10866 | 0.98458 | -0.10886 | 0.31756
122 | 0.00032062 | 8.0079e-05 | -0.00032062 | -8.0354e-05 | 3.1804e-09 | -2.7489e-07 | 0.00048446 | 0.00048456 | 0.00048456 | 0.98458 | -0.10886 | 0.98457 | -0.10893 | 0.17947

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22727 | 0.057261

## res_load
| p_mw | q_mvar
0 | 0.0024088 | 0.00060371
1 | 0.0014719 | 0.00036889
2 | 0.001986 | 0.00049773
3 | 0.0011594 | 0.00029057
4 | 0.0024887 | 0.00062373
5 | 0.0039635 | 0.00099336
6 | 0.0054915 | 0.0013763
7 | 0.0030707 | 0.00076959
8 | 0.0021556 | 0.00054026
9 | 0.0031051 | 0.00077821
10 | 0.0026164 | 0.00065573
11 | 0.0020358 | 0.00051023
12 | 0.0031188 | 0.00078165
13 | 0.0038793 | 0.00097225
14 | 0.0029787 | 0.00074654
15 | 0.0028799 | 0.00072178
16 | 0.0030868 | 0.00077362
17 | 0.0015632 | 0.00039179
18 | 0.0012435 | 0.00031164
19 | 0.0016254 | 0.00040737
20 | 0.00089107 | 0.00022332
21 | 0.0048837 | 0.001224
22 | 0.0061181 | 0.0015333
23 | 0.0050356 | 0.001262
24 | 0.014408 | 0.0036111
25 | 0.0023275 | 0.00058333
26 | 0.0028157 | 0.00070567
27 | 0.002391 | 0.00059925
28 | 0.0017351 | 0.00043486
29 | 0.0055737 | 0.0013969
30 | 0.0026487 | 0.00066384
31 | 0.0027339 | 0.00068517
32 | 0.004295 | 0.0010764
33 | 0.0061613 | 0.0015442
34 | 0.0048936 | 0.0012265
35 | 0.0027512 | 0.00068952
36 | 0.013827 | 0.0034653
37 | 0.0027223 | 0.00068227
38 | 0.0028115 | 0.00070463
39 | 0.00032866 | 8.2369e-05
40 | 0.00041329 | 0.00010358
41 | 0.00044654 | 0.00011191
42 | 0.00023617 | 5.9189e-05
43 | 0.00032579 | 8.1651e-05
44 | 0.0016884 | 0.00042314
45 | 0.00061029 | 0.00015295
46 | 0.00016659 | 4.1751e-05
47 | 0.00041674 | 0.00010445
48 | 0.00045173 | 0.00011321
49 | 0.0054204 | 0.0013585
50 | 0.0014958 | 0.0003749
51 | 0.00013928 | 3.4907e-05
52 | 0.0020164 | 0.00050535
53 | 0.00032614 | 8.1739e-05
54 | 0.0039579 | 0.00099195
55 | 0.00066795 | 0.0001674
56 | 0.0012521 | 0.0003138
57 | 0.0022775 | 0.00057079
58 | 0.00058647 | 0.00014698
59 | 0.0040904 | 0.0010252
60 | 0.0019371 | 0.00048548
61 | 0.00237 | 0.00059398
62 | 0.0042419 | 0.0010631
63 | 0.0032851 | 0.00082332
64 | 0.0024178 | 0.00060596
65 | 0.0010735 | 0.00026904
66 | 0.0014666 | 0.00036757
67 | 0.00046952 | 0.00011767
68 | 0.0017703 | 0.00044369
69 | 0.0012445 | 0.0003119
70 | 0.0014261 | 0.00035743
71 | 0.00021866 | 5.4802e-05
72 | 0.00038554 | 9.6626e-05
73 | 0.00022201 | 5.564e-05
74 | 0.00040729 | 0.00010208
75 | 0.0081205 | 0.0020352
76 | 0.0019004 | 0.00047629
77 | 0.0014956 | 0.00037482
78 | 0.0043576 | 0.0010921
79 | 0.00011399 | 2.857e-05
80 | 0.0021863 | 0.00054794
81 | 0.00012257 | 3.072e-05
82 | 0.0034171 | 0.00085641
83 | 0.0050507 | 0.0012658
84 | 0.00067836 | 0.00017001
85 | 0.00033024 | 8.2765e-05
86 | 0.00068079 | 0.00017062
87 | 0.00059825 | 0.00014994
88 | 0.00081408 | 0.00020403
89 | 0.00032062 | 8.0354e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1