## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1401-11_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1401-11_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1401-11_0_1_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1401-11_0_1_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1401-11_0_1_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1401-11_0_1_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1401-11_0_1_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1401-11_0_1_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1401-11_0_1_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1401-11_0_1_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1401-11_0_1_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_1401-11_0_1_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1401-11_0_1_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1401-11_0_1_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1401-11_0_1_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1401-11_0_1_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1401-11_0_1_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_1401-11_0_1_node_85 | 0.4 | n |  | TRUE
18 | bus_LV_1401-11_0_1_node_83 | 0.4 | n |  | TRUE
19 | bus_LV_1401-11_0_1_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1401-11_0_1_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1401-11_0_1_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_1401-11_0_1_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1401-11_0_1_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1401-11_0_1_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1401-11_0_1_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1401-11_0_1_node_93 | 0.4 | n |  | TRUE
27 | bus_LV_1401-11_0_1_node_91 | 0.4 | n |  | TRUE
28 | bus_LV_1401-11_0_1_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1401-11_0_1_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1401-11_0_1_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1401-11_0_1_node_84 | 0.4 | n |  | TRUE
32 | bus_MV_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1401-11_0_1_load_0 | 0 | 0.00019971 | 5.0051e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1401-11_0_1_load_2 | 2 | 0.00074996 | 0.00018796 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1401-11_0_1_load_3 | 3 | 0.0016138 | 0.00040446 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1401-11_0_1_load_9 | 6 | 0.0031497 | 0.00078939 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1401-11_0_1_load_7 | 7 | 0.00091842 | 0.00023018 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1401-11_0_1_load_26 | 10 | 0.00016437 | 4.1194e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1401-11_0_1_load_12 | 12 | 0.0019029 | 0.00047692 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1401-11_0_1_load_21 | 16 | 0.00079164 | 0.0001984 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1401-11_0_1_load_85 | 17 | 0.00063766 | 0.00015981 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1401-11_0_1_load_83 | 18 | 0.00063032 | 0.00015797 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1401-11_0_1_load_13 | 19 | 0.032123 | 0.0080507 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1401-11_0_1_load_14 | 20 | 0.0030289 | 0.00075912 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1401-11_0_1_load_25 | 21 | 0.00013722 | 3.439e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1401-11_0_1_load_16 | 22 | 0.0046516 | 0.0011658 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1401-11_0_1_load_17 | 23 | 0.0063148 | 0.0015826 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1401-11_0_1_load_93 | 26 | 0.0038455 | 0.00096378 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1401-11_0_1_load_91 | 27 | 0.0064979 | 0.0016285 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1401-11_0_1_load_24 | 30 | 0.0011784 | 0.00029535 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1401-11_0_1_load_84 | 31 | 0.00021117 | 5.2924e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1401-11_0_1_line_0 | NAYY 4x150 SE | 0 | 1 | 0.014746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1401-11_0_1_line_1 | NAYY 4x150 SE | 0 | 2 | 0.026223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1401-11_0_1_line_2 | NAYY 4x150 SE | 1 | 3 | 0.054976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1401-11_0_1_line_3 | NAYY 4x150 SE | 1 | 4 | 0.042303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1401-11_0_1_line_4 | NAYY 4x150 SE | 3 | 5 | 0.039932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1401-11_0_1_line_5 | NAYY 4x150 SE | 4 | 6 | 0.018846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1401-11_0_1_line_6 | NAYY 4x150 SE | 4 | 7 | 0.044458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1401-11_0_1_line_7 | NAYY 4x150 SE | 5 | 20 | 0.018541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1401-11_0_1_line_8 | NAYY 4x150 SE | 5 | 23 | 0.012808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1401-11_0_1_line_9 | NAYY 4x150 SE | 7 | 13 | 0.081606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1401-11_0_1_line_10 | NAYY 4x150 SE | 8 | 9 | 0.006351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1401-11_0_1_line_11 | NAYY 4x150 SE | 8 | 10 | 0.034796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1401-11_0_1_line_12 | NAYY 4x150 SE | 9 | 21 | 0.04477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1401-11_0_1_line_13 | NAYY 4x150 SE | 9 | 11 | 0.057443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1401-11_0_1_line_14 | NAYY 4x150 SE | 10 | 29 | 0.01834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1401-11_0_1_line_15 | NAYY 4x150 SE | 11 | 12 | 0.0095415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1401-11_0_1_line_16 | NAYY 4x150 SE | 13 | 14 | 0.064374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1401-11_0_1_line_17 | NAYY 4x150 SE | 13 | 15 | 0.1288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1401-11_0_1_line_18 | NAYY 4x150 SE | 14 | 16 | 0.04627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1401-11_0_1_line_19 | NAYY 4x150 SE | 15 | 17 | 0.011551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1401-11_0_1_line_20 | NAYY 4x150 SE | 15 | 18 | 0.022415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1401-11_0_1_line_21 | NAYY 4x150 SE | 16 | 28 | 0.035132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1401-11_0_1_line_22 | NAYY 4x150 SE | 18 | 31 | 0.011429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1401-11_0_1_line_23 | NAYY 4x150 SE | 19 | 20 | 0.027188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1401-11_0_1_line_24 | NAYY 4x150 SE | 21 | 30 | 0.016096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1401-11_0_1_line_25 | NAYY 4x150 SE | 22 | 23 | 0.063117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1401-11_0_1_line_26 | NAYY 4x150 SE | 22 | 24 | 0.026608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1401-11_0_1_line_27 | NAYY 4x150 SE | 24 | 25 | 0.16721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1401-11_0_1_line_28 | NAYY 4x150 SE | 25 | 26 | 0.023366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1401-11_0_1_line_29 | NAYY 4x150 SE | 25 | 27 | 0.028559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1401-11_0_1_line_30 | NAYY 4x150 SE | 28 | 29 | 0.014689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1401-11_0_1_trafo_13 | 0.25 MVA 20/0.4 kV | 32 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2663982.6506 | 1199469.6892 | 2663968.0972 | 1199472.0665
1 | 2663942.2173 | 1199476.2939 | 2663968.0972 | 1199472.0665
2 | 2663982.6506 | 1199469.6892 | 2663978.5868 | 1199448.1441 | 2663970.3686 | 1199420.6398 | 2663969.2133 | 1199416.4507
3 | 2663982.6506 | 1199469.6892 | 2663984.9565 | 1199489.7035 | 2663987.2206 | 1199496.5651 | 2663996.5986 | 1199508.1835
4 | 2663958.597 | 1199377.9553 | 2663969.2133 | 1199416.4507
5 | 2663996.5986 | 1199508.1835 | 2663979.8008 | 1199516.8199
6 | 2663996.5986 | 1199508.1835 | 2664024.5084 | 1199542.7898
7 | 2663958.597 | 1199377.9553 | 2663976.4754 | 1199373.0419
8 | 2663958.597 | 1199377.9553 | 2663954.8143 | 1199365.7187
9 | 2664075.7381 | 1199606.3114 | 2664024.5084 | 1199542.7898
10 | 2664108.162 | 1199459.7721 | 2664108.0854 | 1199453.4231
11 | 2664108.162 | 1199459.7721 | 2664120.6164 | 1199482.697 | 2664126.1003 | 1199489.459
12 | 2664108.0854 | 1199453.4231 | 2664117.0481 | 1199441.9902 | 2664130.14 | 1199431.0574 | 2664134.2995 | 1199431.569 | 2664138.3777 | 1199439.5869
13 | 2664065.393 | 1199415.7543 | 2664079.0446 | 1199422.9271 | 2664108.0854 | 1199453.4231
14 | 2664137.6522 | 1199503.7033 | 2664126.1003 | 1199489.459
15 | 2664065.393 | 1199415.7543 | 2664061.1136 | 1199407.2263
16 | 2664138.357 | 1199591.9743 | 2664132.4673 | 1199593.7788 | 2664116.2 | 1199599.8079 | 2664095.8552 | 1199601.9578 | 2664075.7381 | 1199606.3114
17 | 2664067.956 | 1199719.9954 | 2664079.3866 | 1199713.3917 | 2664094.6904 | 1199695.6453 | 2664096.467 | 1199682.6344 | 2664075.7381 | 1199606.3114
18 | 2664138.357 | 1199591.9743 | 2664134.2234 | 1199575.5869 | 2664133.4891 | 1199555.3225 | 2664134.686 | 1199546.3096
19 | 2664067.956 | 1199719.9954 | 2664056.4088 | 1199719.7159
20 | 2664067.956 | 1199719.9954 | 2664083.242 | 1199725.2067 | 2664088.7483 | 1199728.1959
21 | 2664147.6325 | 1199514.5056 | 2664136.5954 | 1199531.9309 | 2664134.686 | 1199546.3096
22 | 2664088.7483 | 1199728.1959 | 2664098.7931 | 1199733.6486
23 | 2664002.6919 | 1199365.8371 | 2663976.4754 | 1199373.0419
24 | 2664138.3777 | 1199439.5869 | 2664140.0935 | 1199442.9601 | 2664145.5809 | 1199453.9815
25 | 2663951.0503 | 1199302.9095 | 2663950.8878 | 1199332.0457 | 2663951.9014 | 1199349.0332 | 2663952.7073 | 1199356.2684 | 2663954.8143 | 1199365.7187
26 | 2663953.8652 | 1199276.5224 | 2663952.482 | 1199283.4006 | 2663951.095 | 1199294.8926 | 2663951.0503 | 1199302.9095
27 | 2663953.8652 | 1199276.5224 | 2663983.4034 | 1199283.4536 | 2664014.4623 | 1199286.31 | 2664039.7535 | 1199286.6699 | 2664065.5742 | 1199284.5007 | 2664110.5232 | 1199282.2589 | 2664119.9714 | 1199281.6599
28 | 2664119.9714 | 1199281.6599 | 2664121.6656 | 1199285.5693 | 2664129.2669 | 1199303.1056
29 | 2664119.9714 | 1199281.6599 | 2664148.4629 | 1199279.6937
30 | 2664147.6325 | 1199514.5056 | 2664137.6522 | 1199503.7033

## bus_geodata
| x | y | coords
0 | 2663968.0972 | 1199472.0665
1 | 2663982.6506 | 1199469.6892
2 | 2663942.2173 | 1199476.2939
3 | 2663969.2133 | 1199416.4507
4 | 2663996.5986 | 1199508.1835
5 | 2663958.597 | 1199377.9553
6 | 2663979.8008 | 1199516.8199
7 | 2664024.5084 | 1199542.7898
8 | 2664108.162 | 1199459.7721
9 | 2664108.0854 | 1199453.4231
10 | 2664126.1003 | 1199489.459
11 | 2664065.393 | 1199415.7543
12 | 2664061.1136 | 1199407.2263
13 | 2664075.7381 | 1199606.3114
14 | 2664138.357 | 1199591.9743
15 | 2664067.956 | 1199719.9954
16 | 2664134.686 | 1199546.3096
17 | 2664056.4088 | 1199719.7159
18 | 2664088.7483 | 1199728.1959
19 | 2664002.6919 | 1199365.8371
20 | 2663976.4754 | 1199373.0419
21 | 2664138.3777 | 1199439.5869
22 | 2663951.0503 | 1199302.9095
23 | 2663954.8143 | 1199365.7187
24 | 2663953.8652 | 1199276.5224
25 | 2664119.9714 | 1199281.6599
26 | 2664129.2669 | 1199303.1056
27 | 2664148.4629 | 1199279.6937
28 | 2664147.6325 | 1199514.5056
29 | 2664137.6522 | 1199503.7033
30 | 2664145.5809 | 1199453.9815
31 | 2664098.7931 | 1199733.6486
32 | 2664002.6919 | 1199365.8371

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99612 | -0.027278 | 0.00019971 | 5.0051e-05
1 | 0.99614 | -0.027137 | 0 | 0
2 | 0.99609 | -0.027476 | 0.00074996 | 0.00018796
3 | 0.99698 | -0.021199 | 0.0016138 | 0.00040446
4 | 0.99555 | -0.031304 | 0 | 0
5 | 0.99768 | -0.016245 | 0 | 0
6 | 0.99546 | -0.031902 | 0.0031497 | 0.00078939
7 | 0.99513 | -0.034275 | 0.00091842 | 0.00023018
8 | 0.99331 | -0.04715 | 0 | 0
9 | 0.99328 | -0.047358 | 0 | 0
10 | 0.99347 | -0.046013 | 0.00016437 | 4.1194e-05
11 | 0.99313 | -0.048466 | 0 | 0
12 | 0.9931 | -0.04865 | 0.0019029 | 0.00047692
13 | 0.99447 | -0.038972 | 0 | 0
14 | 0.99408 | -0.041705 | 0 | 0
15 | 0.9942 | -0.040909 | 0 | 0
16 | 0.99381 | -0.043668 | 0.00079164 | 0.0001984
17 | 0.99418 | -0.040984 | 0.00063766 | 0.00015981
18 | 0.99417 | -0.0411 | 0.00063032 | 0.00015797
19 | 1 | 0 | -0.037598 | -0.0092301
20 | 0.99857 | -0.0099837 | 0.0030289 | 0.00075912
21 | 0.9932 | -0.047956 | 0.00013722 | 3.439e-05
22 | 0.99593 | -0.028514 | 0.0046516 | 0.0011658
23 | 0.99729 | -0.018987 | 0.0063148 | 0.0015826
24 | 0.99554 | -0.03129 | 0 | 0
25 | 0.99306 | -0.048772 | 0 | 0
26 | 0.99293 | -0.049681 | 0.0038455 | 0.00096378
27 | 0.99279 | -0.050651 | 0.0064979 | 0.0016285
28 | 0.99364 | -0.044877 | 0 | 0
29 | 0.99356 | -0.045382 | 0 | 0
30 | 0.99317 | -0.048148 | 0.0011784 | 0.00029535
31 | 0.99416 | -0.041125 | 0.00021117 | 5.2924e-05
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00094969 | -0.00023768 | 0.00094971 | 0.00023749 | 1.8515e-08 | -1.8484e-07 | 0.0014185 | 0.0014185 | 0.0014185 | 0.99612 | -0.027278 | 0.99614 | -0.027137 | 0.52538
1 | 0.00074998 | 0.00018762 | -0.00074996 | -0.00018796 | 2.0536e-08 | -3.3345e-07 | 0.0011202 | 0.0011203 | 0.0011203 | 0.99612 | -0.027278 | 0.99609 | -0.027476 | 0.41494
2 | -0.010689 | -0.0026715 | 0.010698 | 0.0026742 | 8.7431e-06 | 2.6464e-06 | 0.015965 | 0.015964 | 0.015965 | 0.99614 | -0.027137 | 0.99698 | -0.021199 | 5.9128
3 | 0.0097393 | 0.002434 | -0.0097337 | -0.0024325 | 5.5854e-06 | 1.5978e-06 | 0.014546 | 0.014546 | 0.014546 | 0.99614 | -0.027137 | 0.99555 | -0.031304 | 5.3875
4 | -0.012312 | -0.0030786 | 0.01232 | 0.0030814 | 8.4113e-06 | 2.714e-06 | 0.018373 | 0.018373 | 0.018373 | 0.99698 | -0.021199 | 0.99768 | -0.016245 | 6.8048
5 | 0.00315 | 0.00078924 | -0.0031497 | -0.00078939 | 2.6067e-07 | -1.4477e-07 | 0.0047081 | 0.0047082 | 0.0047082 | 0.99555 | -0.031304 | 0.99546 | -0.031902 | 1.7438
6 | 0.0065838 | 0.0016432 | -0.0065811 | -0.0016428 | 2.6852e-06 | 4.5493e-07 | 0.0098382 | 0.0098384 | 0.0098384 | 0.99555 | -0.031304 | 0.99513 | -0.034275 | 3.6438
7 | -0.033689 | -0.0084407 | 0.033718 | 0.0084517 | 2.9209e-05 | 1.0992e-05 | 0.050245 | 0.050245 | 0.050245 | 0.99768 | -0.016245 | 0.99857 | -0.0099837 | 18.6094
8 | 0.021369 | 0.0053593 | -0.021361 | -0.0053564 | 8.119e-06 | 2.9555e-06 | 0.031873 | 0.031873 | 0.031873 | 0.99768 | -0.016245 | 0.99729 | -0.018987 | 11.8047
9 | 0.0056627 | 0.0014126 | -0.005659 | -0.0014122 | 3.6491e-06 | 3.4399e-07 | 0.0084651 | 0.0084654 | 0.0084654 | 0.99513 | -0.034275 | 0.99447 | -0.038972 | 3.1353
10 | 0.0032191 | 0.00080513 | -0.0032191 | -0.00080518 | 9.214e-08 | -4.6769e-08 | 0.0048218 | 0.0048218 | 0.0048218 | 0.99331 | -0.04715 | 0.99328 | -0.047358 | 1.7859
11 | -0.0032191 | -0.00080513 | 0.0032197 | 0.00080488 | 5.0479e-07 | -2.5633e-07 | 0.0048218 | 0.0048216 | 0.0048218 | 0.99331 | -0.04715 | 0.99347 | -0.046013 | 1.7859
12 | 0.0013158 | 0.000329 | -0.0013157 | -0.00032954 | 1.0853e-07 | -5.377e-07 | 0.0019709 | 0.0019711 | 0.0019711 | 0.99328 | -0.047358 | 0.9932 | -0.047956 | 0.73004
13 | 0.0019033 | 0.00047618 | -0.001903 | -0.00047681 | 2.9136e-07 | -6.3134e-07 | 0.0028509 | 0.0028512 | 0.0028512 | 0.99328 | -0.047358 | 0.99313 | -0.048466 | 1.056
14 | -0.003384 | -0.00084607 | 0.0033843 | 0.00084595 | 2.9391e-07 | -1.2445e-07 | 0.0050678 | 0.0050677 | 0.0050678 | 0.99347 | -0.046013 | 0.99356 | -0.045382 | 1.877
15 | 0.001903 | 0.00047681 | -0.0019029 | -0.00047691 | 4.8402e-08 | -1.0484e-07 | 0.0028512 | 0.0028512 | 0.0028512 | 0.99313 | -0.048466 | 0.9931 | -0.04865 | 1.056
16 | 0.0041795 | 0.0010436 | -0.0041779 | -0.0010438 | 1.5704e-06 | -2.3092e-07 | 0.0062523 | 0.0062526 | 0.0062526 | 0.99447 | -0.038972 | 0.99408 | -0.041705 | 2.3158
17 | 0.0014796 | 0.00036861 | -0.0014792 | -0.00037013 | 3.9375e-07 | -1.5192e-06 | 0.0022131 | 0.0022137 | 0.0022137 | 0.99447 | -0.038972 | 0.9942 | -0.040909 | 0.81988
18 | 0.0041779 | 0.0010438 | -0.0041768 | -0.001044 | 1.1288e-06 | -1.6554e-07 | 0.0062526 | 0.0062528 | 0.0062528 | 0.99408 | -0.041705 | 0.99381 | -0.043668 | 2.3159
19 | 0.00063767 | 0.00015966 | -0.00063766 | -0.00015981 | 6.5648e-09 | -1.4725e-07 | 0.00095434 | 0.0009544 | 0.0009544 | 0.9942 | -0.040909 | 0.99418 | -0.040984 | 0.35348
20 | 0.00084151 | 0.00021047 | -0.00084149 | -0.00021075 | 2.2185e-08 | -2.8213e-07 | 0.0012593 | 0.0012594 | 0.0012594 | 0.9942 | -0.040909 | 0.99417 | -0.0411 | 0.46646
21 | 0.0033851 | 0.00084561 | -0.0033845 | -0.00084585 | 5.6297e-07 | -2.386e-07 | 0.0050675 | 0.0050677 | 0.0050677 | 0.99381 | -0.043668 | 0.99364 | -0.044877 | 1.8769
22 | 0.00021117 | 5.2776e-05 | -0.00021117 | -5.2924e-05 | 7.1234e-10 | -1.4793e-07 | 0.00031601 | 0.00031607 | 0.00031607 | 0.99417 | -0.0411 | 0.99416 | -0.041125 | 0.11706
23 | 0.036798 | 0.00923 | -0.036747 | -0.0092108 | 5.0872e-05 | 1.921e-05 | 0.054759 | 0.054759 | 0.054759 | 1 | 0 | 0.99857 | -0.0099837 | 20.281
24 | 0.0011785 | 0.00029515 | -0.0011784 | -0.00029535 | 3.131e-08 | -1.9626e-07 | 0.0017655 | 0.0017656 | 0.0017656 | 0.9932 | -0.047956 | 0.99317 | -0.048148 | 0.65392
25 | -0.015026 | -0.0037669 | 0.015046 | 0.0037737 | 1.9851e-05 | 6.8127e-06 | 0.022451 | 0.022451 | 0.022451 | 0.99593 | -0.028514 | 0.99729 | -0.018987 | 8.3151
26 | 0.010375 | 0.0026011 | -0.010371 | -0.0025999 | 3.9896e-06 | 1.1883e-06 | 0.015501 | 0.015501 | 0.015501 | 0.99593 | -0.028514 | 0.99554 | -0.03129 | 5.7411
27 | 0.010371 | 0.0025999 | -0.010346 | -0.0025925 | 2.5072e-05 | 7.4743e-06 | 0.015501 | 0.015502 | 0.015502 | 0.99554 | -0.03129 | 0.99306 | -0.048772 | 5.7414
28 | 0.003846 | 0.00096366 | -0.0038455 | -0.00096378 | 4.8423e-07 | -1.1602e-07 | 0.0057629 | 0.005763 | 0.005763 | 0.99306 | -0.048772 | 0.99293 | -0.049681 | 2.1344
29 | 0.0064995 | 0.0016288 | -0.0064979 | -0.0016285 | 1.6903e-06 | 2.8073e-07 | 0.009739 | 0.0097391 | 0.0097391 | 0.99306 | -0.048772 | 0.99279 | -0.050651 | 3.6071
30 | 0.0033845 | 0.00084585 | -0.0033843 | -0.00084595 | 2.354e-07 | -9.9713e-08 | 0.0050677 | 0.0050677 | 0.0050677 | 0.99364 | -0.044877 | 0.99356 | -0.045382 | 1.8769

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.069721 | 0.017281

## res_load
| p_mw | q_mvar
0 | 0.00019971 | 5.0051e-05
1 | 0.00074996 | 0.00018796
2 | 0.0016138 | 0.00040446
3 | 0.0031497 | 0.00078939
4 | 0.00091842 | 0.00023018
5 | 0.00016437 | 4.1194e-05
6 | 0.0019029 | 0.00047692
7 | 0.00079164 | 0.0001984
8 | 0.00063766 | 0.00015981
9 | 0.00063032 | 0.00015797
10 | 0.032123 | 0.0080507
11 | 0.0030289 | 0.00075912
12 | 0.00013722 | 3.439e-05
13 | 0.0046516 | 0.0011658
14 | 0.0063148 | 0.0015826
15 | 0.0038455 | 0.00096378
16 | 0.0064979 | 0.0016285
17 | 0.0011784 | 0.00029535
18 | 0.00021117 | 5.2924e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1