## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1401-28_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1401-28_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1401-28_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1401-28_0_3_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_1401-28_0_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1401-28_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1401-28_0_3_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1401-28_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1401-28_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1401-28_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1401-28_0_3_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_1401-28_0_3_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_1401-28_0_3_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1401-28_0_3_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_1401-28_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1401-28_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1401-28_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1401-28_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1401-28_0_3_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1401-28_0_3_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_1401-28_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1401-28_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1401-28_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1401-28_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1401-28_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1401-28_0_3_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1401-28_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1401-28_0_3_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1401-28_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1401-28_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1401-28_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1401-28_0_3_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_1401-28_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1401-28_0_3_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_1401-28_0_3_node_31 | 0.4 | n |  | TRUE
35 | bus_MV_136_0_node_251 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1401-28_0_3_load_0 | 0 | 0.022249 | 0.0055761 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1401-28_0_3_load_1 | 1 | 0.025619 | 0.0064206 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1401-28_0_3_load_2 | 2 | 0.0016011 | 0.00040128 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1401-28_0_3_load_7 | 4 | 0.0045092 | 0.0011301 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1401-28_0_3_load_9 | 5 | 0.0032601 | 0.00081706 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1401-28_0_3_load_3 | 6 | 0.021806 | 0.0054652 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1401-28_0_3_load_4 | 7 | 0.0056783 | 0.0014231 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1401-28_0_3_load_5 | 8 | 0.0048182 | 0.0012075 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1401-28_0_3_load_6 | 9 | 0.0040093 | 0.0010048 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1401-28_0_3_load_29 | 10 | 0.0053867 | 0.00135 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1401-28_0_3_load_34 | 11 | 0.0036118 | 0.0009052 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1401-28_0_3_load_28 | 12 | 0.0030253 | 0.00075821 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1401-28_0_3_load_32 | 13 | 0.0039103 | 0.00098 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1401-28_0_3_load_11 | 15 | 0.0027898 | 0.00069919 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1401-28_0_3_load_12 | 16 | 0.0076384 | 0.0019144 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1401-28_0_3_load_13 | 17 | 0.0069219 | 0.0017348 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1401-28_0_3_load_19 | 18 | 0.0027101 | 0.00067923 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1401-28_0_3_load_14 | 20 | 0.0038873 | 0.00097424 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1401-28_0_3_load_15 | 21 | 0.0026736 | 0.00067006 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1401-28_0_3_load_16 | 22 | 0.0046943 | 0.0011765 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1401-28_0_3_load_18 | 24 | 0.0067317 | 0.0016871 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1401-28_0_3_load_22 | 25 | 0.0037329 | 0.00093555 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1401-28_0_3_load_26 | 26 | 0.0037319 | 0.00093531 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1401-28_0_3_load_21 | 27 | 0.037649 | 0.0094356 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1401-28_0_3_load_24 | 28 | 0.0040084 | 0.0010046 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1401-28_0_3_load_23 | 29 | 0.0043402 | 0.0010878 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1401-28_0_3_load_25 | 30 | 0.0027271 | 0.00068349 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1401-28_0_3_load_36 | 31 | 0.0020959 | 0.00052529 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1401-28_0_3_load_27 | 32 | 0.005183 | 0.001299 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1401-28_0_3_load_30 | 33 | 0.0040613 | 0.0010179 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1401-28_0_3_load_31 | 34 | 0.0037092 | 0.0009296 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1401-28_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.039688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1401-28_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0036301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1401-28_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.087006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1401-28_0_3_line_3 | NAYY 4x150 SE | 3 | 5 | 0.032884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1401-28_0_3_line_4 | NAYY 4x150 SE | 3 | 4 | 0.010211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1401-28_0_3_line_5 | NAYY 4x150 SE | 5 | 14 | 0.074154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1401-28_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.02401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1401-28_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.020326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1401-28_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0022165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1401-28_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.020353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1401-28_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.048774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1401-28_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.0081935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1401-28_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.0060624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1401-28_0_3_line_13 | NAYY 4x150 SE | 12 | 32 | 0.012822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1401-28_0_3_line_14 | NAYY 4x150 SE | 13 | 33 | 0.0063642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1401-28_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.027921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1401-28_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.0013654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1401-28_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.025609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1401-28_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.014667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1401-28_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.018602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1401-28_0_3_line_20 | NAYY 4x150 SE | 19 | 25 | 0.021151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1401-28_0_3_line_21 | NAYY 4x150 SE | 20 | 21 | 0.014277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1401-28_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.007479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1401-28_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.020156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1401-28_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.015923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1401-28_0_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.012376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1401-28_0_3_line_26 | NAYY 4x150 SE | 23 | 26 | 0.016851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1401-28_0_3_line_27 | NAYY 4x150 SE | 24 | 27 | 0.020573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1401-28_0_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.0073147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_1401-28_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.0063759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1401-28_0_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.013468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1401-28_0_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.035214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1401-28_0_3_line_32 | NAYY 4x150 SE | 30 | 32 | 0.0084132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1401-28_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.007256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1401-28_0_3_trafo_5 | 0.25 MVA 20/0.4 kV | 35 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2663199.7745 | 1198737.9743 | 2663193.2349 | 1198698.8293
1 | 2663199.7745 | 1198737.9743 | 2663200.3727 | 1198741.5547
2 | 2663193.2349 | 1198698.8293 | 2663279.9008 | 1198691.14
3 | 2663279.9008 | 1198691.14 | 2663276.3279 | 1198668.978 | 2663274.0486 | 1198658.7936
4 | 2663279.9008 | 1198691.14 | 2663281.6635 | 1198701.1978
5 | 2663258.4621 | 1198586.2958 | 2663274.0486 | 1198658.7936
6 | 2663132.7567 | 1198683.5478 | 2663127.9151 | 1198684.2296 | 2663124.4317 | 1198683.8259 | 2663122.6121 | 1198682.3392 | 2663121.728 | 1198679.5282 | 2663122.3342 | 1198669.2288
7 | 2663152.8842 | 1198680.7134 | 2663132.7567 | 1198683.5478
8 | 2663122.4645 | 1198667.0161 | 2663122.3342 | 1198669.2288
9 | 2663123.6604 | 1198646.698 | 2663122.4645 | 1198667.0161
10 | 2663122.4645 | 1198667.0161 | 2663075.4424 | 1198654.0612
11 | 2663123.6604 | 1198646.698 | 2663124.1419 | 1198638.5187
12 | 2663070.1415 | 1198651.1197 | 2663075.4424 | 1198654.0612
13 | 2663124.8953 | 1198625.7193 | 2663124.1419 | 1198638.5187
14 | 2663064.5767 | 1198648.0317 | 2663070.1415 | 1198651.1197
15 | 2663258.4621 | 1198586.2958 | 2663230.9291 | 1198590.9338
16 | 2663230.9291 | 1198590.9338 | 2663229.5827 | 1198591.1606
17 | 2663204.5694 | 1198589.9649 | 2663214.3831 | 1198592.9558 | 2663218.9676 | 1198592.9487 | 2663229.5827 | 1198591.1606
18 | 2663204.5694 | 1198589.9649 | 2663203.8395 | 1198589.7425 | 2663191.3418 | 1198583.6495
19 | 2663173.8346 | 1198584.0555 | 2663176.9721 | 1198581.8984 | 2663182.5376 | 1198581.2902 | 2663188.6417 | 1198582.3331 | 2663191.3418 | 1198583.6495
20 | 2663173.8346 | 1198584.0555 | 2663170.4978 | 1198587.0664 | 2663161.2418 | 1198600.9143
21 | 2663156.0147 | 1198627.315 | 2663169.5243 | 1198631.9324
22 | 2663176.6013 | 1198634.3513 | 2663169.5243 | 1198631.9324
23 | 2663153.3231 | 1198610.3432 | 2663151.0736 | 1198614.9555 | 2663150.1629 | 1198620.4269 | 2663151.3457 | 1198623.7969 | 2663153.1006 | 1198625.6388 | 2663156.0147 | 1198627.315 | 2663156.0147 | 1198627.315
24 | 2663190.8318 | 1198640.9686 | 2663188.8956 | 1198638.9914 | 2663185.2505 | 1198637.3075 | 2663176.6013 | 1198634.3513
25 | 2663153.3231 | 1198610.3432 | 2663158.079 | 1198605.6462 | 2663161.2418 | 1198600.9143
26 | 2663153.3231 | 1198610.3432 | 2663138.8076 | 1198601.7849
27 | 2663195.0216 | 1198660.9913 | 2663192.6231 | 1198645.1233 | 2663190.8318 | 1198640.9686
28 | 2663131.6717 | 1198600.3754 | 2663131.6717 | 1198600.3754 | 2663134.3583 | 1198600.5261 | 2663138.8076 | 1198601.7849
29 | 2663126.8031 | 1198603.97 | 2663126.9968 | 1198603.1833 | 2663128.728 | 1198601.5005 | 2663131.6717 | 1198600.3754
30 | 2663126.8031 | 1198603.97 | 2663125.9784 | 1198607.3194 | 2663125.3897 | 1198617.3206
31 | 2663126.8031 | 1198603.97 | 2663092.4115 | 1198596.4032
32 | 2663125.3897 | 1198617.3206 | 2663124.8953 | 1198625.7193
33 | 2663064.5767 | 1198648.0317 | 2663062.1208 | 1198646.6689 | 2663057.98 | 1198645.0465 | 2663057.98 | 1198645.0465

## bus_geodata
| x | y | coords
0 | 2663199.7745 | 1198737.9743
1 | 2663193.2349 | 1198698.8293
2 | 2663200.3727 | 1198741.5547
3 | 2663279.9008 | 1198691.14
4 | 2663281.6635 | 1198701.1978
5 | 2663274.0486 | 1198658.7936
6 | 2663132.7567 | 1198683.5478
7 | 2663122.3342 | 1198669.2288
8 | 2663152.8842 | 1198680.7134
9 | 2663122.4645 | 1198667.0161
10 | 2663123.6604 | 1198646.698
11 | 2663075.4424 | 1198654.0612
12 | 2663124.1419 | 1198638.5187
13 | 2663070.1415 | 1198651.1197
14 | 2663258.4621 | 1198586.2958
15 | 2663230.9291 | 1198590.9338
16 | 2663229.5827 | 1198591.1606
17 | 2663204.5694 | 1198589.9649
18 | 2663191.3418 | 1198583.6495
19 | 2663173.8346 | 1198584.0555
20 | 2663169.5243 | 1198631.9324
21 | 2663156.0147 | 1198627.315
22 | 2663176.6013 | 1198634.3513
23 | 2663153.3231 | 1198610.3432
24 | 2663190.8318 | 1198640.9686
25 | 2663161.2418 | 1198600.9143
26 | 2663138.8076 | 1198601.7849
27 | 2663195.0216 | 1198660.9913
28 | 2663131.6717 | 1198600.3754
29 | 2663126.8031 | 1198603.97
30 | 2663125.3897 | 1198617.3206
31 | 2663092.4115 | 1198596.4032
32 | 2663124.8953 | 1198625.7193
33 | 2663064.5767 | 1198648.0317
34 | 2663057.98 | 1198645.0465
35 | 2663153.3231 | 1198610.3432

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97093 | -0.20476 | 0.022249 | 0.0055761
1 | 0.97232 | -0.19475 | 0.025619 | 0.0064206
2 | 0.97092 | -0.20482 | 0.0016011 | 0.00040128
3 | 0.97863 | -0.1496 | 0 | 0
4 | 0.97856 | -0.15008 | 0.0045092 | 0.0011301
5 | 0.98123 | -0.13115 | 0.0032601 | 0.00081706
6 | 0.9979 | -0.014506 | 0.021806 | 0.0054652
7 | 0.99567 | -0.029962 | 0.0056783 | 0.0014231
8 | 1 | 0 | -0.21794 | -0.054832
9 | 0.99547 | -0.03135 | 0.0040093 | 0.0010048
10 | 0.99383 | -0.042798 | 0.0053867 | 0.00135
11 | 0.9944 | -0.038872 | 0.0036118 | 0.0009052
12 | 0.99318 | -0.047268 | 0.0030253 | 0.00075821
13 | 0.9943 | -0.039587 | 0.0039103 | 0.00098
14 | 0.98434 | -0.10921 | 0 | 0
15 | 0.98512 | -0.10373 | 0.0027898 | 0.00069919
16 | 0.98516 | -0.10344 | 0.0076384 | 0.0019144
17 | 0.98601 | -0.097506 | 0.0069219 | 0.0017348
18 | 0.98654 | -0.093762 | 0.0027101 | 0.00067923
19 | 0.98724 | -0.088847 | 0 | 0
20 | 0.98581 | -0.099079 | 0.0038873 | 0.00097424
21 | 0.9869 | -0.091322 | 0.0026736 | 0.00067006
22 | 0.98527 | -0.10285 | 0.0046943 | 0.0011765
23 | 0.98853 | -0.079848 | 0 | 0
24 | 0.98425 | -0.11012 | 0.0067317 | 0.0016871
25 | 0.98804 | -0.083267 | 0.0037329 | 0.00093555
26 | 0.98964 | -0.072013 | 0.0037319 | 0.00093531
27 | 0.98313 | -0.11811 | 0.037649 | 0.0094356
28 | 0.99014 | -0.068524 | 0.0040084 | 0.0010046
29 | 0.99059 | -0.0654 | 0.0043402 | 0.0010878
30 | 0.99157 | -0.058515 | 0.0027271 | 0.00068349
31 | 0.99048 | -0.066151 | 0.0020959 | 0.00052529
32 | 0.9922 | -0.054144 | 0.005183 | 0.001299
33 | 0.99423 | -0.040086 | 0.0040613 | 0.0010179
34 | 0.99419 | -0.040358 | 0.0037092 | 0.0009296
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.02385 | -0.0059773 | 0.023883 | 0.0059895 | 3.3087e-05 | 1.2234e-05 | 0.036552 | 0.036552 | 0.036552 | 0.97093 | -0.20476 | 0.97232 | -0.19475 | 13.5377
1 | 0.0016012 | 0.00040125 | -0.0016011 | -0.00040128 | 1.364e-08 | -3.9648e-08 | 0.0024539 | 0.0024539 | 0.0024539 | 0.97093 | -0.20476 | 0.97092 | -0.20482 | 0.90885
2 | -0.049502 | -0.01241 | 0.049813 | 0.012529 | 0.00031159 | 0.00011876 | 0.075758 | 0.075757 | 0.075758 | 0.97232 | -0.19475 | 0.97863 | -0.1496 | 28.0584
3 | -0.054323 | -0.013659 | 0.054463 | 0.013712 | 0.00014005 | 5.3451e-05 | 0.082614 | 0.082614 | 0.082614 | 0.97863 | -0.1496 | 0.98123 | -0.13115 | 30.5978
4 | 0.0045095 | 0.0011301 | -0.0045092 | -0.0011301 | 2.9956e-07 | -1.3073e-08 | 0.0068567 | 0.0068567 | 0.0068567 | 0.97863 | -0.1496 | 0.97856 | -0.15008 | 2.5395
5 | -0.057723 | -0.01453 | 0.0579 | 0.014596 | 0.00017737 | 6.6339e-05 | 0.087558 | 0.087557 | 0.087558 | 0.98123 | -0.13115 | 0.98434 | -0.10921 | 16.2144
6 | 0.19489 | 0.049198 | -0.19447 | -0.049037 | 0.00042215 | 0.00016143 | 0.29074 | 0.29074 | 0.29074 | 0.9979 | -0.014506 | 0.99567 | -0.029962 | 35.894
7 | -0.2167 | -0.054663 | 0.21714 | 0.054832 | 0.00044179 | 0.00016912 | 0.32326 | 0.32326 | 0.32326 | 0.9979 | -0.014506 | 1 | 0 | 39.9083
8 | 0.18879 | 0.047613 | -0.18876 | -0.047599 | 3.673e-05 | 1.404e-05 | 0.28225 | 0.28226 | 0.28226 | 0.99567 | -0.029962 | 0.99547 | -0.03135 | 34.8463
9 | 0.16944 | 0.042756 | -0.16917 | -0.042652 | 0.00027179 | 0.00010374 | 0.25338 | 0.25338 | 0.25338 | 0.99547 | -0.03135 | 0.99383 | -0.042798 | 31.281
10 | 0.01531 | 0.0038386 | -0.015294 | -0.0038331 | 1.5941e-05 | 5.4978e-06 | 0.022886 | 0.022886 | 0.022886 | 0.99547 | -0.03135 | 0.9944 | -0.038872 | 8.4764
11 | 0.16378 | 0.041302 | -0.16368 | -0.041263 | 0.00010256 | 3.9127e-05 | 0.24531 | 0.24531 | 0.24531 | 0.99383 | -0.042798 | 0.99318 | -0.047268 | 30.2853
12 | 0.011683 | 0.0029279 | -0.011681 | -0.0029276 | 1.1561e-06 | 3.6601e-07 | 0.017482 | 0.017482 | 0.017482 | 0.9944 | -0.038872 | 0.9943 | -0.039587 | 6.4747
13 | 0.16065 | 0.040505 | -0.1605 | -0.040446 | 0.00015461 | 5.8968e-05 | 0.24078 | 0.24078 | 0.24078 | 0.99318 | -0.047268 | 0.9922 | -0.054144 | 29.7258
14 | 0.0077712 | 0.0019475 | -0.0077706 | -0.0019474 | 5.3713e-07 | 1.2405e-07 | 0.01163 | 0.01163 | 0.01163 | 0.9943 | -0.039587 | 0.99423 | -0.040086 | 4.3074
15 | -0.0579 | -0.014596 | 0.057945 | 0.014612 | 4.4522e-05 | 1.6058e-05 | 0.087557 | 0.087557 | 0.087557 | 0.98434 | -0.10921 | 0.98512 | -0.10373 | 10.8095
16 | -0.060734 | -0.015311 | 0.060737 | 0.015312 | 2.3918e-06 | 8.6776e-07 | 0.091771 | 0.091771 | 0.091771 | 0.98512 | -0.10373 | 0.98516 | -0.10344 | 11.3297
17 | -0.068375 | -0.017226 | 0.068432 | 0.017247 | 5.6848e-05 | 2.0885e-05 | 0.10331 | 0.10331 | 0.10331 | 0.98516 | -0.10344 | 0.98601 | -0.097506 | 12.754
18 | -0.075354 | -0.018982 | 0.075393 | 0.018997 | 3.9476e-05 | 1.4621e-05 | 0.11375 | 0.11375 | 0.11375 | 0.98601 | -0.097506 | 0.98654 | -0.093762 | 14.0436
19 | -0.078104 | -0.019676 | 0.078157 | 0.019696 | 5.3731e-05 | 1.9953e-05 | 0.11784 | 0.11784 | 0.11784 | 0.98654 | -0.093762 | 0.98724 | -0.088847 | 14.5483
20 | -0.078157 | -0.019696 | 0.078218 | 0.019718 | 6.1092e-05 | 2.2685e-05 | 0.11784 | 0.11784 | 0.11784 | 0.98724 | -0.088847 | 0.98804 | -0.083267 | 14.5482
21 | -0.053074 | -0.013316 | 0.053131 | 0.013338 | 5.7183e-05 | 2.1811e-05 | 0.080117 | 0.080117 | 0.080117 | 0.98581 | -0.099079 | 0.9869 | -0.091322 | 29.6731
22 | 0.049187 | 0.012342 | -0.049161 | -0.012332 | 2.5729e-05 | 9.8004e-06 | 0.07425 | 0.07425 | 0.07425 | 0.98581 | -0.099079 | 0.98527 | -0.10285 | 27.5
23 | -0.055805 | -0.014008 | 0.055894 | 0.014042 | 8.9058e-05 | 3.3995e-05 | 0.084149 | 0.084148 | 0.084149 | 0.9869 | -0.091322 | 0.98853 | -0.079848 | 31.1661
24 | 0.044467 | 0.011156 | -0.044422 | -0.011139 | 4.4816e-05 | 1.7034e-05 | 0.06716 | 0.06716 | 0.06716 | 0.98527 | -0.10285 | 0.98425 | -0.11012 | 24.8742
25 | 0.081991 | 0.020669 | -0.081951 | -0.020654 | 3.9238e-05 | 1.4616e-05 | 0.12346 | 0.12346 | 0.12346 | 0.98853 | -0.079848 | 0.98804 | -0.083267 | 15.2422
26 | -0.13788 | -0.034711 | 0.13804 | 0.034768 | 0.00015107 | 5.7455e-05 | 0.20761 | 0.20761 | 0.20761 | 0.98853 | -0.079848 | 0.98964 | -0.072013 | 25.6309
27 | 0.03769 | 0.0094514 | -0.037649 | -0.0094356 | 4.1684e-05 | 1.5771e-05 | 0.056983 | 0.056983 | 0.056983 | 0.98425 | -0.11012 | 0.98313 | -0.11811 | 21.1049
28 | -0.14177 | -0.035703 | 0.14184 | 0.03573 | 6.917e-05 | 2.6322e-05 | 0.21322 | 0.21322 | 0.21322 | 0.98964 | -0.072013 | 0.99014 | -0.068524 | 26.3236
29 | -0.14585 | -0.036734 | 0.14591 | 0.036759 | 6.3748e-05 | 2.4272e-05 | 0.21925 | 0.21925 | 0.21925 | 0.99014 | -0.068524 | 0.99059 | -0.0654 | 27.0673
30 | -0.15235 | -0.038371 | 0.15249 | 0.038427 | 0.00014679 | 5.5938e-05 | 0.22891 | 0.22891 | 0.22891 | 0.99059 | -0.0654 | 0.99157 | -0.058515 | 28.2609
31 | 0.0020961 | 0.00052492 | -0.0020959 | -0.00052529 | 2.1785e-07 | -3.6949e-07 | 0.0031486 | 0.0031487 | 0.0031487 | 0.99059 | -0.0654 | 0.99048 | -0.066151 | 1.1662
32 | -0.15522 | -0.039111 | 0.15531 | 0.039147 | 9.5008e-05 | 3.6216e-05 | 0.23301 | 0.23301 | 0.23301 | 0.99157 | -0.058515 | 0.9922 | -0.054144 | 28.7661
33 | 0.0037093 | 0.00092956 | -0.0037092 | -0.0009296 | 1.3954e-07 | -4.0425e-08 | 0.0055515 | 0.0055515 | 0.0055515 | 0.99423 | -0.040086 | 0.99419 | -0.040358 | 2.0561

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22276 | 0.05604

## res_load
| p_mw | q_mvar
0 | 0.022249 | 0.0055761
1 | 0.025619 | 0.0064206
2 | 0.0016011 | 0.00040128
3 | 0.0045092 | 0.0011301
4 | 0.0032601 | 0.00081706
5 | 0.021806 | 0.0054652
6 | 0.0056783 | 0.0014231
7 | 0.0048182 | 0.0012075
8 | 0.0040093 | 0.0010048
9 | 0.0053867 | 0.00135
10 | 0.0036118 | 0.0009052
11 | 0.0030253 | 0.00075821
12 | 0.0039103 | 0.00098
13 | 0.0027898 | 0.00069919
14 | 0.0076384 | 0.0019144
15 | 0.0069219 | 0.0017348
16 | 0.0027101 | 0.00067923
17 | 0.0038873 | 0.00097424
18 | 0.0026736 | 0.00067006
19 | 0.0046943 | 0.0011765
20 | 0.0067317 | 0.0016871
21 | 0.0037329 | 0.00093555
22 | 0.0037319 | 0.00093531
23 | 0.037649 | 0.0094356
24 | 0.0040084 | 0.0010046
25 | 0.0043402 | 0.0010878
26 | 0.0027271 | 0.00068349
27 | 0.0020959 | 0.00052529
28 | 0.005183 | 0.001299
29 | 0.0040613 | 0.0010179
30 | 0.0037092 | 0.0009296

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1