## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1401-47_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1401-47_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1401-47_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1401-47_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1401-47_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1401-47_0_2_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1401-47_0_2_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1401-47_0_2_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1401-47_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1401-47_0_2_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1401-47_0_2_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1401-47_0_2_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1401-47_0_2_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1401-47_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1401-47_0_2_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1401-47_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1401-47_0_2_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1401-47_0_2_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1401-47_0_2_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1401-47_0_2_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1401-47_0_2_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1401-47_0_2_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1401-47_0_2_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_1401-47_0_2_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1401-47_0_2_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_1401-47_0_2_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1401-47_0_2_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1401-47_0_2_node_27 | 0.4 | n |  | TRUE
28 | bus_MV_136_0_node_89 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1401-47_0_2_load_0 | 0 | 0.011086 | 0.0027785 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1401-47_0_2_load_1 | 1 | 0.015266 | 0.003826 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1401-47_0_2_load_3 | 3 | 0.0036908 | 0.000925 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1401-47_0_2_load_4 | 4 | 0.003449 | 0.0008644 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1401-47_0_2_load_15 | 5 | 0.014934 | 0.0037429 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1401-47_0_2_load_16 | 6 | 0.017743 | 0.0044468 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1401-47_0_2_load_10 | 7 | 0.0033235 | 0.00083296 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1401-47_0_2_load_5 | 9 | 0.0032377 | 0.00081143 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1401-47_0_2_load_6 | 10 | 0.0070669 | 0.0017711 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1401-47_0_2_load_8 | 11 | 0.0020257 | 0.00050769 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1401-47_0_2_load_9 | 12 | 0.0019601 | 0.00049126 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1401-47_0_2_load_11 | 13 | 0.0020505 | 0.00051391 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1401-47_0_2_load_14 | 14 | 0.0030379 | 0.00076137 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1401-47_0_2_load_12 | 15 | 0.0023605 | 0.00059159 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1401-47_0_2_load_17 | 16 | 0.017094 | 0.0042841 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1401-47_0_2_load_13 | 17 | 0.0034435 | 0.00086303 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1401-47_0_2_load_20 | 18 | 0.013911 | 0.0034864 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1401-47_0_2_load_21 | 20 | 0.013323 | 0.0033391 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1401-47_0_2_load_19 | 21 | 0.0089972 | 0.0022549 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1401-47_0_2_load_25 | 22 | 0.00834 | 0.0020902 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1401-47_0_2_load_22 | 23 | 0.00544 | 0.0013634 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1401-47_0_2_load_23 | 24 | 0.013952 | 0.0034966 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1401-47_0_2_load_24 | 25 | 0.0032787 | 0.00082171 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1401-47_0_2_load_27 | 27 | 0.010888 | 0.0027287 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1401-47_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1401-47_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.032503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1401-47_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.020933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1401-47_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.022635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1401-47_0_2_line_4 | NAYY 4x150 SE | 3 | 7 | 5.199e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1401-47_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.018739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1401-47_0_2_line_6 | NAYY 4x150 SE | 6 | 16 | 0.010509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1401-47_0_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.015367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1401-47_0_2_line_8 | NAYY 4x150 SE | 8 | 12 | 0.010217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1401-47_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.01492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1401-47_0_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.019625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1401-47_0_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.022215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1401-47_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.0074969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1401-47_0_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.040646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1401-47_0_2_line_14 | NAYY 4x150 SE | 13 | 15 | 0.015266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1401-47_0_2_line_15 | NAYY 4x150 SE | 15 | 17 | 0.029981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1401-47_0_2_line_16 | NAYY 4x150 SE | 15 | 18 | 0.042517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1401-47_0_2_line_17 | NAYY 4x150 SE | 16 | 19 | 0.0050861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1401-47_0_2_line_18 | NAYY 4x150 SE | 17 | 22 | 0.027594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1401-47_0_2_line_19 | NAYY 4x150 SE | 18 | 21 | 0.024785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1401-47_0_2_line_20 | NAYY 4x150 SE | 19 | 20 | 0.035444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1401-47_0_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.013739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1401-47_0_2_line_22 | NAYY 4x150 SE | 20 | 23 | 0.00061001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1401-47_0_2_line_23 | NAYY 4x150 SE | 22 | 26 | 0.034322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1401-47_0_2_line_24 | NAYY 4x150 SE | 23 | 24 | 0.0018252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1401-47_0_2_line_25 | NAYY 4x150 SE | 24 | 25 | 0.015822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1401-47_0_2_line_26 | NAYY 4x150 SE | 26 | 27 | 0.018677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1401-47_0_2_trafo_20 | 0.25 MVA 20/0.4 kV | 28 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2663001.6436 | 1198630.4616 | 2663001.3598 | 1198630.0075 | 2662999.4299 | 1198627.4301 | 2662995.6643 | 1198624.889 | 2662994.9474 | 1198623.5473 | 2662994.7974 | 1198620.4328 | 2662995.4272 | 1198616.064
1 | 2663030.6426 | 1198640.6112 | 2663007.7658 | 1198637.0792 | 2663004.962 | 1198635.7711 | 2663001.6436 | 1198630.4616
2 | 2663030.6426 | 1198640.6112 | 2663033.9959 | 1198619.9486
3 | 2663030.6426 | 1198640.6112 | 2663052.9854 | 1198644.2361
4 | 2663034.0043 | 1198619.8973 | 2663033.9959 | 1198619.9486
5 | 2662942.557 | 1198566.9401 | 2662941.6792 | 1198574.3574 | 2662939.4464 | 1198583.9062 | 2662938.8965 | 1198585.2621
6 | 2662942.557 | 1198566.9401 | 2662942.557 | 1198566.9401 | 2662941.4728 | 1198559.2464 | 2662940.5161 | 1198556.6792
7 | 2663036.4659 | 1198604.7292 | 2663034.0043 | 1198619.8973
8 | 2663036.4659 | 1198604.7292 | 2663037.5323 | 1198594.5682
9 | 2663036.4659 | 1198604.7292 | 2663021.7355 | 1198602.3587
10 | 2663021.7355 | 1198602.3587 | 2663010.9601 | 1198600.6247 | 2663009.681 | 1198599.8774 | 2663009.2668 | 1198598.7168 | 2663010.1038 | 1198592.7787
11 | 2663013.2045 | 1198570.7815 | 2663010.1038 | 1198592.7787
12 | 2663014.2508 | 1198563.358 | 2663013.2045 | 1198570.7815
13 | 2663059.8032 | 1198577.869 | 2663039.6407 | 1198574.4782 | 2663037.5323 | 1198594.5682
14 | 2663014.2508 | 1198563.358 | 2663016.3816 | 1198548.2415
15 | 2663025.4767 | 1198519.8498 | 2663021.5989 | 1198530.5399 | 2663019.1275 | 1198538.8632 | 2663017.2096 | 1198542.3673 | 2663016.3816 | 1198548.2415
16 | 2663016.3816 | 1198548.2415 | 2662974.6137 | 1198540.295
17 | 2662938.74 | 1198551.9133 | 2662940.5161 | 1198556.6792
18 | 2663025.4767 | 1198519.8498 | 2663043.4307 | 1198498.8958
19 | 2662951.0599 | 1198545.8326 | 2662961.7206 | 1198540.5707 | 2662974.6137 | 1198540.295
20 | 2662938.74 | 1198551.9133 | 2662934.0773 | 1198541.9917 | 2662923.759 | 1198519.7912
21 | 2662938.74 | 1198551.9133 | 2662951.0599 | 1198545.8326
22 | 2662923.759 | 1198519.7912 | 2662923.5018 | 1198519.238
23 | 2663043.4307 | 1198498.8958 | 2663042.3259 | 1198511.2248 | 2663062.1004 | 1198520.8501
24 | 2662923.5018 | 1198519.238 | 2662922.7326 | 1198517.5829
25 | 2662916.0639 | 1198503.2349 | 2662922.7326 | 1198517.5829
26 | 2663066.5336 | 1198502.7083 | 2663062.1004 | 1198520.8501

## bus_geodata
| x | y | coords
0 | 2663001.6436 | 1198630.4616
1 | 2662995.4272 | 1198616.064
2 | 2663030.6426 | 1198640.6112
3 | 2663033.996 | 1198619.9486
4 | 2663052.9854 | 1198644.2361
5 | 2662938.8965 | 1198585.2621
6 | 2662942.557 | 1198566.9401
7 | 2663034.0043 | 1198619.8973
8 | 2663036.4659 | 1198604.7292
9 | 2663021.7355 | 1198602.3587
10 | 2663010.1038 | 1198592.7787
11 | 2663013.2045 | 1198570.7815
12 | 2663037.5323 | 1198594.5682
13 | 2663014.2508 | 1198563.358
14 | 2663059.8032 | 1198577.869
15 | 2663016.3816 | 1198548.2415
16 | 2662940.5161 | 1198556.6792
17 | 2663025.4767 | 1198519.8498
18 | 2662974.6137 | 1198540.295
19 | 2662938.74 | 1198551.9133
20 | 2662923.759 | 1198519.7912
21 | 2662951.0599 | 1198545.8326
22 | 2663043.4307 | 1198498.8958
23 | 2662923.5018 | 1198519.238
24 | 2662922.7326 | 1198517.5829
25 | 2662916.0639 | 1198503.2349
26 | 2663062.1004 | 1198520.8501
27 | 2663066.5336 | 1198502.7083
28 | 2662938.74 | 1198551.9133

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9864 | -0.095455 | 0.011086 | 0.0027785
1 | 0.98601 | -0.098173 | 0.015266 | 0.003826
2 | 0.98763 | -0.086679 | 0 | 0
3 | 0.98854 | -0.0803 | 0.0036908 | 0.000925
4 | 0.98752 | -0.087478 | 0.003449 | 0.0008644
5 | 0.99368 | -0.044231 | 0.014934 | 0.0037429
6 | 0.99409 | -0.041403 | 0.017743 | 0.0044468
7 | 0.98854 | -0.080282 | 0.0033235 | 0.00083296
8 | 0.98936 | -0.074508 | 0 | 0
9 | 0.99026 | -0.06815 | 0.0032377 | 0.00081143
10 | 0.99153 | -0.05916 | 0.0070669 | 0.0017711
11 | 0.9932 | -0.047422 | 0.0020257 | 0.00050769
12 | 0.98928 | -0.075029 | 0.0019601 | 0.00049126
13 | 0.99379 | -0.043316 | 0.0020505 | 0.00051391
14 | 0.9891 | -0.076289 | 0.0030379 | 0.00076137
15 | 0.99503 | -0.034654 | 0.0023605 | 0.00059159
16 | 0.99458 | -0.037936 | 0.017094 | 0.0042841
17 | 0.99405 | -0.041516 | 0.0034435 | 0.00086303
18 | 1 | 0 | -0.17816 | -0.044627
19 | 0.99494 | -0.035383 | 0 | 0
20 | 0.99311 | -0.04827 | 0.013323 | 0.0033391
21 | 0.99663 | -0.023522 | 0.0089972 | 0.0022549
22 | 0.99329 | -0.04688 | 0.00834 | 0.0020902
23 | 0.99309 | -0.04841 | 0.00544 | 0.0013634
24 | 0.99305 | -0.048728 | 0.013952 | 0.0034966
25 | 0.99297 | -0.049253 | 0.0032787 | 0.00082171
26 | 0.99275 | -0.050664 | 0 | 0
27 | 0.99246 | -0.052724 | 0.010888 | 0.0027287
28 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.015272 | 0.003828 | -0.015266 | -0.003826 | 5.7467e-06 | 1.9889e-06 | 0.023038 | 0.023038 | 0.023038 | 0.9864 | -0.095455 | 0.98601 | -0.098173 | 8.5327
1 | -0.026358 | -0.0066065 | 0.02639 | 0.0066184 | 3.2066e-05 | 1.1918e-05 | 0.039762 | 0.039762 | 0.039762 | 0.9864 | -0.095455 | 0.98763 | -0.086679 | 14.7268
2 | -0.029839 | -0.0074827 | 0.029866 | 0.0074926 | 2.6403e-05 | 9.8868e-06 | 0.044959 | 0.044959 | 0.044959 | 0.98763 | -0.086679 | 0.98854 | -0.0803 | 16.6515
3 | 0.0034494 | 0.00086425 | -0.003449 | -0.0008644 | 3.8147e-07 | -1.429e-07 | 0.0051969 | 0.005197 | 0.005197 | 0.98763 | -0.086679 | 0.98752 | -0.087478 | 1.9248
4 | -0.033557 | -0.0084176 | 0.033557 | 0.0084176 | 8.2782e-08 | 3.1172e-08 | 0.050515 | 0.050515 | 0.050515 | 0.98854 | -0.0803 | 0.98854 | -0.080282 | 18.7091
5 | -0.014934 | -0.0037429 | 0.01494 | 0.0037449 | 5.8481e-06 | 2.0064e-06 | 0.022364 | 0.022364 | 0.022364 | 0.99368 | -0.044231 | 0.99409 | -0.041403 | 8.2829
6 | -0.032683 | -0.0081918 | 0.032699 | 0.0081977 | 1.5696e-05 | 5.9005e-06 | 0.048923 | 0.048923 | 0.048923 | 0.99409 | -0.041403 | 0.99458 | -0.037936 | 18.1196
7 | -0.03688 | -0.0092505 | 0.03691 | 0.0092617 | 2.9554e-05 | 1.117e-05 | 0.055517 | 0.055517 | 0.055517 | 0.98854 | -0.080282 | 0.98936 | -0.074508 | 20.562
8 | 0.0049989 | 0.0012523 | -0.0049986 | -0.0012523 | 3.6037e-07 | 7.4136e-09 | 0.0075183 | 0.0075184 | 0.0075184 | 0.98936 | -0.074508 | 0.98928 | -0.075029 | 2.7846
9 | -0.041909 | -0.010514 | 0.041946 | 0.010528 | 3.6993e-05 | 1.4036e-05 | 0.063036 | 0.063036 | 0.063036 | 0.98936 | -0.074508 | 0.99026 | -0.06815 | 23.3466
10 | -0.045183 | -0.01134 | 0.04524 | 0.011361 | 5.6459e-05 | 2.1462e-05 | 0.067901 | 0.067901 | 0.067901 | 0.99026 | -0.06815 | 0.99153 | -0.05916 | 25.1484
11 | -0.052307 | -0.013132 | 0.052392 | 0.013165 | 8.5434e-05 | 3.2572e-05 | 0.078506 | 0.078506 | 0.078506 | 0.99153 | -0.05916 | 0.9932 | -0.047422 | 29.0763
12 | -0.054418 | -0.013672 | 0.054449 | 0.013684 | 3.1104e-05 | 1.1866e-05 | 0.081541 | 0.081541 | 0.081541 | 0.9932 | -0.047422 | 0.99379 | -0.043316 | 30.2003
13 | 0.0030384 | 0.00076105 | -0.0030379 | -0.00076137 | 5.2974e-07 | -3.1804e-07 | 0.0045701 | 0.0045702 | 0.0045702 | 0.98928 | -0.075029 | 0.9891 | -0.076289 | 1.6927
14 | -0.0565 | -0.014198 | 0.056568 | 0.014224 | 6.8196e-05 | 2.6031e-05 | 0.084611 | 0.084611 | 0.084611 | 0.99379 | -0.043316 | 0.99503 | -0.034654 | 31.3375
15 | 0.022716 | 0.0056977 | -0.022694 | -0.0056898 | 2.1591e-05 | 7.9153e-06 | 0.033972 | 0.033972 | 0.033972 | 0.99503 | -0.034654 | 0.99405 | -0.041516 | 12.5823
16 | -0.081644 | -0.020513 | 0.08204 | 0.020665 | 0.00039561 | 0.0001516 | 0.12211 | 0.12211 | 0.12211 | 0.99503 | -0.034654 | 1 | 0 | 45.2271
17 | -0.049793 | -0.012482 | 0.04981 | 0.012488 | 1.7614e-05 | 6.7085e-06 | 0.074497 | 0.074497 | 0.074497 | 0.99458 | -0.037936 | 0.99494 | -0.035383 | 27.5915
18 | 0.019251 | 0.0048267 | -0.019236 | -0.0048216 | 1.4299e-05 | 5.1422e-06 | 0.028818 | 0.028818 | 0.028818 | 0.99405 | -0.041516 | 0.99329 | -0.04688 | 10.6732
19 | 0.095319 | 0.023962 | -0.095008 | -0.023843 | 0.00031125 | 0.00011939 | 0.14186 | 0.14186 | 0.14186 | 1 | 0 | 0.99663 | -0.023522 | 52.5417
20 | 0.036059 | 0.0090454 | -0.035995 | -0.0090211 | 6.4332e-05 | 2.4284e-05 | 0.053932 | 0.053933 | 0.053933 | 0.99494 | -0.035383 | 0.99311 | -0.04827 | 19.9751
21 | -0.08587 | -0.021534 | 0.086011 | 0.021588 | 0.0001414 | 5.4207e-05 | 0.12843 | 0.12843 | 0.12843 | 0.99494 | -0.035383 | 0.99663 | -0.023522 | 47.5665
22 | 0.022672 | 0.0056821 | -0.022671 | -0.0056819 | 4.3925e-07 | 1.6105e-07 | 0.03397 | 0.03397 | 0.03397 | 0.99311 | -0.04827 | 0.99309 | -0.04841 | 12.5815
23 | 0.010896 | 0.0027314 | -0.010891 | -0.0027297 | 5.707e-06 | 1.751e-06 | 0.016324 | 0.016324 | 0.016324 | 0.99329 | -0.04688 | 0.99275 | -0.050664 | 6.0459
24 | 0.017231 | 0.0043185 | -0.017231 | -0.0043182 | 7.5922e-07 | 2.6839e-07 | 0.025819 | 0.025819 | 0.025819 | 0.99309 | -0.04841 | 0.99305 | -0.048728 | 9.5626
25 | 0.0032789 | 0.0008216 | -0.0032787 | -0.00082171 | 2.3833e-07 | -1.1302e-07 | 0.0049132 | 0.0049132 | 0.0049132 | 0.99305 | -0.048728 | 0.99297 | -0.049253 | 1.8197
26 | 0.010891 | 0.0027297 | -0.010888 | -0.0027287 | 3.1056e-06 | 9.5304e-07 | 0.016324 | 0.016324 | 0.016324 | 0.99275 | -0.050664 | 0.99246 | -0.052724 | 6.0459

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19207 | 0.048114

## res_load
| p_mw | q_mvar
0 | 0.011086 | 0.0027785
1 | 0.015266 | 0.003826
2 | 0.0036908 | 0.000925
3 | 0.003449 | 0.0008644
4 | 0.014934 | 0.0037429
5 | 0.017743 | 0.0044468
6 | 0.0033235 | 0.00083296
7 | 0.0032377 | 0.00081143
8 | 0.0070669 | 0.0017711
9 | 0.0020257 | 0.00050769
10 | 0.0019601 | 0.00049126
11 | 0.0020505 | 0.00051391
12 | 0.0030379 | 0.00076137
13 | 0.0023605 | 0.00059159
14 | 0.017094 | 0.0042841
15 | 0.0034435 | 0.00086303
16 | 0.013911 | 0.0034864
17 | 0.013323 | 0.0033391
18 | 0.0089972 | 0.0022549
19 | 0.00834 | 0.0020902
20 | 0.00544 | 0.0013634
21 | 0.013952 | 0.0034966
22 | 0.0032787 | 0.00082171
23 | 0.010888 | 0.0027287

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1