## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1401-4_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1401-4_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1401-4_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1401-4_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1401-4_0_7_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_1401-4_0_7_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1401-4_0_7_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1401-4_0_7_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_1401-4_0_7_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_1401-4_0_7_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_1401-4_0_7_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_1401-4_0_7_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_1401-4_0_7_node_36 | 0.4 | n |  | TRUE
13 | bus_LV_1401-4_0_7_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1401-4_0_7_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1401-4_0_7_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_1401-4_0_7_node_74 | 0.4 | n |  | TRUE
17 | bus_LV_1401-4_0_7_node_73 | 0.4 | n |  | TRUE
18 | bus_LV_1401-4_0_7_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_1401-4_0_7_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1401-4_0_7_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_1401-4_0_7_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1401-4_0_7_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1401-4_0_7_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1401-4_0_7_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1401-4_0_7_node_63 | 0.4 | n |  | TRUE
26 | bus_LV_1401-4_0_7_node_60 | 0.4 | n |  | TRUE
27 | bus_LV_1401-4_0_7_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1401-4_0_7_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_1401-4_0_7_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_1401-4_0_7_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1401-4_0_7_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1401-4_0_7_node_67 | 0.4 | n |  | TRUE
33 | bus_LV_1401-4_0_7_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_1401-4_0_7_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_1401-4_0_7_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_1401-4_0_7_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1401-4_0_7_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1401-4_0_7_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1401-4_0_7_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_1401-4_0_7_node_54 | 0.4 | n |  | TRUE
41 | bus_LV_1401-4_0_7_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_1401-4_0_7_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_1401-4_0_7_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_1401-4_0_7_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_1401-4_0_7_node_72 | 0.4 | n |  | TRUE
46 | bus_LV_1401-4_0_7_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_1401-4_0_7_node_61 | 0.4 | n |  | TRUE
48 | bus_LV_1401-4_0_7_node_56 | 0.4 | n |  | TRUE
49 | bus_LV_1401-4_0_7_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_1401-4_0_7_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_1401-4_0_7_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_1401-4_0_7_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_1401-4_0_7_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_1401-4_0_7_node_76 | 0.4 | n |  | TRUE
55 | bus_LV_1401-4_0_7_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_1401-4_0_7_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_1401-4_0_7_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_1401-4_0_7_node_75 | 0.4 | n |  | TRUE
59 | bus_LV_1401-4_0_7_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_1401-4_0_7_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_1401-4_0_7_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_1401-4_0_7_node_39 | 0.4 | n |  | TRUE
63 | bus_LV_1401-4_0_7_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_1401-4_0_7_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_1401-4_0_7_node_64 | 0.4 | n |  | TRUE
66 | bus_LV_1401-4_0_7_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_1401-4_0_7_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_1401-4_0_7_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_1401-4_0_7_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_1401-4_0_7_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_1401-4_0_7_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_1401-4_0_7_node_59 | 0.4 | n |  | TRUE
73 | bus_LV_1401-4_0_7_node_71 | 0.4 | n |  | TRUE
74 | bus_LV_1401-4_0_7_node_70 | 0.4 | n |  | TRUE
75 | bus_MV_24_0_node_168 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1401-4_0_7_load_0 | 0 | 0.0010824 | 0.00027127 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1401-4_0_7_load_1 | 1 | 0.00053681 | 0.00013454 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1401-4_0_7_load_2 | 2 | 0.00098764 | 0.00024753 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1401-4_0_7_load_3 | 3 | 0.0032035 | 0.00080287 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1401-4_0_7_load_27 | 4 | 0.0010499 | 0.00026314 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1401-4_0_7_load_5 | 6 | 0.0024652 | 0.00061784 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1401-4_0_7_load_25 | 7 | 0.00080832 | 0.00020258 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1401-4_0_7_load_30 | 9 | 0.0038641 | 0.00096843 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1401-4_0_7_load_28 | 10 | 0.0012816 | 0.0003212 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1401-4_0_7_load_29 | 11 | 0.0041493 | 0.0010399 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1401-4_0_7_load_36 | 12 | 0.0018358 | 0.00046009 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1401-4_0_7_load_6 | 13 | 0.0010904 | 0.00027327 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1401-4_0_7_load_33 | 15 | 0.0012265 | 0.0003074 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1401-4_0_7_load_74 | 16 | 0.0010575 | 0.00026505 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1401-4_0_7_load_73 | 17 | 0.0035358 | 0.00088616 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1401-4_0_7_load_8 | 18 | 0.0030544 | 0.0007655 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1401-4_0_7_load_9 | 19 | 0.0024273 | 0.00060834 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1401-4_0_7_load_10 | 20 | 0.008173 | 0.0020483 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1401-4_0_7_load_11 | 21 | 0.0071887 | 0.0018017 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1401-4_0_7_load_12 | 22 | 0.010439 | 0.0026163 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1401-4_0_7_load_20 | 24 | 0.010882 | 0.0027272 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1401-4_0_7_load_60 | 26 | 0.0050495 | 0.0012655 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1401-4_0_7_load_18 | 27 | 0.00098421 | 0.00024667 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1401-4_0_7_load_13 | 28 | 0.0011448 | 0.00028692 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1401-4_0_7_load_15 | 30 | 0.0030325 | 0.00076 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1401-4_0_7_load_16 | 31 | 0.01195 | 0.002995 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1401-4_0_7_load_67 | 32 | 0.00060717 | 0.00015217 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1401-4_0_7_load_31 | 34 | 0.0050399 | 0.0012631 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1401-4_0_7_load_35 | 36 | 0.011394 | 0.0028557 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1401-4_0_7_load_23 | 37 | 0.0024715 | 0.00061942 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1401-4_0_7_load_24 | 38 | 0.002068 | 0.00051829 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1401-4_0_7_load_68 | 39 | 0.0021978 | 0.00055081 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1401-4_0_7_load_54 | 40 | 0.0021975 | 0.00055074 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1401-4_0_7_load_17 | 41 | 0.0038055 | 0.00095375 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1401-4_0_7_load_19 | 42 | 0.00098489 | 0.00024684 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1401-4_0_7_load_21 | 43 | 0.00098539 | 0.00024696 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1401-4_0_7_load_34 | 44 | 0.0048298 | 0.0012105 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1401-4_0_7_load_72 | 45 | 0.0062464 | 0.0015655 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1401-4_0_7_load_42 | 46 | 0.013449 | 0.0033705 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1401-4_0_7_load_61 | 47 | 0.0098793 | 0.002476 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1401-4_0_7_load_56 | 48 | 0.0049265 | 0.0012347 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1401-4_0_7_load_51 | 49 | 0.011212 | 0.00281 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1401-4_0_7_load_52 | 50 | 0.002195 | 0.00055013 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1401-4_0_7_load_45 | 52 | 0.0021493 | 0.00053865 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1401-4_0_7_load_47 | 53 | 0.00067933 | 0.00017026 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1401-4_0_7_load_76 | 54 | 0.00062892 | 0.00015762 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1401-4_0_7_load_49 | 56 | 0.0012108 | 0.00030345 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1401-4_0_7_load_75 | 58 | 0.0016524 | 0.00041412 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1401-4_0_7_load_46 | 59 | 0.00064575 | 0.00016184 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1401-4_0_7_load_38 | 61 | 0.0057961 | 0.0014526 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1401-4_0_7_load_39 | 62 | 0.0029936 | 0.00075027 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1401-4_0_7_load_40 | 63 | 0.00671 | 0.0016817 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1401-4_0_7_load_41 | 64 | 0.0043309 | 0.0010854 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1401-4_0_7_load_64 | 65 | 0.0023756 | 0.00059538 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1401-4_0_7_load_43 | 66 | 0.0011654 | 0.00029209 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1401-4_0_7_load_44 | 67 | 0.00109 | 0.00027319 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1401-4_0_7_load_65 | 68 | 0.0008655 | 0.00021691 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1401-4_0_7_load_55 | 69 | 0.0072029 | 0.0018052 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1401-4_0_7_load_58 | 70 | 0.0029167 | 0.00073098 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1401-4_0_7_load_57 | 71 | 0.0077884 | 0.0019519 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1401-4_0_7_load_59 | 72 | 0.0031154 | 0.00078079 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1401-4_0_7_load_71 | 73 | 0.0044848 | 0.001124 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1401-4_0_7_load_70 | 74 | 0.004265 | 0.0010689 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1401-4_0_7_line_0 | NAYY 4x150 SE | 0 | 1 | 0.024129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1401-4_0_7_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0036993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1401-4_0_7_line_2 | NAYY 4x150 SE | 1 | 3 | 0.032697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1401-4_0_7_line_3 | NAYY 4x150 SE | 1 | 4 | 0.1198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1401-4_0_7_line_4 | NAYY 4x150 SE | 2 | 5 | 0.046946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1401-4_0_7_line_5 | NAYY 4x150 SE | 3 | 6 | 0.017633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1401-4_0_7_line_6 | NAYY 4x150 SE | 4 | 10 | 0.019037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1401-4_0_7_line_7 | NAYY 4x150 SE | 4 | 11 | 0.055686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1401-4_0_7_line_8 | NAYY 4x150 SE | 4 | 7 | 0.028136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1401-4_0_7_line_9 | NAYY 4x150 SE | 5 | 13 | 0.021812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1401-4_0_7_line_10 | NAYY 4x150 SE | 5 | 14 | 0.012121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1401-4_0_7_line_11 | NAYY 4x150 SE | 7 | 8 | 0.029377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1401-4_0_7_line_12 | NAYY 4x150 SE | 8 | 9 | 0.33641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1401-4_0_7_line_13 | NAYY 4x150 SE | 9 | 34 | 0.042115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1401-4_0_7_line_14 | NAYY 4x150 SE | 10 | 12 | 0.0065206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1401-4_0_7_line_15 | NAYY 4x150 SE | 13 | 15 | 0.010132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1401-4_0_7_line_16 | NAYY 4x150 SE | 14 | 16 | 0.026045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1401-4_0_7_line_17 | NAYY 4x150 SE | 16 | 17 | 0.031765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1401-4_0_7_line_18 | NAYY 4x150 SE | 17 | 65 | 0.05233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1401-4_0_7_line_19 | NAYY 4x150 SE | 18 | 19 | 0.027737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1401-4_0_7_line_20 | NAYY 4x150 SE | 18 | 20 | 0.010464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1401-4_0_7_line_21 | NAYY 4x150 SE | 19 | 21 | 0.028303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1401-4_0_7_line_22 | NAYY 4x150 SE | 20 | 22 | 0.020823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1401-4_0_7_line_23 | NAYY 4x150 SE | 21 | 23 | 0.034023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1401-4_0_7_line_24 | NAYY 4x150 SE | 22 | 24 | 0.0013984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1401-4_0_7_line_25 | NAYY 4x150 SE | 23 | 25 | 0.018788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1401-4_0_7_line_26 | NAYY 4x150 SE | 23 | 26 | 0.046988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1401-4_0_7_line_27 | NAYY 4x150 SE | 24 | 27 | 0.054583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1401-4_0_7_line_28 | NAYY 4x150 SE | 25 | 45 | 0.011622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1401-4_0_7_line_29 | NAYY 4x150 SE | 25 | 46 | 0.060061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1401-4_0_7_line_30 | NAYY 4x150 SE | 26 | 47 | 0.022056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1401-4_0_7_line_31 | NAYY 4x150 SE | 27 | 41 | 0.012295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1401-4_0_7_line_32 | NAYY 4x150 SE | 28 | 29 | 0.022636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1401-4_0_7_line_33 | NAYY 4x150 SE | 29 | 30 | 0.071952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1401-4_0_7_line_34 | NAYY 4x150 SE | 29 | 31 | 0.035801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1401-4_0_7_line_35 | NAYY 4x150 SE | 30 | 37 | 0.019849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1401-4_0_7_line_36 | NAYY 4x150 SE | 31 | 32 | 0.10313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_1401-4_0_7_line_37 | NAYY 4x150 SE | 32 | 33 | 0.08176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1401-4_0_7_line_38 | NAYY 4x150 SE | 33 | 60 | 0.013934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1401-4_0_7_line_39 | NAYY 4x150 SE | 34 | 35 | 0.02385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1401-4_0_7_line_40 | NAYY 4x150 SE | 35 | 36 | 0.010012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1401-4_0_7_line_41 | NAYY 4x150 SE | 37 | 38 | 0.064627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1401-4_0_7_line_42 | NAYY 4x150 SE | 38 | 48 | 0.069414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1401-4_0_7_line_43 | NAYY 4x150 SE | 39 | 40 | 0.0066069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1401-4_0_7_line_44 | NAYY 4x150 SE | 40 | 50 | 0.0049938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1401-4_0_7_line_45 | NAYY 4x150 SE | 41 | 42 | 0.0029581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1401-4_0_7_line_46 | NAYY 4x150 SE | 42 | 43 | 0.0053651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1401-4_0_7_line_47 | NAYY 4x150 SE | 43 | 44 | 0.034536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1401-4_0_7_line_48 | NAYY 4x150 SE | 45 | 73 | 0.025187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1401-4_0_7_line_49 | NAYY 4x150 SE | 46 | 63 | 0.022498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1401-4_0_7_line_50 | NAYY 4x150 SE | 47 | 60 | 0.075564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1401-4_0_7_line_51 | NAYY 4x150 SE | 48 | 52 | 0.22417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1401-4_0_7_line_52 | NAYY 4x150 SE | 48 | 51 | 0.05392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1401-4_0_7_line_53 | NAYY 4x150 SE | 49 | 50 | 0.025342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1401-4_0_7_line_54 | NAYY 4x150 SE | 49 | 51 | 0.02273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1401-4_0_7_line_55 | NAYY 4x150 SE | 51 | 69 | 0.023807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1401-4_0_7_line_56 | NAYY 4x150 SE | 52 | 66 | 0.00014211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1401-4_0_7_line_57 | NAYY 4x150 SE | 53 | 54 | 0.19959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1401-4_0_7_line_58 | NAYY 4x150 SE | 54 | 58 | 0.015085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1401-4_0_7_line_59 | NAYY 4x150 SE | 55 | 56 | 0.027399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1401-4_0_7_line_60 | NAYY 4x150 SE | 55 | 57 | 0.076501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1401-4_0_7_line_61 | NAYY 4x150 SE | 57 | 58 | 0.055689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1401-4_0_7_line_62 | NAYY 4x150 SE | 58 | 59 | 0.29579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1401-4_0_7_line_63 | NAYY 4x150 SE | 59 | 68 | 0.036497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1401-4_0_7_line_64 | NAYY 4x150 SE | 59 | 67 | 0.028186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1401-4_0_7_line_65 | NAYY 4x150 SE | 61 | 62 | 0.0026381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_1401-4_0_7_line_66 | NAYY 4x150 SE | 61 | 63 | 0.0037303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_1401-4_0_7_line_67 | NAYY 4x150 SE | 62 | 64 | 0.017369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_1401-4_0_7_line_68 | NAYY 4x150 SE | 64 | 65 | 0.0022409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_1401-4_0_7_line_69 | NAYY 4x150 SE | 66 | 67 | 0.10036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1401-4_0_7_line_70 | NAYY 4x150 SE | 69 | 70 | 0.0039391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1401-4_0_7_line_71 | NAYY 4x150 SE | 70 | 71 | 0.017023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1401-4_0_7_line_72 | NAYY 4x150 SE | 71 | 72 | 0.011436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1401-4_0_7_line_73 | NAYY 4x150 SE | 73 | 74 | 0.054178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1401-4_0_7_trafo_62 | 0.25 MVA 20/0.4 kV | 75 | 60 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2665019.6109 | 1201853.0399 | 2664997.2579 | 1201862.1253
1 | 2665019.6109 | 1201853.0399 | 2665021.2352 | 1201852.3797 | 2665023.139 | 1201852.7827
2 | 2664997.2579 | 1201862.1253 | 2664993.4764 | 1201863.6623 | 2665008.4602 | 1201888.0408
3 | 2664997.2579 | 1201862.1253 | 2664879.4192 | 1201883.7018
4 | 2665069.0674 | 1201862.5063 | 2665023.139 | 1201852.7827
5 | 2665017.6932 | 1201903.0627 | 2665008.4602 | 1201888.0408
6 | 2664879.4192 | 1201883.7018 | 2664871.2101 | 1201866.5254
7 | 2664879.4192 | 1201883.7018 | 2664885.0903 | 1201896.9379 | 2664885.1982 | 1201930.448 | 2664887.7872 | 1201937.78
8 | 2664879.4192 | 1201883.7018 | 2664858.4203 | 1201902.4287
9 | 2665069.0674 | 1201862.5063 | 2665047.7287 | 1201857.9886
10 | 2665079.232 | 1201869.1543 | 2665069.0674 | 1201862.5063
11 | 2664836.4958 | 1201921.9811 | 2664858.4203 | 1201902.4287
12 | 2664836.4958 | 1201921.9811 | 2664502.4888 | 1201962.1231
13 | 2664502.4888 | 1201962.1231 | 2664502.0724 | 1201960.23 | 2664496.7405 | 1201956.3924 | 2664493.6937 | 1201960.1395 | 2664499.5035 | 1201988.3251
14 | 2664871.2101 | 1201866.5254 | 2664868.3983 | 1201860.6422
15 | 2665047.7287 | 1201857.9886 | 2665037.8168 | 1201855.8902
16 | 2665079.232 | 1201869.1543 | 2665082.259 | 1201843.2858
17 | 2665082.259 | 1201843.2858 | 2665084.7123 | 1201822.3192 | 2665085.056 | 1201814.5294 | 2665085.0393 | 1201811.6714
18 | 2665085.0393 | 1201811.6714 | 2665085.0188 | 1201808.1586 | 2665084.4525 | 1201800.0587 | 2665083.6583 | 1201794.0131 | 2665082.0319 | 1201786.1129 | 2665077.9581 | 1201775.0952 | 2665075.5022 | 1201770.677 | 2665072.0675 | 1201765.2697 | 2665070.0302 | 1201762.6402
19 | 2664985.3525 | 1201767.4535 | 2664963.3785 | 1201760.4067 | 2664958.9351 | 1201758.9989
20 | 2664995.3169 | 1201770.649 | 2664985.3525 | 1201767.4535
21 | 2664942.9045 | 1201745.6848 | 2664941.6877 | 1201752.5885 | 2664943.1956 | 1201757.4078 | 2664947.6507 | 1201759.2795 | 2664957.1284 | 1201758.4265 | 2664958.9351 | 1201758.9989
22 | 2664995.3169 | 1201770.649 | 2665015.1457 | 1201777.0079
23 | 2664954.6609 | 1201713.7618 | 2664942.9531 | 1201745.4091 | 2664942.9045 | 1201745.6848
24 | 2665015.1457 | 1201777.0079 | 2665016.4773 | 1201777.4349
25 | 2664972.8123 | 1201718.8066 | 2664954.6609 | 1201713.7618
26 | 2664954.6609 | 1201713.7618 | 2664909.4304 | 1201701.0308
27 | 2665016.4773 | 1201777.4349 | 2665044.0501 | 1201786.2773 | 2665046.8108 | 1201787.8749 | 2665047.9236 | 1201789.8327 | 2665053.2368 | 1201809.3062
28 | 2664972.8123 | 1201718.8066 | 2664968.3732 | 1201711.2649 | 2664965.6293 | 1201710.4196
29 | 2664972.8123 | 1201718.8066 | 2665022.8137 | 1201733.9371 | 2665030.2273 | 1201736.4263
30 | 2664909.4304 | 1201701.0308 | 2664905.194 | 1201699.8384 | 2664888.3461 | 1201694.5614
31 | 2665062.0525 | 1201815.0823 | 2665057.3556 | 1201814.828 | 2665055.5333 | 1201814.4302 | 2665054.1667 | 1201812.7143 | 2665053.2368 | 1201809.3062
32 | 2664658.3804 | 1201630.333 | 2664643.9495 | 1201637.3366 | 2664638.3372 | 1201640.8009
33 | 2664658.3804 | 1201630.333 | 2664645.9734 | 1201611.3875 | 2664641.3315 | 1201605.6561 | 2664617.5279 | 1201571.1373
34 | 2664658.3804 | 1201630.333 | 2664666.1008 | 1201635.7419 | 2664681.651 | 1201651.1972 | 2664683.689 | 1201655.153
35 | 2664610.3571 | 1201552.7346 | 2664611.5772 | 1201554.3927 | 2664617.2087 | 1201570.6744 | 2664617.5279 | 1201571.1373
36 | 2664767.7574 | 1201595.4099 | 2664683.689 | 1201655.153
37 | 2664819.3609 | 1201657.0703 | 2664819.2151 | 1201655.0786 | 2664818.7101 | 1201653.2165 | 2664817.5795 | 1201650.7917 | 2664815.9327 | 1201648.2389 | 2664812.88 | 1201645.482 | 2664808.6232 | 1201642.1561 | 2664802.3855 | 1201637.6079 | 2664795.084 | 1201631.4918 | 2664788.0243 | 1201624.1331 | 2664783.3122 | 1201617.8783 | 2664772.8622 | 1201602.3891 | 2664767.7574 | 1201595.4099
38 | 2664816.6714 | 1201670.6492 | 2664819.0003 | 1201662.2472 | 2664819.4228 | 1201659.7837 | 2664819.3609 | 1201657.0703
39 | 2664502.694 | 1202011.912 | 2664501.7141 | 1201999.0493 | 2664499.5035 | 1201988.3251
40 | 2664502.694 | 1202011.912 | 2664508.8293 | 1202019.8233
41 | 2664564.8312 | 1201507.5596 | 2664580.9742 | 1201518.9297 | 2664600.1228 | 1201538.8262 | 2664610.3571 | 1201552.7346
42 | 2664576.3082 | 1201439.1006 | 2664564.8312 | 1201507.5596
43 | 2664675.6398 | 1201493.8253 | 2664670.3678 | 1201489.8434
44 | 2664666.3011 | 1201486.9578 | 2664667.2942 | 1201487.5219 | 2664670.3678 | 1201489.8434
45 | 2665062.0525 | 1201815.0823 | 2665065.0063 | 1201815.2421
46 | 2665070.3635 | 1201815.5321 | 2665065.0063 | 1201815.2421
47 | 2665076.5013 | 1201788.6542 | 2665078.8499 | 1201809.2142 | 2665079.0579 | 1201813.1744 | 2665077.7816 | 1201815.0505 | 2665076.129 | 1201815.8441 | 2665070.3635 | 1201815.5321
48 | 2664965.6293 | 1201710.4196 | 2664941.5581 | 1201703.0042
49 | 2665050.7941 | 1201745.4256 | 2665046.5 | 1201743.0225 | 2665039.9725 | 1201739.9608 | 2665032.2249 | 1201737.097 | 2665030.2273 | 1201736.4263
50 | 2664816.6714 | 1201670.6492 | 2664867.7517 | 1201688.1249 | 2664874.5637 | 1201690.2446 | 2664888.3461 | 1201694.5614
51 | 2664576.3082 | 1201439.1006 | 2664353.3167 | 1201416.113
52 | 2664624.669 | 1201462.924 | 2664602.9985 | 1201451.6831 | 2664576.3082 | 1201439.1006
53 | 2664644.2735 | 1201474.427 | 2664645.1891 | 1201474.9642 | 2664666.3011 | 1201486.9578
54 | 2664624.669 | 1201462.924 | 2664644.2735 | 1201474.427
55 | 2664624.669 | 1201462.924 | 2664631.4437 | 1201450.9346 | 2664632.4823 | 1201447.7995 | 2664632.129 | 1201445.2831 | 2664629.3927 | 1201442.1071
56 | 2664353.3167 | 1201416.113 | 2664353.1996 | 1201416.0326
57 | 2664029.9535 | 1201483.9809 | 2664100.4654 | 1201670.7034
58 | 2664029.9535 | 1201483.9809 | 2664026.8202 | 1201474.4972 | 2664023.1338 | 1201470.9769
59 | 2663989.5332 | 1201470.0286 | 2663999.4772 | 1201473.2814 | 2664010.9693 | 1201485.4895 | 2664011.0802 | 1201485.6194
60 | 2663984.7536 | 1201432.3217 | 2663979.5544 | 1201431.6545 | 2663971.8837 | 1201431.4834 | 2663964.0519 | 1201432.8448 | 2663957.3522 | 1201437.9651 | 2663966.9768 | 1201441.9038 | 2663975.7721 | 1201447.9348 | 2663979.3681 | 1201451.8868 | 2663985.258 | 1201462.6896 | 2663989.5332 | 1201470.0286
61 | 2663984.7536 | 1201432.3217 | 2663994.3076 | 1201437.8717 | 2664000.5694 | 1201443.0863 | 2664011.6626 | 1201454.1672 | 2664015.5637 | 1201463.748 | 2664023.1338 | 1201470.9769
62 | 2664276.3117 | 1201318.0351 | 2664023.1338 | 1201470.9769
63 | 2664258.2856 | 1201289.2111 | 2664264.5449 | 1201294.8301 | 2664270.3295 | 1201302.6526 | 2664269.0376 | 1201310.2321 | 2664276.3117 | 1201318.0351
64 | 2664276.3117 | 1201318.0351 | 2664285.7882 | 1201328.2007 | 2664295.1802 | 1201338.9692
65 | 2665053.922 | 1201747.4445 | 2665056.0449 | 1201749.0108
66 | 2665053.922 | 1201747.4445 | 2665052.416 | 1201746.3333 | 2665050.7941 | 1201745.4256
67 | 2665056.0449 | 1201749.0108 | 2665058.4112 | 1201750.7568 | 2665063.84 | 1201755.4631 | 2665067.9844 | 1201759.9999 | 2665068.6576 | 1201760.8687
68 | 2665068.6576 | 1201760.8687 | 2665070.0302 | 1201762.6402
69 | 2664353.1996 | 1201416.0326 | 2664333.9209 | 1201402.8074 | 2664323.2847 | 1201395.2774 | 2664317.9915 | 1201388.4941 | 2664313.9475 | 1201378.8004 | 2664308.9759 | 1201359.1018 | 2664301.8412 | 1201346.6065 | 2664295.1802 | 1201338.9692
70 | 2664626.4589 | 1201439.4785 | 2664629.3927 | 1201442.1071 | 2664629.3927 | 1201442.1071
71 | 2664613.7803 | 1201428.1189 | 2664626.4589 | 1201439.4785
72 | 2664603.63 | 1201422.8505 | 2664613.7803 | 1201428.1189
73 | 2664889.7818 | 1201687.0537 | 2664941.5581 | 1201703.0042

## bus_geodata
| x | y | coords
0 | 2665019.6109 | 1201853.0399
1 | 2664997.2579 | 1201862.1253
2 | 2665023.139 | 1201852.7827
3 | 2665008.4602 | 1201888.0408
4 | 2664879.4192 | 1201883.7018
5 | 2665069.0674 | 1201862.5063
6 | 2665017.6932 | 1201903.0627
7 | 2664858.4203 | 1201902.4287
8 | 2664836.4958 | 1201921.9811
9 | 2664502.4888 | 1201962.1231
10 | 2664871.2101 | 1201866.5254
11 | 2664887.7872 | 1201937.78
12 | 2664868.3983 | 1201860.6422
13 | 2665047.7287 | 1201857.9886
14 | 2665079.232 | 1201869.1543
15 | 2665037.8168 | 1201855.8902
16 | 2665082.259 | 1201843.2858
17 | 2665085.0393 | 1201811.6714
18 | 2664985.3525 | 1201767.4535
19 | 2664958.9351 | 1201758.9989
20 | 2664995.3169 | 1201770.649
21 | 2664942.9045 | 1201745.6848
22 | 2665015.1457 | 1201777.0079
23 | 2664954.6609 | 1201713.7618
24 | 2665016.4773 | 1201777.4349
25 | 2664972.8123 | 1201718.8066
26 | 2664909.4304 | 1201701.0308
27 | 2665053.2368 | 1201809.3062
28 | 2664638.3372 | 1201640.8009
29 | 2664658.3804 | 1201630.333
30 | 2664617.5279 | 1201571.1373
31 | 2664683.689 | 1201655.153
32 | 2664767.7573 | 1201595.4099
33 | 2664819.3609 | 1201657.0703
34 | 2664499.5035 | 1201988.3251
35 | 2664502.694 | 1202011.912
36 | 2664508.8293 | 1202019.8233
37 | 2664610.3571 | 1201552.7346
38 | 2664564.8312 | 1201507.5596
39 | 2664675.6398 | 1201493.8253
40 | 2664670.3677 | 1201489.8434
41 | 2665062.0525 | 1201815.0823
42 | 2665065.0063 | 1201815.2421
43 | 2665070.3635 | 1201815.5321
44 | 2665076.5013 | 1201788.6542
45 | 2664965.6293 | 1201710.4196
46 | 2665030.2273 | 1201736.4263
47 | 2664888.3461 | 1201694.5614
48 | 2664576.3082 | 1201439.1006
49 | 2664644.2735 | 1201474.427
50 | 2664666.3011 | 1201486.9578
51 | 2664624.669 | 1201462.924
52 | 2664353.3167 | 1201416.113
53 | 2664100.4654 | 1201670.7034
54 | 2664029.9535 | 1201483.9809
55 | 2663989.5332 | 1201470.0286
56 | 2664011.0802 | 1201485.6194
57 | 2663984.7536 | 1201432.3217
58 | 2664023.1338 | 1201470.9769
59 | 2664276.3117 | 1201318.0351
60 | 2664816.6714 | 1201670.6492
61 | 2665053.922 | 1201747.4445
62 | 2665056.0449 | 1201749.0108
63 | 2665050.7941 | 1201745.4256
64 | 2665068.6576 | 1201760.8687
65 | 2665070.0302 | 1201762.6402
66 | 2664353.1996 | 1201416.0326
67 | 2664295.1802 | 1201338.9692
68 | 2664258.2856 | 1201289.2111
69 | 2664629.3927 | 1201442.1071
70 | 2664626.4589 | 1201439.4785
71 | 2664613.7803 | 1201428.1189
72 | 2664603.63 | 1201422.8505
73 | 2664941.5581 | 1201703.0042
74 | 2664889.7818 | 1201687.0537
75 | 2664819.3609 | 1201657.0703

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98094 | -0.13373 | 0.0010824 | 0.00027127
1 | 0.98052 | -0.13672 | 0.00053681 | 0.00013454
2 | 0.98101 | -0.13326 | 0.00098764 | 0.00024753
3 | 0.98025 | -0.13864 | 0.0032035 | 0.00080287
4 | 0.9788 | -0.14898 | 0.0010499 | 0.00026314
5 | 0.98187 | -0.12713 | 0 | 0
6 | 0.98019 | -0.1391 | 0.0024652 | 0.00061784
7 | 0.97851 | -0.15105 | 0.00080832 | 0.00020258
8 | 0.97822 | -0.15313 | 0 | 0
9 | 0.97321 | -0.18899 | 0.0038641 | 0.00096843
10 | 0.97872 | -0.1496 | 0.0012816 | 0.0003212
11 | 0.97847 | -0.15139 | 0.0041493 | 0.0010399
12 | 0.9787 | -0.14973 | 0.0018358 | 0.00046009
13 | 0.98179 | -0.12765 | 0.0010904 | 0.00027327
14 | 0.9821 | -0.12545 | 0 | 0
15 | 0.98178 | -0.12778 | 0.0012265 | 0.0003074
16 | 0.98261 | -0.12184 | 0.0010575 | 0.00026505
17 | 0.98325 | -0.11733 | 0.0035358 | 0.00088616
18 | 0.98263 | -0.1217 | 0.0030544 | 0.0007655
19 | 0.98441 | -0.10906 | 0.0024273 | 0.00060834
20 | 0.982 | -0.12615 | 0.008173 | 0.0020483
21 | 0.98632 | -0.09551 | 0.0071887 | 0.0018017
22 | 0.98101 | -0.13325 | 0.010439 | 0.0026163
23 | 0.98898 | -0.076791 | 0 | 0
24 | 0.98096 | -0.13357 | 0.010882 | 0.0027272
25 | 0.98811 | -0.082899 | 0 | 0
26 | 0.99237 | -0.053014 | 0.0050495 | 0.0012655
27 | 0.98004 | -0.14015 | 0.00098421 | 0.00024667
28 | 0.99167 | -0.05782 | 0.0011448 | 0.00028692
29 | 0.99171 | -0.057557 | 0 | 0
30 | 0.98956 | -0.072572 | 0.0030325 | 0.00076
31 | 0.9928 | -0.049969 | 0.01195 | 0.002995
32 | 0.99652 | -0.024065 | 0.00060717 | 0.00015217
33 | 0.99949 | -0.0034943 | 0 | 0
34 | 0.9722 | -0.1963 | 0.0050399 | 0.0012631
35 | 0.9718 | -0.19917 | 0 | 0
36 | 0.97163 | -0.20037 | 0.011394 | 0.0028557
37 | 0.989 | -0.076521 | 0.0024715 | 0.00061942
38 | 0.98637 | -0.095045 | 0.002068 | 0.00051829
39 | 0.97698 | -0.16182 | 0.0021978 | 0.00055081
40 | 0.977 | -0.16167 | 0.0021975 | 0.00055074
41 | 0.97985 | -0.1415 | 0.0038055 | 0.00095375
42 | 0.97982 | -0.14171 | 0.00098489 | 0.00024684
43 | 0.97978 | -0.14204 | 0.00098539 | 0.00024696
44 | 0.97953 | -0.14377 | 0.0048298 | 0.0012105
45 | 0.98786 | -0.084682 | 0.0062464 | 0.0015655
46 | 0.98577 | -0.099407 | 0.013449 | 0.0033705
47 | 0.99401 | -0.041534 | 0.0098793 | 0.002476
48 | 0.98092 | -0.13368 | 0.0049265 | 0.0012347
49 | 0.97727 | -0.1597 | 0.011212 | 0.00281
50 | 0.97703 | -0.16144 | 0.002195 | 0.00055013
51 | 0.97786 | -0.15547 | 0 | 0
52 | 0.97762 | -0.15742 | 0.0021493 | 0.00053865
53 | 0.97436 | -0.18106 | 0.00067933 | 0.00017026
54 | 0.97455 | -0.17961 | 0.00062892 | 0.00015762
55 | 0.97435 | -0.1811 | 0 | 0
56 | 0.9743 | -0.18145 | 0.0012108 | 0.00030345
57 | 0.97448 | -0.18012 | 0 | 0
58 | 0.97458 | -0.1794 | 0.0016524 | 0.00041412
59 | 0.97639 | -0.16631 | 0.00064575 | 0.00016184
60 | 1 | 0 | -0.24405 | -0.061457
61 | 0.98494 | -0.10534 | 0.0057961 | 0.0014526
62 | 0.98487 | -0.10584 | 0.0029936 | 0.00075027
63 | 0.98504 | -0.10457 | 0.00671 | 0.0016817
64 | 0.98443 | -0.10891 | 0.0043309 | 0.0010854
65 | 0.98438 | -0.10927 | 0.0023756 | 0.00059538
66 | 0.97761 | -0.15743 | 0.0011654 | 0.00029209
67 | 0.97662 | -0.16461 | 0.00109 | 0.00027319
68 | 0.97634 | -0.16664 | 0.0008655 | 0.00021691
69 | 0.97713 | -0.1607 | 0.0072029 | 0.0018052
70 | 0.97705 | -0.16127 | 0.0029167 | 0.00073098
71 | 0.97678 | -0.16321 | 0.0077884 | 0.0019519
72 | 0.97673 | -0.16358 | 0.0031154 | 0.00078079
73 | 0.98754 | -0.086938 | 0.0044848 | 0.001124
74 | 0.98721 | -0.089305 | 0.004265 | 0.0010689
75 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.035834 | 0.0089896 | -0.035819 | -0.0089848 | 1.4831e-05 | 4.7908e-06 | 0.05436 | 0.054361 | 0.054361 | 0.98094 | -0.13373 | 0.98052 | -0.13672 | 6.7112
1 | -0.036916 | -0.0092609 | 0.036918 | 0.0092617 | 2.4132e-06 | 7.8805e-07 | 0.056002 | 0.056002 | 0.056002 | 0.98094 | -0.13373 | 0.98101 | -0.13326 | 6.9138
2 | 0.0056704 | 0.0014207 | -0.0056689 | -0.0014205 | 1.5108e-06 | 1.6878e-07 | 0.0086051 | 0.0086052 | 0.0086052 | 0.98052 | -0.13672 | 0.98025 | -0.13864 | 3.1871
3 | 0.029612 | 0.0074296 | -0.029561 | -0.0074147 | 5.0328e-05 | 1.4832e-05 | 0.044941 | 0.044943 | 0.044943 | 0.98052 | -0.13672 | 0.9788 | -0.14898 | 5.5485
4 | -0.037906 | -0.0095092 | 0.037938 | 0.0095198 | 3.2285e-05 | 1.0638e-05 | 0.0575 | 0.0575 | 0.0575 | 0.98101 | -0.13326 | 0.98187 | -0.12713 | 7.0988
5 | 0.0024654 | 0.00061768 | -0.0024652 | -0.00061784 | 1.541e-07 | -1.63e-07 | 0.0037423 | 0.0037424 | 0.0037424 | 0.98025 | -0.13864 | 0.98019 | -0.1391 | 1.3861
6 | 0.0031177 | 0.00078108 | -0.0031174 | -0.00078122 | 2.6685e-07 | -1.3662e-07 | 0.0047395 | 0.0047396 | 0.0047396 | 0.9788 | -0.14898 | 0.97872 | -0.1496 | 1.7554
7 | 0.0041507 | 0.0010397 | -0.0041493 | -0.0010399 | 1.3835e-06 | -1.6756e-07 | 0.0063098 | 0.0063101 | 0.0063101 | 0.9788 | -0.14898 | 0.97847 | -0.15139 | 2.3371
8 | 0.021243 | 0.0053308 | -0.021237 | -0.0053295 | 6.1046e-06 | 1.2873e-06 | 0.032297 | 0.032297 | 0.032297 | 0.9788 | -0.14898 | 0.97851 | -0.15105 | 3.9873
9 | 0.0023171 | 0.00058034 | -0.0023169 | -0.00058055 | 1.6782e-07 | -2.113e-07 | 0.0035114 | 0.0035115 | 0.0035115 | 0.98187 | -0.12713 | 0.98179 | -0.12765 | 1.3006
10 | -0.040255 | -0.0101 | 0.040265 | 0.010103 | 9.3846e-06 | 3.1494e-06 | 0.061011 | 0.061011 | 0.061011 | 0.98187 | -0.12713 | 0.9821 | -0.12545 | 7.5322
11 | 0.020429 | 0.0051269 | -0.020423 | -0.0051257 | 5.8979e-06 | 1.1617e-06 | 0.031068 | 0.031069 | 0.031069 | 0.97851 | -0.15105 | 0.97822 | -0.15313 | 3.8356
12 | 0.020423 | 0.0051257 | -0.020321 | -0.0050952 | 0.00010132 | 3.0567e-05 | 0.031069 | 0.031072 | 0.031072 | 0.97822 | -0.15313 | 0.97321 | -0.18899 | 5.754
13 | 0.016457 | 0.0041267 | -0.016441 | -0.0041209 | 1.6641e-05 | 5.8775e-06 | 0.025164 | 0.025164 | 0.025164 | 0.97321 | -0.18899 | 0.9722 | -0.1963 | 9.3199
14 | 0.0018358 | 0.00046002 | -0.0018358 | -0.00046009 | 3.1697e-08 | -6.975e-08 | 0.0027911 | 0.0027911 | 0.0027911 | 0.97872 | -0.1496 | 0.9787 | -0.14973 | 1.0337
15 | 0.0012266 | 0.00030728 | -0.0012265 | -0.0003074 | 2.1848e-08 | -1.1972e-07 | 0.0018589 | 0.001859 | 0.001859 | 0.98179 | -0.12765 | 0.98178 | -0.12778 | 0.68851
16 | -0.040265 | -0.010103 | 0.040285 | 0.01011 | 2.0165e-05 | 6.7665e-06 | 0.061011 | 0.06101 | 0.061011 | 0.9821 | -0.12545 | 0.98261 | -0.12184 | 7.5322
17 | -0.041343 | -0.010375 | 0.041368 | 0.010384 | 2.5901e-05 | 8.7542e-06 | 0.062612 | 0.062611 | 0.062612 | 0.98261 | -0.12184 | 0.98325 | -0.11733 | 7.7299
18 | -0.044904 | -0.01127 | 0.044955 | 0.011287 | 5.0274e-05 | 1.7343e-05 | 0.067962 | 0.067962 | 0.067962 | 0.98325 | -0.11733 | 0.98438 | -0.10927 | 8.3904
19 | -0.044211 | -0.011088 | 0.044288 | 0.011118 | 7.7585e-05 | 2.9488e-05 | 0.066952 | 0.066952 | 0.066952 | 0.98263 | -0.1217 | 0.98441 | -0.10906 | 24.7971
20 | 0.041156 | 0.010323 | -0.041131 | -0.010313 | 2.5365e-05 | 9.6235e-06 | 0.062327 | 0.062327 | 0.062327 | 0.98263 | -0.1217 | 0.982 | -0.12615 | 23.084
21 | -0.046716 | -0.011726 | 0.046804 | 0.01176 | 8.8083e-05 | 3.3517e-05 | 0.070621 | 0.070621 | 0.070621 | 0.98441 | -0.10906 | 0.98632 | -0.09551 | 26.156
22 | 0.032958 | 0.0082648 | -0.032926 | -0.0082526 | 3.241e-05 | 1.2202e-05 | 0.049942 | 0.049943 | 0.049943 | 0.982 | -0.12615 | 0.98101 | -0.13325 | 18.4972
23 | -0.053992 | -0.013561 | 0.054133 | 0.013615 | 0.0001409 | 5.3758e-05 | 0.081466 | 0.081466 | 0.081466 | 0.98632 | -0.09551 | 0.98898 | -0.076791 | 30.1727
24 | 0.022486 | 0.0056363 | -0.022485 | -0.0056359 | 1.0151e-06 | 3.7278e-07 | 0.034108 | 0.034108 | 0.034108 | 0.98101 | -0.13325 | 0.98096 | -0.13357 | 12.6327
25 | 0.095963 | 0.024113 | -0.095882 | -0.024083 | 8.1495e-05 | 3.0622e-05 | 0.14441 | 0.14441 | 0.14441 | 0.98898 | -0.076791 | 0.98811 | -0.082899 | 17.8282
26 | -0.1501 | -0.037728 | 0.15059 | 0.037918 | 0.00049864 | 0.00018997 | 0.22587 | 0.22587 | 0.22587 | 0.98898 | -0.076791 | 0.99237 | -0.053014 | 27.8857
27 | 0.011604 | 0.0029087 | -0.011593 | -0.0029054 | 1.0553e-05 | 3.3704e-06 | 0.017602 | 0.017602 | 0.017602 | 0.98096 | -0.13357 | 0.98004 | -0.14015 | 6.5194
28 | 0.015004 | 0.0037602 | -0.015 | -0.003759 | 3.7025e-06 | 1.2752e-06 | 0.022595 | 0.022595 | 0.022595 | 0.98811 | -0.082899 | 0.98786 | -0.084682 | 8.3685
29 | 0.080878 | 0.020322 | -0.080692 | -0.020253 | 0.00018538 | 6.8996e-05 | 0.12181 | 0.12181 | 0.12181 | 0.98811 | -0.082899 | 0.98577 | -0.099407 | 15.0389
30 | -0.15564 | -0.039184 | 0.15589 | 0.039279 | 0.00025001 | 9.5302e-05 | 0.23345 | 0.23345 | 0.23345 | 0.99237 | -0.053014 | 0.99401 | -0.041534 | 28.8204
31 | 0.010609 | 0.0026587 | -0.010607 | -0.0026581 | 1.9907e-06 | 6.1076e-07 | 0.016108 | 0.016108 | 0.016108 | 0.98004 | -0.14015 | 0.97985 | -0.1415 | 5.966
32 | -0.0011448 | -0.00028692 | 0.0011448 | 0.00028664 | 4.1677e-08 | -2.7602e-07 | 0.0017178 | 0.0017177 | 0.0017178 | 0.99167 | -0.05782 | 0.99171 | -0.057557 | 0.63622
33 | 0.06221 | 0.015677 | -0.06208 | -0.015629 | 0.00013049 | 4.7407e-05 | 0.093374 | 0.093375 | 0.093375 | 0.99171 | -0.057557 | 0.98956 | -0.072572 | 11.5277
34 | -0.063355 | -0.015963 | 0.063422 | 0.015988 | 6.7334e-05 | 2.451e-05 | 0.095091 | 0.095091 | 0.095091 | 0.99171 | -0.057557 | 0.9928 | -0.049969 | 11.7397
35 | 0.059047 | 0.014869 | -0.059015 | -0.014858 | 3.2567e-05 | 1.1761e-05 | 0.088815 | 0.088815 | 0.088815 | 0.98956 | -0.072572 | 0.989 | -0.076521 | 10.9648
36 | -0.075372 | -0.018983 | 0.075646 | 0.019084 | 0.00027393 | 0.00010134 | 0.113 | 0.113 | 0.113 | 0.9928 | -0.049969 | 0.99652 | -0.024065 | 13.9509
37 | -0.076254 | -0.019237 | 0.076474 | 0.019318 | 0.00022065 | 8.166e-05 | 0.11391 | 0.11391 | 0.11391 | 0.99652 | -0.024065 | 0.99949 | -0.0034943 | 14.0626
38 | -0.076474 | -0.019318 | 0.076512 | 0.019332 | 3.7604e-05 | 1.3915e-05 | 0.11391 | 0.11391 | 0.11391 | 0.99949 | -0.0034943 | 1 | 0 | 14.0625
39 | 0.011401 | 0.0028577 | -0.011396 | -0.0028563 | 4.5316e-06 | 1.4473e-06 | 0.01745 | 0.01745 | 0.01745 | 0.9722 | -0.1963 | 0.9718 | -0.19917 | 6.4629
40 | 0.011396 | 0.0028563 | -0.011394 | -0.0028557 | 1.9023e-06 | 6.0763e-07 | 0.01745 | 0.01745 | 0.01745 | 0.9718 | -0.19917 | 0.97163 | -0.20037 | 6.463
41 | 0.056543 | 0.014238 | -0.056397 | -0.014184 | 0.00014601 | 5.4505e-05 | 0.085096 | 0.085097 | 0.085097 | 0.989 | -0.076521 | 0.98637 | -0.095045 | 15.7587
42 | 0.054329 | 0.013665 | -0.054038 | -0.013554 | 0.00029109 | 0.00011108 | 0.081977 | 0.081978 | 0.081978 | 0.98637 | -0.095045 | 0.98092 | -0.13368 | 30.3621
43 | -0.0021978 | -0.00055081 | 0.0021978 | 0.00055074 | 4.6194e-08 | -6.4967e-08 | 0.0033474 | 0.0033473 | 0.0033474 | 0.97698 | -0.16182 | 0.977 | -0.16167 | 1.2398
44 | -0.0043953 | -0.0011015 | 0.0043954 | 0.0011015 | 1.3964e-07 | -8.8301e-09 | 0.0066942 | 0.0066942 | 0.0066942 | 0.977 | -0.16167 | 0.97703 | -0.16144 | 2.4793
45 | 0.0068017 | 0.0017043 | -0.0068015 | -0.0017043 | 1.9693e-07 | 3.8484e-08 | 0.010329 | 0.010329 | 0.010329 | 0.97985 | -0.1415 | 0.97982 | -0.14171 | 3.8256
46 | 0.0058166 | 0.0014575 | -0.0058163 | -0.0014574 | 2.6122e-07 | 3.2898e-08 | 0.0088333 | 0.0088333 | 0.0088333 | 0.97982 | -0.14171 | 0.97978 | -0.14204 | 3.2716
47 | 0.0048309 | 0.0012105 | -0.0048298 | -0.0012105 | 1.16e-06 | 1.1334e-08 | 0.0073368 | 0.0073369 | 0.0073369 | 0.97978 | -0.14204 | 0.97953 | -0.14377 | 2.7174
48 | 0.0087539 | 0.0021935 | -0.0087512 | -0.0021928 | 2.7327e-06 | 7.2868e-07 | 0.013186 | 0.013186 | 0.013186 | 0.98786 | -0.084682 | 0.98754 | -0.086938 | 4.8837
49 | 0.067244 | 0.016883 | -0.067195 | -0.016865 | 4.8224e-05 | 1.7688e-05 | 0.10151 | 0.10151 | 0.10151 | 0.98577 | -0.099407 | 0.98504 | -0.10457 | 12.5327
50 | -0.16577 | -0.041755 | 0.16674 | 0.042125 | 0.0009685 | 0.00036954 | 0.24823 | 0.24823 | 0.24823 | 0.99401 | -0.041534 | 1 | 0 | 30.6462
51 | 0.010137 | 0.0025338 | -0.010103 | -0.0025239 | 3.3067e-05 | 9.8976e-06 | 0.015374 | 0.015375 | 0.015375 | 0.98092 | -0.13368 | 0.97762 | -0.15742 | 5.6946
52 | 0.038975 | 0.0097859 | -0.038857 | -0.0097413 | 0.00011764 | 4.4567e-05 | 0.05913 | 0.05913 | 0.05913 | 0.98092 | -0.13368 | 0.97786 | -0.15547 | 21.9001
53 | 0.006592 | 0.0016519 | -0.0065904 | -0.0016516 | 1.5931e-06 | 2.9529e-07 | 0.010037 | 0.010037 | 0.010037 | 0.97727 | -0.1597 | 0.97703 | -0.16144 | 3.7175
54 | -0.017804 | -0.0044619 | 0.017815 | 0.0044656 | 1.0423e-05 | 3.724e-06 | 0.027109 | 0.027109 | 0.027109 | 0.97727 | -0.1597 | 0.97786 | -0.15547 | 10.0403
55 | 0.021043 | 0.0052757 | -0.021027 | -0.0052701 | 1.5233e-05 | 5.5602e-06 | 0.032021 | 0.032022 | 0.032022 | 0.97786 | -0.15547 | 0.97713 | -0.1607 | 11.8598
56 | 0.0079542 | 0.0019852 | -0.0079542 | -0.0019852 | 1.2991e-08 | 3.2148e-09 | 0.012104 | 0.012104 | 0.012104 | 0.97762 | -0.15742 | 0.97761 | -0.15743 | 4.483
57 | -0.00067933 | -0.00017026 | 0.00067947 | 0.00016782 | 1.3394e-07 | -2.4349e-06 | 0.0010375 | 0.0010366 | 0.0010375 | 0.97436 | -0.18106 | 0.97455 | -0.17961 | 0.38425
58 | -0.0013084 | -0.00032544 | 0.0013084 | 0.00032527 | 3.7533e-08 | -1.7353e-07 | 0.0019968 | 0.0019968 | 0.0019968 | 0.97455 | -0.17961 | 0.97458 | -0.1794 | 0.73957
59 | 0.0012108 | 0.00030313 | -0.0012108 | -0.00030345 | 5.8459e-08 | -3.1876e-07 | 0.0018491 | 0.0018492 | 0.0018492 | 0.97435 | -0.1811 | 0.9743 | -0.18145 | 0.68488
60 | -0.0012108 | -0.00030313 | 0.001211 | 0.00030224 | 1.6318e-07 | -8.9018e-07 | 0.0018491 | 0.0018487 | 0.0018491 | 0.97435 | -0.1811 | 0.97448 | -0.18012 | 0.68483
61 | -0.001211 | -0.00030224 | 0.0012111 | 0.00030159 | 1.1875e-07 | -6.4819e-07 | 0.0018487 | 0.0018485 | 0.0018487 | 0.97448 | -0.18012 | 0.97458 | -0.1794 | 0.68471
62 | -0.0041719 | -0.001041 | 0.0041794 | 0.0010402 | 7.4834e-06 | -8.1438e-07 | 0.0063681 | 0.0063668 | 0.0063681 | 0.97458 | -0.1794 | 0.97639 | -0.16631 | 2.3586
63 | 0.00086554 | 0.00021647 | -0.0008655 | -0.00021691 | 3.9621e-08 | -4.4121e-07 | 0.0013189 | 0.0013191 | 0.0013191 | 0.97639 | -0.16631 | 0.97634 | -0.16664 | 0.48855
64 | -0.0056907 | -0.0014185 | 0.005692 | 0.0014186 | 1.322e-06 | 1.5586e-07 | 0.0086698 | 0.0086697 | 0.0086698 | 0.97639 | -0.16631 | 0.97662 | -0.16461 | 3.2111
65 | 0.054683 | 0.013728 | -0.054679 | -0.013727 | 3.7458e-06 | 1.34e-06 | 0.082622 | 0.082622 | 0.082622 | 0.98494 | -0.10534 | 0.98487 | -0.10584 | 10.2002
66 | -0.060479 | -0.015181 | 0.060485 | 0.015183 | 6.4787e-06 | 2.3494e-06 | 0.091378 | 0.091378 | 0.091378 | 0.98494 | -0.10534 | 0.98504 | -0.10457 | 11.2813
67 | 0.051685 | 0.012977 | -0.051663 | -0.012969 | 2.2036e-05 | 7.8127e-06 | 0.078099 | 0.078099 | 0.078099 | 0.98487 | -0.10584 | 0.98443 | -0.10891 | 9.6419
68 | 0.047332 | 0.011884 | -0.04733 | -0.011883 | 2.3864e-06 | 8.3238e-07 | 0.071553 | 0.071553 | 0.071553 | 0.98443 | -0.10891 | 0.98438 | -0.10927 | 8.8337
69 | 0.0067887 | 0.0016931 | -0.006782 | -0.0016918 | 6.6828e-06 | 1.3133e-06 | 0.01033 | 0.010331 | 0.010331 | 0.97761 | -0.15743 | 0.97662 | -0.16461 | 3.8261
70 | 0.013825 | 0.0034649 | -0.013824 | -0.0034646 | 1.0894e-06 | 3.6968e-07 | 0.021053 | 0.021053 | 0.021053 | 0.97713 | -0.1607 | 0.97705 | -0.16127 | 7.7973
71 | 0.010907 | 0.0027336 | -0.010904 | -0.0027327 | 2.9309e-06 | 9.1414e-07 | 0.016611 | 0.016611 | 0.016611 | 0.97705 | -0.16127 | 0.97678 | -0.16321 | 6.1522
72 | 0.0031156 | 0.00078071 | -0.0031154 | -0.00078079 | 1.6075e-07 | -8.1313e-08 | 0.0047462 | 0.0047462 | 0.0047462 | 0.97678 | -0.16321 | 0.97673 | -0.16358 | 1.7579
73 | 0.0042664 | 0.0010688 | -0.004265 | -0.0010689 | 1.3971e-06 | -1.5558e-07 | 0.0064284 | 0.0064287 | 0.0064287 | 0.98754 | -0.086938 | 0.98721 | -0.089305 | 2.381

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24405 | 0.061457

## res_load
| p_mw | q_mvar
0 | 0.0010824 | 0.00027127
1 | 0.00053681 | 0.00013454
2 | 0.00098764 | 0.00024753
3 | 0.0032035 | 0.00080287
4 | 0.0010499 | 0.00026314
5 | 0.0024652 | 0.00061784
6 | 0.00080832 | 0.00020258
7 | 0.0038641 | 0.00096843
8 | 0.0012816 | 0.0003212
9 | 0.0041493 | 0.0010399
10 | 0.0018358 | 0.00046009
11 | 0.0010904 | 0.00027327
12 | 0.0012265 | 0.0003074
13 | 0.0010575 | 0.00026505
14 | 0.0035358 | 0.00088616
15 | 0.0030544 | 0.0007655
16 | 0.0024273 | 0.00060834
17 | 0.008173 | 0.0020483
18 | 0.0071887 | 0.0018017
19 | 0.010439 | 0.0026163
20 | 0.010882 | 0.0027272
21 | 0.0050495 | 0.0012655
22 | 0.00098421 | 0.00024667
23 | 0.0011448 | 0.00028692
24 | 0.0030325 | 0.00076
25 | 0.01195 | 0.002995
26 | 0.00060717 | 0.00015217
27 | 0.0050399 | 0.0012631
28 | 0.011394 | 0.0028557
29 | 0.0024715 | 0.00061942
30 | 0.002068 | 0.00051829
31 | 0.0021978 | 0.00055081
32 | 0.0021975 | 0.00055074
33 | 0.0038055 | 0.00095375
34 | 0.00098489 | 0.00024684
35 | 0.00098539 | 0.00024696
36 | 0.0048298 | 0.0012105
37 | 0.0062464 | 0.0015655
38 | 0.013449 | 0.0033705
39 | 0.0098793 | 0.002476
40 | 0.0049265 | 0.0012347
41 | 0.011212 | 0.00281
42 | 0.002195 | 0.00055013
43 | 0.0021493 | 0.00053865
44 | 0.00067933 | 0.00017026
45 | 0.00062892 | 0.00015762
46 | 0.0012108 | 0.00030345
47 | 0.0016524 | 0.00041412
48 | 0.00064575 | 0.00016184
49 | 0.0057961 | 0.0014526
50 | 0.0029936 | 0.00075027
51 | 0.00671 | 0.0016817
52 | 0.0043309 | 0.0010854
53 | 0.0023756 | 0.00059538
54 | 0.0011654 | 0.00029209
55 | 0.00109 | 0.00027319
56 | 0.0008655 | 0.00021691
57 | 0.0072029 | 0.0018052
58 | 0.0029167 | 0.00073098
59 | 0.0077884 | 0.0019519
60 | 0.0031154 | 0.00078079
61 | 0.0044848 | 0.001124
62 | 0.004265 | 0.0010689

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1