## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1402-25_1_6_node_131 | 0.4 | n |  | TRUE
1 | bus_LV_1402-25_1_6_node_32 | 0.4 | n |  | TRUE
2 | bus_LV_1402-25_1_6_node_147 | 0.4 | n |  | TRUE
3 | bus_LV_1402-25_1_6_node_148 | 0.4 | n |  | TRUE
4 | bus_LV_1402-25_1_6_node_150 | 0.4 | n |  | TRUE
5 | bus_LV_1402-25_1_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1402-25_1_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1402-25_1_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1402-25_1_6_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1402-25_1_6_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1402-25_1_6_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_1402-25_1_6_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_1402-25_1_6_node_114 | 0.4 | n |  | TRUE
13 | bus_LV_1402-25_1_6_node_48 | 0.4 | n |  | TRUE
14 | bus_LV_1402-25_1_6_node_87 | 0.4 | n |  | TRUE
15 | bus_LV_1402-25_1_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1402-25_1_6_node_84 | 0.4 | n |  | TRUE
17 | bus_LV_1402-25_1_6_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1402-25_1_6_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1402-25_1_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1402-25_1_6_node_151 | 0.4 | n |  | TRUE
21 | bus_LV_1402-25_1_6_node_115 | 0.4 | n |  | TRUE
22 | bus_LV_1402-25_1_6_node_77 | 0.4 | n |  | TRUE
23 | bus_LV_1402-25_1_6_node_118 | 0.4 | n |  | TRUE
24 | bus_LV_1402-25_1_6_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_1402-25_1_6_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1402-25_1_6_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1402-25_1_6_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1402-25_1_6_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1402-25_1_6_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1402-25_1_6_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_1402-25_1_6_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1402-25_1_6_node_149 | 0.4 | n |  | TRUE
33 | bus_LV_1402-25_1_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1402-25_1_6_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_1402-25_1_6_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_1402-25_1_6_node_141 | 0.4 | n |  | TRUE
37 | bus_LV_1402-25_1_6_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1402-25_1_6_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_1402-25_1_6_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1402-25_1_6_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1402-25_1_6_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_1402-25_1_6_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_1402-25_1_6_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_1402-25_1_6_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_1402-25_1_6_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_1402-25_1_6_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_1402-25_1_6_node_155 | 0.4 | n |  | TRUE
48 | bus_LV_1402-25_1_6_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1402-25_1_6_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_1402-25_1_6_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_1402-25_1_6_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_1402-25_1_6_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_1402-25_1_6_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_1402-25_1_6_node_47 | 0.4 | n |  | TRUE
55 | bus_LV_1402-25_1_6_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_1402-25_1_6_node_136 | 0.4 | n |  | TRUE
57 | bus_LV_1402-25_1_6_node_134 | 0.4 | n |  | TRUE
58 | bus_LV_1402-25_1_6_node_135 | 0.4 | n |  | TRUE
59 | bus_LV_1402-25_1_6_node_146 | 0.4 | n |  | TRUE
60 | bus_LV_1402-25_1_6_node_145 | 0.4 | n |  | TRUE
61 | bus_LV_1402-25_1_6_node_140 | 0.4 | n |  | TRUE
62 | bus_LV_1402-25_1_6_node_74 | 0.4 | n |  | TRUE
63 | bus_LV_1402-25_1_6_node_75 | 0.4 | n |  | TRUE
64 | bus_LV_1402-25_1_6_node_153 | 0.4 | n |  | TRUE
65 | bus_LV_1402-25_1_6_node_98 | 0.4 | n |  | TRUE
66 | bus_LV_1402-25_1_6_node_79 | 0.4 | n |  | TRUE
67 | bus_LV_1402-25_1_6_node_80 | 0.4 | n |  | TRUE
68 | bus_LV_1402-25_1_6_node_91 | 0.4 | n |  | TRUE
69 | bus_LV_1402-25_1_6_node_88 | 0.4 | n |  | TRUE
70 | bus_LV_1402-25_1_6_node_81 | 0.4 | n |  | TRUE
71 | bus_LV_1402-25_1_6_node_82 | 0.4 | n |  | TRUE
72 | bus_LV_1402-25_1_6_node_83 | 0.4 | n |  | TRUE
73 | bus_LV_1402-25_1_6_node_85 | 0.4 | n |  | TRUE
74 | bus_LV_1402-25_1_6_node_86 | 0.4 | n |  | TRUE
75 | bus_LV_1402-25_1_6_node_92 | 0.4 | n |  | TRUE
76 | bus_LV_1402-25_1_6_node_95 | 0.4 | n |  | TRUE
77 | bus_LV_1402-25_1_6_node_89 | 0.4 | n |  | TRUE
78 | bus_LV_1402-25_1_6_node_90 | 0.4 | n |  | TRUE
79 | bus_LV_1402-25_1_6_node_102 | 0.4 | n |  | TRUE
80 | bus_LV_1402-25_1_6_node_103 | 0.4 | n |  | TRUE
81 | bus_LV_1402-25_1_6_node_108 | 0.4 | n |  | TRUE
82 | bus_LV_1402-25_1_6_node_94 | 0.4 | n |  | TRUE
83 | bus_LV_1402-25_1_6_node_93 | 0.4 | n |  | TRUE
84 | bus_LV_1402-25_1_6_node_96 | 0.4 | n |  | TRUE
85 | bus_LV_1402-25_1_6_node_97 | 0.4 | n |  | TRUE
86 | bus_LV_1402-25_1_6_node_99 | 0.4 | n |  | TRUE
87 | bus_LV_1402-25_1_6_node_100 | 0.4 | n |  | TRUE
88 | bus_LV_1402-25_1_6_node_101 | 0.4 | n |  | TRUE
89 | bus_LV_1402-25_1_6_node_110 | 0.4 | n |  | TRUE
90 | bus_LV_1402-25_1_6_node_104 | 0.4 | n |  | TRUE
91 | bus_LV_1402-25_1_6_node_105 | 0.4 | n |  | TRUE
92 | bus_LV_1402-25_1_6_node_106 | 0.4 | n |  | TRUE
93 | bus_LV_1402-25_1_6_node_107 | 0.4 | n |  | TRUE
94 | bus_LV_1402-25_1_6_node_109 | 0.4 | n |  | TRUE
95 | bus_LV_1402-25_1_6_node_112 | 0.4 | n |  | TRUE
96 | bus_LV_1402-25_1_6_node_111 | 0.4 | n |  | TRUE
97 | bus_LV_1402-25_1_6_node_113 | 0.4 | n |  | TRUE
98 | bus_LV_1402-25_1_6_node_116 | 0.4 | n |  | TRUE
99 | bus_LV_1402-25_1_6_node_117 | 0.4 | n |  | TRUE
100 | bus_LV_1402-25_1_6_node_119 | 0.4 | n |  | TRUE
101 | bus_LV_1402-25_1_6_node_120 | 0.4 | n |  | TRUE
102 | bus_LV_1402-25_1_6_node_121 | 0.4 | n |  | TRUE
103 | bus_LV_1402-25_1_6_node_138 | 0.4 | n |  | TRUE
104 | bus_LV_1402-25_1_6_node_122 | 0.4 | n |  | TRUE
105 | bus_LV_1402-25_1_6_node_123 | 0.4 | n |  | TRUE
106 | bus_LV_1402-25_1_6_node_124 | 0.4 | n |  | TRUE
107 | bus_LV_1402-25_1_6_node_125 | 0.4 | n |  | TRUE
108 | bus_LV_1402-25_1_6_node_126 | 0.4 | n |  | TRUE
109 | bus_LV_1402-25_1_6_node_127 | 0.4 | n |  | TRUE
110 | bus_LV_1402-25_1_6_node_130 | 0.4 | n |  | TRUE
111 | bus_LV_1402-25_1_6_node_128 | 0.4 | n |  | TRUE
112 | bus_LV_1402-25_1_6_node_129 | 0.4 | n |  | TRUE
113 | bus_LV_1402-25_1_6_node_154 | 0.4 | n |  | TRUE
114 | bus_LV_1402-25_1_6_node_133 | 0.4 | n |  | TRUE
115 | bus_LV_1402-25_1_6_node_132 | 0.4 | n |  | TRUE
116 | bus_LV_1402-25_1_6_node_137 | 0.4 | n |  | TRUE
117 | bus_LV_1402-25_1_6_node_139 | 0.4 | n |  | TRUE
118 | bus_MV_137_0_node_150 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1402-25_1_6_load_131 | 0 | 0.00036258 | 9.087e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1402-25_1_6_load_32 | 1 | 0.0012111 | 0.00030353 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1402-25_1_6_load_147 | 2 | 0.00047738 | 0.00011964 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1402-25_1_6_load_148 | 3 | 0.00049692 | 0.00012454 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1402-25_1_6_load_150 | 4 | 0.0071791 | 0.0017992 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1402-25_1_6_load_5 | 5 | 0.0015705 | 0.0003936 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1402-25_1_6_load_8 | 8 | 0.00092964 | 0.00023299 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1402-25_1_6_load_51 | 11 | 0.0024961 | 0.00062557 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1402-25_1_6_load_48 | 13 | 0.0021739 | 0.00054483 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1402-25_1_6_load_87 | 14 | 0.00079163 | 0.0001984 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1402-25_1_6_load_10 | 15 | 0.0013405 | 0.00033597 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1402-25_1_6_load_84 | 16 | 0.0023431 | 0.00058724 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1402-25_1_6_load_13 | 19 | 0.0042867 | 0.0010743 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1402-25_1_6_load_151 | 20 | 0.0085133 | 0.0021336 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1402-25_1_6_load_77 | 22 | 0.0024263 | 0.0006081 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1402-25_1_6_load_118 | 23 | 0.00093643 | 0.00023469 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1402-25_1_6_load_78 | 24 | 0.0030477 | 0.00076382 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1402-25_1_6_load_14 | 25 | 0.00059456 | 0.00014901 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1402-25_1_6_load_17 | 28 | 0.0062066 | 0.0015555 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1402-25_1_6_load_18 | 29 | 0.00052598 | 0.00013182 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1402-25_1_6_load_19 | 30 | 0.0024554 | 0.00061538 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1402-25_1_6_load_27 | 34 | 0.0014014 | 0.00035122 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1402-25_1_6_load_26 | 35 | 0.0012593 | 0.00031561 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1402-25_1_6_load_21 | 38 | 0.0010054 | 0.00025198 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1402-25_1_6_load_28 | 39 | 0.00572 | 0.0014336 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1402-25_1_6_load_25 | 40 | 0.0040749 | 0.0010213 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1402-25_1_6_load_22 | 41 | 0.0012729 | 0.00031902 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1402-25_1_6_load_40 | 42 | 0.00070854 | 0.00017758 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1402-25_1_6_load_38 | 43 | 0.00088196 | 0.00022104 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1402-25_1_6_load_29 | 45 | 0.00074348 | 0.00018633 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1402-25_1_6_load_30 | 46 | 0.0023447 | 0.00058764 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1402-25_1_6_load_155 | 47 | 0.0020201 | 0.00050629 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1402-25_1_6_load_31 | 48 | 0.0021662 | 0.00054291 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1402-25_1_6_load_33 | 49 | 0.0011532 | 0.00028902 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1402-25_1_6_load_34 | 50 | 0.00216 | 0.00054134 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1402-25_1_6_load_36 | 52 | 0.000704 | 0.00017644 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1402-25_1_6_load_39 | 53 | 0.00066576 | 0.00016686 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1402-25_1_6_load_47 | 54 | 0.0012009 | 0.00030098 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1402-25_1_6_load_49 | 55 | 0.00095363 | 0.000239 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1402-25_1_6_load_136 | 56 | 0.0010117 | 0.00025356 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1402-25_1_6_load_134 | 57 | 0.00054514 | 0.00013663 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1402-25_1_6_load_145 | 60 | 0.00048639 | 0.0001219 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1402-25_1_6_load_74 | 62 | 0.0068096 | 0.0017067 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1402-25_1_6_load_75 | 63 | 0.0015774 | 0.00039533 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1402-25_1_6_load_153 | 64 | 0.0025363 | 0.00063567 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1402-25_1_6_load_98 | 65 | 0.013941 | 0.0034938 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1402-25_1_6_load_79 | 66 | 0.0049755 | 0.001247 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1402-25_1_6_load_91 | 68 | 0.0030361 | 0.00076091 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1402-25_1_6_load_88 | 69 | 0.0013076 | 0.00032772 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1402-25_1_6_load_81 | 70 | 0.0013669 | 0.00034258 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1402-25_1_6_load_82 | 71 | 0.0013848 | 0.00034708 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1402-25_1_6_load_85 | 73 | 0.0023341 | 0.00058498 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1402-25_1_6_load_86 | 74 | 0.0012406 | 0.00031093 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1402-25_1_6_load_89 | 77 | 0.002353 | 0.00058973 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1402-25_1_6_load_102 | 79 | 0.00147 | 0.00036843 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1402-25_1_6_load_103 | 80 | 0.0018052 | 0.00045242 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1402-25_1_6_load_108 | 81 | 0.0028659 | 0.00071825 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1402-25_1_6_load_94 | 82 | 0.0019709 | 0.00049396 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1402-25_1_6_load_93 | 83 | 0.0022367 | 0.00056056 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1402-25_1_6_load_96 | 84 | 0.00073109 | 0.00018323 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1402-25_1_6_load_97 | 85 | 0.0013019 | 0.00032628 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1402-25_1_6_load_99 | 86 | 0.013957 | 0.003498 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1402-25_1_6_load_100 | 87 | 0.0031712 | 0.00079478 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1402-25_1_6_load_101 | 88 | 0.0040311 | 0.0010103 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1402-25_1_6_load_104 | 90 | 0.0031182 | 0.00078149 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1402-25_1_6_load_105 | 91 | 0.0031182 | 0.00078149 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1402-25_1_6_load_106 | 92 | 0.0028263 | 0.00070835 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1402-25_1_6_load_107 | 93 | 0.0045948 | 0.0011516 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1402-25_1_6_load_109 | 94 | 0.0022498 | 0.00056386 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1402-25_1_6_load_112 | 95 | 0.0020853 | 0.00052263 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1402-25_1_6_load_111 | 96 | 0.0028017 | 0.00070216 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1402-25_1_6_load_113 | 97 | 0.0021287 | 0.0005335 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1402-25_1_6_load_116 | 98 | 0.00085395 | 0.00021402 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1402-25_1_6_load_119 | 100 | 0.0020532 | 0.00051459 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1402-25_1_6_load_120 | 101 | 0.00095559 | 0.00023949 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1402-25_1_6_load_121 | 102 | 0.0053165 | 0.0013324 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1402-25_1_6_load_138 | 103 | 0.0025664 | 0.0006432 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1402-25_1_6_load_122 | 104 | 0.0014089 | 0.00035311 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1402-25_1_6_load_123 | 105 | 0.001268 | 0.00031778 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1402-25_1_6_load_124 | 106 | 0.00079623 | 0.00019955 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1402-25_1_6_load_125 | 107 | 0.00093516 | 0.00023437 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1402-25_1_6_load_126 | 108 | 0.0018192 | 0.00045594 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1402-25_1_6_load_127 | 109 | 0.0014643 | 0.000367 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1402-25_1_6_load_130 | 110 | 0.00067907 | 0.00017019 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1402-25_1_6_load_154 | 113 | 0.00044912 | 0.00011256 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1402-25_1_6_load_132 | 115 | 0.00050628 | 0.00012689 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1402-25_1_6_load_137 | 116 | 0.0026801 | 0.00067168 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1402-25_1_6_load_139 | 117 | 0.0032804 | 0.00082215 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1402-25_1_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.089802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1402-25_1_6_line_1 | NAYY 4x150 SE | 1 | 28 | 0.08227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1402-25_1_6_line_2 | NAYY 4x150 SE | 2 | 3 | 0.026455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1402-25_1_6_line_3 | NAYY 4x150 SE | 3 | 4 | 0.27515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1402-25_1_6_line_4 | NAYY 4x150 SE | 4 | 58 | 0.52374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1402-25_1_6_line_5 | NAYY 4x150 SE | 5 | 6 | 0.035475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1402-25_1_6_line_6 | NAYY 4x150 SE | 5 | 7 | 0.011868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1402-25_1_6_line_7 | NAYY 4x150 SE | 6 | 8 | 0.019826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1402-25_1_6_line_8 | NAYY 4x150 SE | 7 | 9 | 0.022857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1402-25_1_6_line_9 | NAYY 4x150 SE | 8 | 14 | 0.028764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1402-25_1_6_line_10 | NAYY 4x150 SE | 9 | 15 | 0.048324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1402-25_1_6_line_11 | NAYY 4x150 SE | 10 | 11 | 0.1202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1402-25_1_6_line_12 | NAYY 4x150 SE | 10 | 12 | 0.11101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1402-25_1_6_line_13 | NAYY 4x150 SE | 10 | 13 | 0.17645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1402-25_1_6_line_14 | NAYY 4x150 SE | 11 | 61 | 0.012568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1402-25_1_6_line_15 | NAYY 4x150 SE | 12 | 97 | 0.10177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1402-25_1_6_line_16 | NAYY 4x150 SE | 13 | 54 | 0.057875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1402-25_1_6_line_17 | NAYY 4x150 SE | 14 | 16 | 0.023601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1402-25_1_6_line_18 | NAYY 4x150 SE | 15 | 17 | 0.0048724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1402-25_1_6_line_19 | NAYY 4x150 SE | 16 | 71 | 0.028555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1402-25_1_6_line_20 | NAYY 4x150 SE | 17 | 18 | 0.16764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1402-25_1_6_line_21 | NAYY 4x150 SE | 17 | 19 | 0.024008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1402-25_1_6_line_22 | NAYY 4x150 SE | 18 | 20 | 0.026449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1402-25_1_6_line_23 | NAYY 4x150 SE | 18 | 21 | 0.077518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1402-25_1_6_line_24 | NAYY 4x150 SE | 19 | 22 | 0.05169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1402-25_1_6_line_25 | NAYY 4x150 SE | 21 | 23 | 0.082804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1402-25_1_6_line_26 | NAYY 4x150 SE | 22 | 24 | 0.025205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1402-25_1_6_line_27 | NAYY 4x150 SE | 23 | 99 | 0.012937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1402-25_1_6_line_28 | NAYY 4x150 SE | 25 | 26 | 0.025029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1402-25_1_6_line_29 | NAYY 4x150 SE | 25 | 27 | 0.090816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1402-25_1_6_line_30 | NAYY 4x150 SE | 26 | 28 | 0.136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1402-25_1_6_line_31 | NAYY 4x150 SE | 26 | 29 | 0.039015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1402-25_1_6_line_32 | NAYY 4x150 SE | 27 | 30 | 0.03145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1402-25_1_6_line_33 | NAYY 4x150 SE | 27 | 31 | 0.073847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1402-25_1_6_line_34 | NAYY 4x150 SE | 29 | 32 | 0.025641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1402-25_1_6_line_35 | NAYY 4x150 SE | 30 | 33 | 0.0040236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1402-25_1_6_line_36 | NAYY 4x150 SE | 31 | 34 | 0.0072364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1402-25_1_6_line_37 | NAYY 4x150 SE | 31 | 35 | 0.0082562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1402-25_1_6_line_38 | NAYY 4x150 SE | 32 | 36 | 0.12722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_1402-25_1_6_line_39 | NAYY 4x150 SE | 33 | 37 | 0.038946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1402-25_1_6_line_40 | NAYY 4x150 SE | 33 | 38 | 0.0084585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1402-25_1_6_line_41 | NAYY 4x150 SE | 34 | 39 | 0.0021665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1402-25_1_6_line_42 | NAYY 4x150 SE | 35 | 40 | 0.002124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1402-25_1_6_line_43 | NAYY 4x150 SE | 36 | 114 | 0.032252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1402-25_1_6_line_44 | NAYY 4x150 SE | 36 | 61 | 0.091817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_1402-25_1_6_line_45 | NAYY 4x150 SE | 36 | 110 | 0.10334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1402-25_1_6_line_46 | NAYY 4x150 SE | 37 | 42 | 0.010824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1402-25_1_6_line_47 | NAYY 4x150 SE | 37 | 43 | 0.014198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1402-25_1_6_line_48 | NAYY 4x150 SE | 38 | 41 | 0.0034785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1402-25_1_6_line_49 | NAYY 4x150 SE | 39 | 45 | 0.0087294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1402-25_1_6_line_50 | NAYY 4x150 SE | 43 | 44 | 0.0072846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1402-25_1_6_line_51 | NAYY 4x150 SE | 44 | 53 | 0.015022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1402-25_1_6_line_52 | NAYY 4x150 SE | 44 | 51 | 0.018881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1402-25_1_6_line_53 | NAYY 4x150 SE | 45 | 46 | 0.01785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1402-25_1_6_line_54 | NAYY 4x150 SE | 45 | 47 | 0.30641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1402-25_1_6_line_55 | NAYY 4x150 SE | 46 | 48 | 0.013915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1402-25_1_6_line_56 | NAYY 4x150 SE | 49 | 50 | 0.00643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1402-25_1_6_line_57 | NAYY 4x150 SE | 49 | 51 | 0.010124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1402-25_1_6_line_58 | NAYY 4x150 SE | 51 | 52 | 0.014615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1402-25_1_6_line_59 | NAYY 4x150 SE | 54 | 55 | 0.011869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1402-25_1_6_line_60 | NAYY 4x150 SE | 55 | 56 | 0.28458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1402-25_1_6_line_61 | NAYY 4x150 SE | 56 | 57 | 0.014972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1402-25_1_6_line_62 | NAYY 4x150 SE | 57 | 58 | 0.027654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1402-25_1_6_line_63 | NAYY 4x150 SE | 57 | 59 | 0.19675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1402-25_1_6_line_64 | NAYY 4x150 SE | 59 | 60 | 0.022757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1402-25_1_6_line_65 | NAYY 4x150 SE | 61 | 103 | 0.0075025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1402-25_1_6_line_66 | NAYY 4x150 SE | 62 | 63 | 0.022949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1402-25_1_6_line_67 | NAYY 4x150 SE | 63 | 64 | 0.041831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1402-25_1_6_line_68 | NAYY 4x150 SE | 63 | 65 | 0.084596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1402-25_1_6_line_69 | NAYY 4x150 SE | 65 | 86 | 0.011113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1402-25_1_6_line_70 | NAYY 4x150 SE | 65 | 85 | 0.025083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1402-25_1_6_line_71 | NAYY 4x150 SE | 66 | 67 | 0.021478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1402-25_1_6_line_72 | NAYY 4x150 SE | 67 | 68 | 0.038478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_1402-25_1_6_line_73 | NAYY 4x150 SE | 67 | 69 | 0.038229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_1402-25_1_6_line_74 | NAYY 4x150 SE | 68 | 81 | 0.022951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_1402-25_1_6_line_75 | NAYY 4x150 SE | 69 | 77 | 0.025072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_1402-25_1_6_line_76 | NAYY 4x150 SE | 70 | 71 | 0.0063807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1402-25_1_6_line_77 | NAYY 4x150 SE | 70 | 72 | 0.011471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_1402-25_1_6_line_78 | NAYY 4x150 SE | 72 | 73 | 0.037852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_1402-25_1_6_line_79 | NAYY 4x150 SE | 72 | 74 | 0.03593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_1402-25_1_6_line_80 | NAYY 4x150 SE | 73 | 75 | 0.010113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_1402-25_1_6_line_81 | NAYY 4x150 SE | 74 | 76 | 0.010635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
82 | LV_1402-25_1_6_line_82 | NAYY 4x150 SE | 75 | 82 | 0.014187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1402-25_1_6_line_83 | NAYY 4x150 SE | 76 | 84 | 0.0028919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1402-25_1_6_line_84 | NAYY 4x150 SE | 76 | 83 | 0.040347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1402-25_1_6_line_85 | NAYY 4x150 SE | 77 | 78 | 0.023761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
86 | LV_1402-25_1_6_line_86 | NAYY 4x150 SE | 78 | 79 | 0.011593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1402-25_1_6_line_87 | NAYY 4x150 SE | 78 | 80 | 0.0070753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1402-25_1_6_line_88 | NAYY 4x150 SE | 79 | 90 | 0.0050694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1402-25_1_6_line_89 | NAYY 4x150 SE | 80 | 82 | 0.018192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1402-25_1_6_line_90 | NAYY 4x150 SE | 81 | 94 | 0.00075455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1402-25_1_6_line_91 | NAYY 4x150 SE | 84 | 85 | 0.028603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1402-25_1_6_line_92 | NAYY 4x150 SE | 86 | 87 | 0.097725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1402-25_1_6_line_93 | NAYY 4x150 SE | 87 | 88 | 0.028385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1402-25_1_6_line_94 | NAYY 4x150 SE | 88 | 89 | 0.12547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1402-25_1_6_line_95 | NAYY 4x150 SE | 89 | 96 | 0.055141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1402-25_1_6_line_96 | NAYY 4x150 SE | 90 | 91 | 0.024351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1402-25_1_6_line_97 | NAYY 4x150 SE | 91 | 92 | 0.00095112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1402-25_1_6_line_98 | NAYY 4x150 SE | 92 | 93 | 0.024962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1402-25_1_6_line_99 | NAYY 4x150 SE | 94 | 95 | 0.0079112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
100 | LV_1402-25_1_6_line_100 | NAYY 4x150 SE | 95 | 97 | 0.021952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_1402-25_1_6_line_101 | NAYY 4x150 SE | 98 | 99 | 0.013069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1402-25_1_6_line_102 | NAYY 4x150 SE | 99 | 100 | 0.016298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1402-25_1_6_line_103 | NAYY 4x150 SE | 100 | 101 | 0.0038568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1402-25_1_6_line_104 | NAYY 4x150 SE | 101 | 102 | 0.023253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1402-25_1_6_line_105 | NAYY 4x150 SE | 103 | 116 | 0.0065097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1402-25_1_6_line_106 | NAYY 4x150 SE | 104 | 105 | 0.0083707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1402-25_1_6_line_107 | NAYY 4x150 SE | 104 | 106 | 0.017948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1402-25_1_6_line_108 | NAYY 4x150 SE | 105 | 107 | 0.00089926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1402-25_1_6_line_109 | NAYY 4x150 SE | 106 | 108 | 0.016032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1402-25_1_6_line_110 | NAYY 4x150 SE | 107 | 109 | 0.028009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1402-25_1_6_line_111 | NAYY 4x150 SE | 108 | 110 | 0.02434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1402-25_1_6_line_112 | NAYY 4x150 SE | 109 | 111 | 0.11194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1402-25_1_6_line_113 | NAYY 4x150 SE | 111 | 112 | 0.059589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1402-25_1_6_line_114 | NAYY 4x150 SE | 112 | 113 | 0.14186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1402-25_1_6_line_115 | NAYY 4x150 SE | 114 | 115 | 0.027653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1402-25_1_6_line_116 | NAYY 4x150 SE | 116 | 117 | 0.0076014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1402-25_1_6_trafo_114 | 0.25 MVA 20/0.4 kV | 118 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2672155.5555 | 1186382.1298 | 2672093.4256 | 1186446.97
1 | 2672155.5555 | 1186382.1298 | 2672164.0544 | 1186377.0955 | 2672181.175 | 1186367.8963 | 2672200.0524 | 1186358.5627 | 2672228.7141 | 1186344.5647
2 | 2671678.7518 | 1187167.58 | 2671676.5603 | 1187141.2158
3 | 2671676.5603 | 1187141.2158 | 2671678.1387 | 1186866.0717
4 | 2672184.8334 | 1186733.5225 | 2671678.1387 | 1186866.0717
5 | 2673022.3786 | 1186308.1094 | 2673011.1945 | 1186289.073 | 2673008.599 | 1186275.9303
6 | 2673006.2998 | 1186264.2876 | 2673008.599 | 1186275.9303
7 | 2673022.3786 | 1186308.1094 | 2673017.5093 | 1186312.5416 | 2673013.6343 | 1186313.6617 | 2673006.2942 | 1186313.5722 | 2673004.4835 | 1186313.1145
8 | 2673006.0855 | 1186241.805 | 2673004.1507 | 1186253.4105 | 2673006.2998 | 1186264.2876
9 | 2673004.4835 | 1186313.1145 | 2673000.7481 | 1186312.1704 | 2672994.0947 | 1186310.2104 | 2672978.1586 | 1186312.8957 | 2672976.3646 | 1186313.1687
10 | 2673006.0855 | 1186241.805 | 2672985.9013 | 1186259.9143 | 2672974.5834 | 1186265.6131 | 2672966.3462 | 1186267.8483
11 | 2672534.8793 | 1186345.599 | 2672523.221 | 1186332.8281 | 2672512.6609 | 1186339.0151 | 2672509.8159 | 1186330.0754 | 2672475.1053 | 1186298.8926 | 2672465.4861 | 1186306.7809 | 2672449.0541 | 1186297.4878 | 2672445.9333 | 1186296.3839
12 | 2672534.8793 | 1186345.599 | 2672623.5908 | 1186412.3352
13 | 2672534.8793 | 1186345.599 | 2672481.5913 | 1186358.8286 | 2672448.5414 | 1186366.9893 | 2672432.7775 | 1186371.8794 | 2672423.8732 | 1186374.9291 | 2672418.899 | 1186377.3482 | 2672413.4866 | 1186381.2962 | 2672406.657 | 1186386.9614 | 2672398.8381 | 1186394.2935 | 2672384.2216 | 1186405.9015 | 2672375.5614 | 1186412.8349
14 | 2672434.0847 | 1186292.1926 | 2672445.9333 | 1186296.3839
15 | 2672623.5908 | 1186412.3352 | 2672644.8123 | 1186401.6751 | 2672719.2297 | 1186378.2329
16 | 2672327.367 | 1186442.5465 | 2672352.6687 | 1186433.5701 | 2672356.321 | 1186431.2906 | 2672358.9762 | 1186428.799 | 2672366.3786 | 1186420.5613 | 2672369.789 | 1186417.4562 | 2672375.5614 | 1186412.8349
17 | 2672952.8664 | 1186314.8051 | 2672955.7782 | 1186314.6242 | 2672968.0132 | 1186314.4397 | 2672976.3646 | 1186313.1687
18 | 2672961.6438 | 1186269.1243 | 2672966.3462 | 1186267.8483
19 | 2672952.8664 | 1186314.8051 | 2672940.9701 | 1186315.5444 | 2672932.7143 | 1186317.3339 | 2672925.2611 | 1186320.7246
20 | 2672961.6438 | 1186269.1243 | 2672936.7173 | 1186262.4724 | 2672851.226 | 1186284.9234 | 2672838.4095 | 1186287.1133 | 2672822.822 | 1186284.3444 | 2672798.6031 | 1186277.8574
21 | 2672961.6438 | 1186269.1243 | 2672938.335 | 1186274.8763
22 | 2672798.6031 | 1186277.8574 | 2672787.1725 | 1186275.2615 | 2672773.6387 | 1186269.2824
23 | 2672723.6369 | 1186294.5792 | 2672743.8301 | 1186286.9531 | 2672787.2818 | 1186283.2231 | 2672798.6031 | 1186277.8574
24 | 2672888.9759 | 1186289.8241 | 2672896.2016 | 1186286.4046 | 2672916.9507 | 1186280.1534 | 2672938.335 | 1186274.8763
25 | 2672723.6369 | 1186294.5792 | 2672719.9899 | 1186294.5238 | 2672717.8553 | 1186291.8296 | 2672718.1565 | 1186287.7642 | 2672723.556 | 1186263.5376 | 2672723.0247 | 1186254.5036 | 2672717.1648 | 1186243.1147 | 2672717.5432 | 1186233.3246 | 2672714.0572 | 1186226.2893 | 2672707.3162 | 1186223.4486
26 | 2672888.9759 | 1186289.8241 | 2672876.1381 | 1186295.8995 | 2672866.2147 | 1186300.65
27 | 2672695.3949 | 1186218.4249 | 2672707.3162 | 1186223.4486
28 | 2672306.7145 | 1186249.051 | 2672305.136 | 1186244.5293 | 2672302.8304 | 1186238.9204 | 2672299.8252 | 1186233.1029 | 2672296.6436 | 1186227.9949 | 2672295.6224 | 1186226.7509
29 | 2672225.2988 | 1186169.7891 | 2672227.8633 | 1186172.2881 | 2672231.704 | 1186175.9032 | 2672235.9651 | 1186179.4678 | 2672241.6655 | 1186183.9169 | 2672246.4317 | 1186187.3542 | 2672261.6247 | 1186197.5545 | 2672274.2092 | 1186206.3671 | 2672281.0103 | 1186211.9301 | 2672285.9561 | 1186216.2924 | 2672292.5599 | 1186223.0205 | 2672295.6224 | 1186226.7509
30 | 2672306.7145 | 1186249.051 | 2672307.362 | 1186251.6715 | 2672307.9921 | 1186255.7371 | 2672308.5276 | 1186261.9472 | 2672308.5194 | 1186267.0501 | 2672308.2304 | 1186272.0273 | 2672307.1475 | 1186277.6509 | 2672305.2457 | 1186284.1095 | 2672302.726 | 1186290.5496 | 2672299.3213 | 1186296.3341 | 2672295.9274 | 1186301.2294 | 2672292.4352 | 1186305.4119 | 2672287.5328 | 1186310.7337 | 2672281.4862 | 1186316.0194 | 2672272.9197 | 1186322.0641 | 2672262.2999 | 1186328.1618 | 2672228.7141 | 1186344.5647
31 | 2672306.7145 | 1186249.051 | 2672319.8161 | 1186248.5199 | 2672321.9181 | 1186249.5015 | 2672323.2867 | 1186251.1856 | 2672324.4045 | 1186253.4115 | 2672324.8345 | 1186255.7181 | 2672324.4749 | 1186260.2164 | 2672322.8669 | 1186272.1716
32 | 2672225.2988 | 1186169.7891 | 2672214.5689 | 1186182.4672 | 2672212.3479 | 1186181.2175 | 2672206.4748 | 1186183.5036 | 2672200.4857 | 1186183.3758
33 | 2672181.4448 | 1186127.0911 | 2672203.8914 | 1186124.3377 | 2672203.9898 | 1186126.3067 | 2672204.7019 | 1186131.1737 | 2672205.8647 | 1186136.0016 | 2672208.7536 | 1186144.5081 | 2672210.5883 | 1186148.6771 | 2672212.691 | 1186152.7716 | 2672214.8292 | 1186156.4439 | 2672217.3943 | 1186160.1659 | 2672220.1346 | 1186163.9123 | 2672225.2988 | 1186169.7891
34 | 2672315.4744 | 1186296.5069 | 2672318.8688 | 1186289.6772 | 2672320.9015 | 1186283.7649 | 2672322.337 | 1186276.1111 | 2672322.8669 | 1186272.1716
35 | 2672196.5966 | 1186184.4073 | 2672200.4857 | 1186183.3758
36 | 2672181.4448 | 1186127.0911 | 2672179.0009 | 1186120.2798
37 | 2672181.4448 | 1186127.0911 | 2672185.3714 | 1186134.3537
38 | 2672362.3771 | 1186240.8181 | 2672367.4112 | 1186270.074 | 2672367.7776 | 1186278.2721 | 2672366.8852 | 1186283.2865 | 2672365.5499 | 1186288.3289 | 2672362.4073 | 1186293.8942 | 2672358.4736 | 1186298.6162 | 2672352.6554 | 1186302.6705 | 2672346.7692 | 1186305.4122 | 2672321.6337 | 1186313.4913 | 2672317.703 | 1186314.1776 | 2672315.0674 | 1186313.7789 | 2672313.1036 | 1186312.7323 | 2672311.6292 | 1186310.969 | 2672311.0357 | 1186307.6599 | 2672311.678 | 1186304.3991 | 2672315.4744 | 1186296.5069
39 | 2672198.8731 | 1186219.0218 | 2672191.5502 | 1186207.3712 | 2672191.0038 | 1186204.5852 | 2672198.6156 | 1186189.1122 | 2672196.5966 | 1186184.4073
40 | 2672196.5966 | 1186184.4073 | 2672191.7542 | 1186183.4818 | 2672190.3026 | 1186183.6199 | 2672189.6362 | 1186184.4569 | 2672189.6242 | 1186185.4573 | 2672189.6242 | 1186185.4573
41 | 2672179.0009 | 1186120.2798 | 2672178.62 | 1186118.1471
42 | 2672186.6468 | 1186136.0521 | 2672185.3714 | 1186134.3537 | 2672185.3714 | 1186134.3537
43 | 2672362.3771 | 1186240.8181 | 2672366.058 | 1186248.178 | 2672373.5124 | 1186271.0149
44 | 2672434.0847 | 1186292.1926 | 2672415.2435 | 1186270.7189 | 2672392.1019 | 1186254.6187 | 2672366.058 | 1186248.178 | 2672362.3771 | 1186240.8181
45 | 2672362.3771 | 1186240.8181 | 2672332.0883 | 1186170.7111 | 2672313.7693 | 1186150.9207
46 | 2672188.9677 | 1186223.4495 | 2672198.8731 | 1186219.0218
47 | 2672198.8731 | 1186219.0218 | 2672205.2976 | 1186229.2386 | 2672206.5888 | 1186230.9312
48 | 2672189.6242 | 1186185.4573 | 2672191.3685 | 1186188.4669
49 | 2672178.62 | 1186118.1471 | 2672177.7713 | 1186113.3943 | 2672177.6845 | 1186109.4938
50 | 2672211.0071 | 1186236.7229 | 2672206.5888 | 1186230.9312
51 | 2672197.3002 | 1186230.4874 | 2672211.0071 | 1186236.7229
52 | 2672222.656 | 1186251.6054 | 2672211.0071 | 1186236.7229
53 | 2672177.6845 | 1186109.4938 | 2672177.5485 | 1186103.3857 | 2672178.4316 | 1186094.7024 | 2672178.2843 | 1186091.6938
54 | 2672177.6845 | 1186109.4938 | 2671871.2832 | 1186111.7315
55 | 2672178.2843 | 1186091.6938 | 2672178.0825 | 1186087.5717 | 2672176.2598 | 1186077.9551
56 | 2672228.9022 | 1186259.5732 | 2672232.8693 | 1186264.6336
57 | 2672222.656 | 1186251.6054 | 2672228.9022 | 1186259.5732
58 | 2672222.656 | 1186251.6054 | 2672231.2012 | 1186239.7348
59 | 2672316.1811 | 1186446.515 | 2672327.367 | 1186442.5465
60 | 2672316.1811 | 1186446.515 | 2672209.6218 | 1186710.3965
61 | 2672209.6218 | 1186710.3965 | 2672208.1965 | 1186712.7918 | 2672206.3962 | 1186724.8429
62 | 2672184.8334 | 1186733.5225 | 2672191.6191 | 1186733.9823 | 2672202.8186 | 1186732.9055 | 2672204.9824 | 1186731.9088 | 2672205.7561 | 1186729.1276 | 2672206.3962 | 1186724.8429
63 | 2672206.3962 | 1186724.8429 | 2672370.0653 | 1186834.0386
64 | 2672370.0653 | 1186834.0386 | 2672382.7639 | 1186852.2249 | 2672383.2548 | 1186852.5262
65 | 2672434.0847 | 1186292.1926 | 2672432.1682 | 1186296.0717 | 2672430.5782 | 1186298.8208
66 | 2672963.1378 | 1186468.2495 | 2672968.6908 | 1186469.2505 | 2672985.4875 | 1186473.42
67 | 2672963.1378 | 1186468.2495 | 2672956.7148 | 1186509.5841
68 | 2672898.2346 | 1186413.9898 | 2672963.1378 | 1186468.2495
69 | 2672898.2346 | 1186413.9898 | 2672894.7021 | 1186415.2291 | 2672887.3438 | 1186415.6295
70 | 2672898.2346 | 1186413.9898 | 2672902.6341 | 1186412.4462 | 2672911.0601 | 1186405.4446 | 2672915.1397 | 1186396.9041
71 | 2672805.6179 | 1186347.3837 | 2672820.8297 | 1186332.2211
72 | 2672805.6179 | 1186347.3837 | 2672791.823 | 1186355.3652 | 2672770.324 | 1186362.1377
73 | 2672805.6179 | 1186347.3837 | 2672810.8292 | 1186353.0948 | 2672816.1276 | 1186354.7824 | 2672825.5263 | 1186353.7627 | 2672833.4323 | 1186347.4773 | 2672837.6537 | 1186344.1367
74 | 2672770.324 | 1186362.1377 | 2672748.4331 | 1186369.0335
75 | 2672837.6537 | 1186344.1367 | 2672838.5794 | 1186343.4042 | 2672842.8748 | 1186340.9772 | 2672848.5566 | 1186341.8801 | 2672851.4553 | 1186346.9962 | 2672849.9623 | 1186352.4145 | 2672849.3432 | 1186354.002
76 | 2672919.4531 | 1186323.3669 | 2672925.2611 | 1186320.7246
77 | 2672909.0549 | 1186328.2079 | 2672913.2691 | 1186326.1802 | 2672919.4531 | 1186323.3669
78 | 2672909.0549 | 1186328.2079 | 2672878.9259 | 1186342.7277 | 2672876.4383 | 1186346.365
79 | 2672909.0549 | 1186328.2079 | 2672912.4201 | 1186335.7422 | 2672912.8304 | 1186342.7847 | 2672911.6825 | 1186349.319 | 2672911.9009 | 1186358.327 | 2672913.6571 | 1186362.9858
80 | 2672870.7292 | 1186354.7129 | 2672876.4383 | 1186346.365
81 | 2672921.5627 | 1186369.5401 | 2672914.4439 | 1186365.073 | 2672913.6571 | 1186362.9858
82 | 2672870.7292 | 1186354.7129 | 2672862.0654 | 1186365.9476
83 | 2672921.5627 | 1186369.5401 | 2672924.3144 | 1186370.4297
84 | 2672921.5627 | 1186369.5401 | 2672917.5828 | 1186370.5033 | 2672914.5595 | 1186373.1236 | 2672908.3456 | 1186379.5741 | 2672902.1438 | 1186384.4014 | 2672889.5673 | 1186390.7077 | 2672888.2436 | 1186391.0477
85 | 2672841.9705 | 1186376.4204 | 2672842.2588 | 1186372.1659 | 2672849.3432 | 1186354.002
86 | 2672841.9705 | 1186376.4204 | 2672837.3177 | 1186377.4979 | 2672830.5258 | 1186378.0838
87 | 2672841.9705 | 1186376.4204 | 2672845.2766 | 1186377.528 | 2672848.8615 | 1186377.3646
88 | 2672825.4707 | 1186378.463 | 2672829.4112 | 1186378.1799 | 2672830.5258 | 1186378.0838
89 | 2672862.0654 | 1186365.9476 | 2672856.5869 | 1186373.0517 | 2672851.4383 | 1186377.2472 | 2672848.8615 | 1186377.3646
90 | 2672748.4331 | 1186369.0335 | 2672747.7134 | 1186369.2602
91 | 2672924.3144 | 1186370.4297 | 2672925.0334 | 1186372.7954 | 2672923.1732 | 1186379.5434 | 2672918.4836 | 1186389.9035 | 2672915.1397 | 1186396.9041
92 | 2672887.3438 | 1186415.6295 | 2672884.6835 | 1186415.7742 | 2672862.3116 | 1186416.8361 | 2672821.2407 | 1186418.7713 | 2672789.7412 | 1186420.5095
93 | 2672761.3798 | 1186421.5905 | 2672776.8287 | 1186421.222 | 2672789.7412 | 1186420.5095
94 | 2672729.1692 | 1186465.5028 | 2672728.3518 | 1186461.1792 | 2672723.0422 | 1186459.1691 | 2672716.4079 | 1186453.1294 | 2672716.864 | 1186450.7558 | 2672724.2539 | 1186448.622 | 2672725.0096 | 1186445.4627 | 2672719.2198 | 1186441.5123 | 2672714.3291 | 1186433.904 | 2672707.7797 | 1186432.8127 | 2672705.9315 | 1186430.4222 | 2672701.9193 | 1186423.992 | 2672711.3365 | 1186422.0718 | 2672725.2733 | 1186420.6067 | 2672736.3214 | 1186420.7409 | 2672752.1275 | 1186421.8112 | 2672761.3798 | 1186421.5905
95 | 2672729.1692 | 1186465.5028 | 2672773.759 | 1186462.8315 | 2672784.1946 | 1186461.9647
96 | 2672801.1743 | 1186380.089 | 2672808.3691 | 1186379.6918 | 2672825.4707 | 1186378.463
97 | 2672800.2247 | 1186380.1414 | 2672801.1743 | 1186380.089
98 | 2672775.3256 | 1186381.8137 | 2672780.3137 | 1186381.2407 | 2672800.2247 | 1186380.1414
99 | 2672740.1677 | 1186371.6372 | 2672747.7134 | 1186369.2602
100 | 2672740.1677 | 1186371.6372 | 2672719.2297 | 1186378.2329
101 | 2672695.3949 | 1186218.4249 | 2672690.3767 | 1186211.2486 | 2672690.5011 | 1186206.9385
102 | 2672695.3949 | 1186218.4249 | 2672688.3204 | 1186233.107
103 | 2672688.3204 | 1186233.107 | 2672686.6818 | 1186236.5076 | 2672686.6749 | 1186236.5893
104 | 2672684.6292 | 1186259.752 | 2672685.4784 | 1186250.7792 | 2672686.6749 | 1186236.5893
105 | 2672424.4507 | 1186301.0188 | 2672430.5782 | 1186298.8208 | 2672430.5782 | 1186298.8208
106 | 2672288.8607 | 1186099.2483 | 2672286.6878 | 1186093.0842 | 2672286.2087 | 1186091.313
107 | 2672288.8607 | 1186099.2483 | 2672294.8273 | 1186116.1753
108 | 2672285.9739 | 1186090.4449 | 2672286.2087 | 1186091.313
109 | 2672300.1572 | 1186131.2957 | 2672294.8273 | 1186116.1753
110 | 2672285.9739 | 1186090.4449 | 2672284.4158 | 1186084.6852 | 2672282.9764 | 1186075.5958 | 2672283.1523 | 1186069.2386 | 2672284.2821 | 1186062.8582
111 | 2672313.7693 | 1186150.9207 | 2672302.9579 | 1186139.241 | 2672300.1572 | 1186131.2957
112 | 2672355.3816 | 1185981.0251 | 2672345.2816 | 1185984.4718 | 2672341.0073 | 1185987.0439 | 2672337.6082 | 1185989.8268 | 2672334.9041 | 1185993.1961 | 2672330.1902 | 1185999.9432 | 2672325.7543 | 1186007.0605 | 2672321.564 | 1186012.7911 | 2672318.1923 | 1186016.4637 | 2672313.8757 | 1186021.2811 | 2672301.7359 | 1186032.4967 | 2672292.7482 | 1186042.4275 | 2672289.2104 | 1186047.2209 | 2672286.8337 | 1186051.9173 | 2672285.3308 | 1186056.9354 | 2672284.2821 | 1186062.8582
113 | 2672410.3669 | 1185979.7885 | 2672399.5095 | 1185982.1254 | 2672381.6282 | 1185987.8461 | 2672374.9919 | 1185989.478 | 2672368.2488 | 1185989.8412 | 2672364.3274 | 1185989.1045 | 2672361.276 | 1185987.7446 | 2672355.3816 | 1185981.0251
114 | 2672410.3669 | 1185979.7885 | 2672425.845 | 1185980.3204 | 2672455.9751 | 1185982.7972 | 2672482.2966 | 1185985.3059 | 2672493.0129 | 1185987.7036 | 2672496.3391 | 1185989.6895 | 2672498.4418 | 1185993.1391 | 2672498.061 | 1185997.4927 | 2672496.4506 | 1186002.5428 | 2672484.3011 | 1186022.0962 | 2672481.3712 | 1186024.5623 | 2672477.8156 | 1186027.0318 | 2672467.8134 | 1186029.3233
115 | 2672373.5124 | 1186271.0149 | 2672377.3901 | 1186287.9828 | 2672374.2198 | 1186297.7281
116 | 2672417.2957 | 1186303.5853 | 2672424.4507 | 1186301.0188

## bus_geodata
| x | y | coords
0 | 2672093.4256 | 1186446.97
1 | 2672155.5555 | 1186382.1298
2 | 2671678.7518 | 1187167.58
3 | 2671676.5603 | 1187141.2158
4 | 2671678.1387 | 1186866.0717
5 | 2673008.599 | 1186275.9303
6 | 2673022.3786 | 1186308.1094
7 | 2673006.2998 | 1186264.2876
8 | 2673004.4835 | 1186313.1145
9 | 2673006.0855 | 1186241.805
10 | 2672534.8793 | 1186345.599
11 | 2672445.9333 | 1186296.3839
12 | 2672623.5908 | 1186412.3352
13 | 2672375.5614 | 1186412.8349
14 | 2672976.3646 | 1186313.1687
15 | 2672966.3462 | 1186267.8483
16 | 2672952.8664 | 1186314.8051
17 | 2672961.6438 | 1186269.1243
18 | 2672798.6031 | 1186277.8574
19 | 2672938.335 | 1186274.8763
20 | 2672773.6387 | 1186269.2824
21 | 2672723.6369 | 1186294.5792
22 | 2672888.9759 | 1186289.8241
23 | 2672707.3162 | 1186223.4486
24 | 2672866.2147 | 1186300.65
25 | 2672295.6224 | 1186226.7509
26 | 2672306.7145 | 1186249.051
27 | 2672225.2988 | 1186169.7891
28 | 2672228.7141 | 1186344.5647
29 | 2672322.8669 | 1186272.1716
30 | 2672200.4857 | 1186183.3758
31 | 2672181.4448 | 1186127.0911
32 | 2672315.4744 | 1186296.5069
33 | 2672196.5966 | 1186184.4074
34 | 2672179.0009 | 1186120.2798
35 | 2672185.3714 | 1186134.3537
36 | 2672362.3771 | 1186240.8181
37 | 2672198.8731 | 1186219.0218
38 | 2672189.6242 | 1186185.4573
39 | 2672178.62 | 1186118.1471
40 | 2672186.6468 | 1186136.0521
41 | 2672191.3685 | 1186188.4669
42 | 2672188.9677 | 1186223.4495
43 | 2672206.5888 | 1186230.9312
44 | 2672211.0071 | 1186236.7229
45 | 2672177.6845 | 1186109.4938
46 | 2672178.2843 | 1186091.6938
47 | 2671871.2832 | 1186111.7315
48 | 2672176.2598 | 1186077.9551
49 | 2672228.9022 | 1186259.5732
50 | 2672232.8693 | 1186264.6336
51 | 2672222.656 | 1186251.6054
52 | 2672231.2012 | 1186239.7348
53 | 2672197.3002 | 1186230.4874
54 | 2672327.367 | 1186442.5465
55 | 2672316.1811 | 1186446.515
56 | 2672209.6218 | 1186710.3965
57 | 2672206.3962 | 1186724.8429
58 | 2672184.8334 | 1186733.5225
59 | 2672370.0653 | 1186834.0386
60 | 2672383.2548 | 1186852.5262
61 | 2672434.0847 | 1186292.1926
62 | 2672985.4875 | 1186473.42
63 | 2672963.1378 | 1186468.2495
64 | 2672956.7148 | 1186509.5841
65 | 2672898.2346 | 1186413.9898
66 | 2672820.8297 | 1186332.2211
67 | 2672805.6179 | 1186347.3837
68 | 2672770.324 | 1186362.1377
69 | 2672837.6537 | 1186344.1367
70 | 2672919.4531 | 1186323.3669
71 | 2672925.2611 | 1186320.7246
72 | 2672909.0549 | 1186328.2079
73 | 2672876.4383 | 1186346.365
74 | 2672913.6571 | 1186362.9858
75 | 2672870.7292 | 1186354.7129
76 | 2672921.5627 | 1186369.5401
77 | 2672849.3432 | 1186354.002
78 | 2672841.9705 | 1186376.4204
79 | 2672830.5258 | 1186378.0838
80 | 2672848.8615 | 1186377.3646
81 | 2672748.4331 | 1186369.0335
82 | 2672862.0654 | 1186365.9476
83 | 2672888.2436 | 1186391.0477
84 | 2672924.3144 | 1186370.4297
85 | 2672915.1397 | 1186396.9041
86 | 2672887.3438 | 1186415.6295
87 | 2672789.7412 | 1186420.5095
88 | 2672761.3798 | 1186421.5905
89 | 2672729.1692 | 1186465.5028
90 | 2672825.4707 | 1186378.463
91 | 2672801.1743 | 1186380.089
92 | 2672800.2247 | 1186380.1414
93 | 2672775.3256 | 1186381.8137
94 | 2672747.7134 | 1186369.2602
95 | 2672740.1677 | 1186371.6372
96 | 2672784.1946 | 1186461.9647
97 | 2672719.2297 | 1186378.2329
98 | 2672690.5011 | 1186206.9385
99 | 2672695.3949 | 1186218.4249
100 | 2672688.3204 | 1186233.107
101 | 2672686.6749 | 1186236.5893
102 | 2672684.6292 | 1186259.752
103 | 2672430.5782 | 1186298.8208
104 | 2672288.8607 | 1186099.2483
105 | 2672286.2087 | 1186091.313
106 | 2672294.8273 | 1186116.1753
107 | 2672285.9739 | 1186090.4449
108 | 2672300.1572 | 1186131.2957
109 | 2672284.2821 | 1186062.8582
110 | 2672313.7693 | 1186150.9207
111 | 2672355.3816 | 1185981.0251
112 | 2672410.3669 | 1185979.7885
113 | 2672467.8134 | 1186029.3233
114 | 2672373.5124 | 1186271.0149
115 | 2672374.2198 | 1186297.7281
116 | 2672424.4507 | 1186301.0188
117 | 2672417.2957 | 1186303.5853
118 | 2672723.6369 | 1186294.5792

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9797 | -0.14247 | 0.00036258 | 9.087e-05
1 | 0.97975 | -0.14213 | 0.0012111 | 0.00030353
2 | 0.9797 | -0.14366 | 0.00047738 | 0.00011964
3 | 0.97972 | -0.14353 | 0.00049692 | 0.00012454
4 | 0.98011 | -0.1407 | 0.0071791 | 0.0017992
5 | 0.97622 | -0.16671 | 0.0015705 | 0.0003936
6 | 0.97677 | -0.16283 | 0 | 0
7 | 0.97605 | -0.16795 | 0 | 0
8 | 0.97707 | -0.16066 | 0.00092964 | 0.00023299
9 | 0.97572 | -0.17033 | 0 | 0
10 | 0.99599 | -0.027781 | 0 | 0
11 | 0.9925 | -0.052138 | 0.0024961 | 0.00062557
12 | 1 | 0 | -0.21446 | -0.054044
13 | 0.99229 | -0.053921 | 0.0021739 | 0.00054483
14 | 0.97752 | -0.15742 | 0.00079163 | 0.0001984
15 | 0.97502 | -0.17537 | 0.0013405 | 0.00033597
16 | 0.9779 | -0.15469 | 0.0023431 | 0.00058724
17 | 0.97495 | -0.17585 | 0 | 0
18 | 0.97266 | -0.19233 | 0 | 0
19 | 0.97461 | -0.17832 | 0.0042867 | 0.0010743
20 | 0.97233 | -0.1947 | 0.0085133 | 0.0021336
21 | 0.97208 | -0.19648 | 0 | 0
22 | 0.97419 | -0.18129 | 0.0024263 | 0.0006081
23 | 0.97085 | -0.20534 | 0.00093643 | 0.00023469
24 | 0.97408 | -0.1821 | 0.0030477 | 0.00076382
25 | 0.98033 | -0.13791 | 0.00059456 | 0.00014901
26 | 0.98148 | -0.12976 | 0 | 0
27 | 0.97625 | -0.16708 | 0 | 0
28 | 0.97994 | -0.14077 | 0.0062066 | 0.0015555
29 | 0.98371 | -0.11394 | 0.00052598 | 0.00013182
30 | 0.97574 | -0.17071 | 0.0024554 | 0.00061538
31 | 0.97411 | -0.1824 | 0 | 0
32 | 0.98519 | -0.10345 | 0 | 0
33 | 0.97569 | -0.17107 | 0 | 0
34 | 0.97396 | -0.1835 | 0.0014014 | 0.00035122
35 | 0.97405 | -0.18286 | 0.0012593 | 0.00031561
36 | 0.98887 | -0.077544 | 0 | 0
37 | 0.97533 | -0.17364 | 0 | 0
38 | 0.97566 | -0.17127 | 0.0010054 | 0.00025198
39 | 0.97392 | -0.18379 | 0.00572 | 0.0014336
40 | 0.97404 | -0.18295 | 0.0040749 | 0.0010213
41 | 0.97565 | -0.17132 | 0.0012729 | 0.00031902
42 | 0.97532 | -0.17372 | 0.00070854 | 0.00017758
43 | 0.97522 | -0.17447 | 0.00088196 | 0.00022104
44 | 0.97517 | -0.17483 | 0 | 0
45 | 0.97383 | -0.18446 | 0.00074348 | 0.00018633
46 | 0.97371 | -0.18531 | 0.0023447 | 0.00058764
47 | 0.97292 | -0.19103 | 0.0020201 | 0.00050629
48 | 0.97366 | -0.18563 | 0.0021662 | 0.00054291
49 | 0.97501 | -0.17598 | 0.0011532 | 0.00028902
50 | 0.97499 | -0.17612 | 0.00216 | 0.00054134
51 | 0.97506 | -0.17562 | 0 | 0
52 | 0.97504 | -0.17573 | 0.000704 | 0.00017644
53 | 0.97515 | -0.17493 | 0.00066576 | 0.00016686
54 | 0.99125 | -0.061253 | 0.0012009 | 0.00030098
55 | 0.99106 | -0.062614 | 0.00095363 | 0.000239
56 | 0.98684 | -0.092564 | 0.0010117 | 0.00025356
57 | 0.98664 | -0.093989 | 0.00054514 | 0.00013663
58 | 0.98632 | -0.096324 | 0 | 0
59 | 0.98651 | -0.094993 | 0 | 0
60 | 0.98649 | -0.095107 | 0.00048639 | 0.0001219
61 | 0.99215 | -0.054588 | 0 | 0
62 | 0.9718 | -0.19845 | 0.0068096 | 0.0017067
63 | 0.97203 | -0.1968 | 0.0015774 | 0.00039533
64 | 0.97187 | -0.19792 | 0.0025363 | 0.00063567
65 | 0.97338 | -0.18704 | 0.013941 | 0.0034938
66 | 0.98752 | -0.086604 | 0.0049755 | 0.001247
67 | 0.98767 | -0.085511 | 0 | 0
68 | 0.98997 | -0.069461 | 0.0030361 | 0.00076091
69 | 0.98549 | -0.10088 | 0.0013076 | 0.00032772
70 | 0.97851 | -0.15035 | 0.0013669 | 0.00034258
71 | 0.97839 | -0.15117 | 0.0013848 | 0.00034708
72 | 0.97872 | -0.14883 | 0 | 0
73 | 0.98043 | -0.13667 | 0.0023341 | 0.00058498
74 | 0.97777 | -0.15562 | 0.0012406 | 0.00031093
75 | 0.9809 | -0.13334 | 0 | 0
76 | 0.97749 | -0.15759 | 0 | 0
77 | 0.98407 | -0.11088 | 0.002353 | 0.00058973
78 | 0.98275 | -0.12019 | 0 | 0
79 | 0.9825 | -0.122 | 0.00147 | 0.00036843
80 | 0.98241 | -0.1226 | 0.0018052 | 0.00045242
81 | 0.99137 | -0.059686 | 0.0028659 | 0.00071825
82 | 0.98156 | -0.12869 | 0.0019709 | 0.00049396
83 | 0.97736 | -0.15853 | 0.0022367 | 0.00056056
84 | 0.97728 | -0.15913 | 0.00073109 | 0.00018323
85 | 0.97518 | -0.17416 | 0.0013019 | 0.00032628
86 | 0.97299 | -0.18985 | 0.013957 | 0.003498
87 | 0.97156 | -0.2002 | 0.0031712 | 0.00079478
88 | 0.97127 | -0.20226 | 0.0040311 | 0.0010103
89 | 0.97076 | -0.20599 | 0 | 0
90 | 0.9824 | -0.12272 | 0.0031182 | 0.00078149
91 | 0.98203 | -0.12538 | 0.0031182 | 0.00078149
92 | 0.98202 | -0.12545 | 0.0028263 | 0.00070835
93 | 0.98185 | -0.12664 | 0.0045948 | 0.0011516
94 | 0.99142 | -0.059358 | 0.0022498 | 0.00056386
95 | 0.99192 | -0.055859 | 0.0020853 | 0.00052263
96 | 0.97053 | -0.20763 | 0.0028017 | 0.00070216
97 | 0.99333 | -0.046012 | 0.0021287 | 0.0005335
98 | 0.97066 | -0.20672 | 0.00085395 | 0.00021402
99 | 0.97068 | -0.2066 | 0 | 0
100 | 0.97048 | -0.20804 | 0.0020532 | 0.00051459
101 | 0.97044 | -0.2083 | 0.00095559 | 0.00023949
102 | 0.97026 | -0.20961 | 0.0053165 | 0.0013324
103 | 0.99206 | -0.055236 | 0.0025664 | 0.0006432
104 | 0.98698 | -0.091008 | 0.0014089 | 0.00035311
105 | 0.98693 | -0.091364 | 0.001268 | 0.00031778
106 | 0.98713 | -0.089986 | 0.00079623 | 0.00019955
107 | 0.98693 | -0.091391 | 0.00093516 | 0.00023437
108 | 0.98727 | -0.088942 | 0.0018192 | 0.00045594
109 | 0.98685 | -0.091949 | 0.0014643 | 0.000367
110 | 0.98756 | -0.086905 | 0.00067907 | 0.00017019
111 | 0.98678 | -0.092492 | 0 | 0
112 | 0.98674 | -0.092777 | 0 | 0
113 | 0.98665 | -0.09344 | 0.00044912 | 0.00011256
114 | 0.98885 | -0.077712 | 0 | 0
115 | 0.98883 | -0.077855 | 0.00050628 | 0.00012689
116 | 0.992 | -0.05563 | 0.0026801 | 0.00067168
117 | 0.99197 | -0.055883 | 0.0032804 | 0.00082215
118 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00036258 | -9.087e-05 | 0.00036259 | 8.9746e-05 | 1.6982e-08 | -1.1243e-06 | 0.0005507 | 0.00055029 | 0.0005507 | 0.9797 | -0.14247 | 0.97975 | -0.14213 | 0.20396
1 | -0.0015737 | -0.00039327 | 0.001574 | 0.00039235 | 2.9311e-07 | -9.2351e-07 | 0.0023897 | 0.0023893 | 0.0023897 | 0.97975 | -0.14213 | 0.97994 | -0.14077 | 0.88506
2 | -0.00047738 | -0.00011964 | 0.00047739 | 0.00011931 | 8.6773e-09 | -3.2979e-07 | 0.00072507 | 0.00072495 | 0.00072507 | 0.9797 | -0.14366 | 0.97972 | -0.14353 | 0.26854
3 | -0.00097431 | -0.00024385 | 0.00097469 | 0.00024053 | 3.756e-07 | -3.3217e-06 | 0.0014797 | 0.0014785 | 0.0014797 | 0.97972 | -0.14353 | 0.98011 | -0.1407 | 0.54803
4 | -0.0081538 | -0.0020398 | 0.0082038 | 0.0020524 | 5.0062e-05 | 1.2612e-05 | 0.012378 | 0.012375 | 0.012378 | 0.98011 | -0.1407 | 0.98632 | -0.096324 | 4.5844
5 | -0.031412 | -0.0078748 | 0.031429 | 0.00788 | 1.6917e-05 | 5.1751e-06 | 0.047881 | 0.047881 | 0.047881 | 0.97622 | -0.16671 | 0.97677 | -0.16283 | 5.9113
6 | 0.029842 | 0.0074812 | -0.029837 | -0.0074797 | 5.1075e-06 | 1.5194e-06 | 0.045488 | 0.045488 | 0.045488 | 0.97622 | -0.16671 | 0.97605 | -0.16795 | 5.6158
7 | -0.031429 | -0.00788 | 0.031439 | 0.0078829 | 9.4542e-06 | 2.8915e-06 | 0.047881 | 0.047881 | 0.047881 | 0.97677 | -0.16283 | 0.97707 | -0.16066 | 5.9112
8 | 0.029837 | 0.0074797 | -0.029827 | -0.0074767 | 9.8372e-06 | 2.9268e-06 | 0.045488 | 0.045488 | 0.045488 | 0.97605 | -0.16795 | 0.97572 | -0.17033 | 5.6158
9 | -0.032368 | -0.0081158 | 0.032383 | 0.0081204 | 1.4539e-05 | 4.5108e-06 | 0.049296 | 0.049296 | 0.049296 | 0.97707 | -0.16066 | 0.97752 | -0.15742 | 6.086
10 | 0.029827 | 0.0074767 | -0.029806 | -0.0074706 | 2.0798e-05 | 6.1899e-06 | 0.045488 | 0.045489 | 0.045489 | 0.97572 | -0.17033 | 0.97502 | -0.17537 | 5.6159
11 | 0.060911 | 0.015357 | -0.060704 | -0.015282 | 0.0002072 | 7.5015e-05 | 0.091034 | 0.091036 | 0.091036 | 0.99599 | -0.027781 | 0.9925 | -0.052138 | 11.239
12 | -0.075602 | -0.019041 | 0.075896 | 0.01915 | 0.00029474 | 0.00010901 | 0.11298 | 0.11298 | 0.11298 | 0.99599 | -0.027781 | 1 | 0 | 13.9483
13 | 0.01469 | 0.0036832 | -0.014637 | -0.0036651 | 5.3039e-05 | 1.8112e-05 | 0.021948 | 0.021949 | 0.021949 | 0.99599 | -0.027781 | 0.99229 | -0.053921 | 8.1291
14 | 0.058208 | 0.014657 | -0.058188 | -0.01465 | 1.992e-05 | 7.1745e-06 | 0.087293 | 0.087293 | 0.087293 | 0.9925 | -0.052138 | 0.99215 | -0.054588 | 10.777
15 | 0.13776 | 0.034894 | -0.13687 | -0.034555 | 0.00089063 | 0.00033857 | 0.20512 | 0.20512 | 0.20512 | 1 | 0 | 0.99333 | -0.046012 | 25.3233
16 | 0.012463 | 0.0031203 | -0.012451 | -0.0031162 | 1.2614e-05 | 4.1045e-06 | 0.018689 | 0.018689 | 0.018689 | 0.99229 | -0.053921 | 0.99125 | -0.061253 | 6.9218
17 | -0.033175 | -0.0083188 | 0.033187 | 0.0083227 | 1.252e-05 | 3.9274e-06 | 0.050501 | 0.050501 | 0.050501 | 0.97752 | -0.15742 | 0.9779 | -0.15469 | 6.2347
18 | 0.028466 | 0.0071346 | -0.028464 | -0.007134 | 1.9127e-06 | 5.5335e-07 | 0.043443 | 0.043443 | 0.043443 | 0.97502 | -0.17537 | 0.97495 | -0.17585 | 5.3633
19 | -0.03553 | -0.0089099 | 0.035548 | 0.0089155 | 1.7362e-05 | 5.6023e-06 | 0.054066 | 0.054066 | 0.054066 | 0.9779 | -0.15469 | 0.97839 | -0.15117 | 6.6748
20 | 0.018697 | 0.0046867 | -0.018654 | -0.0046745 | 4.2595e-05 | 1.2212e-05 | 0.028537 | 0.028538 | 0.028538 | 0.97495 | -0.17585 | 0.97266 | -0.19233 | 5.2849
21 | 0.0097666 | 0.0024473 | -0.0097633 | -0.0024463 | 3.3287e-06 | 9.8099e-07 | 0.014906 | 0.014906 | 0.014906 | 0.97495 | -0.17585 | 0.97461 | -0.17832 | 5.5208
22 | 0.0085161 | 0.0021344 | -0.0085133 | -0.0021336 | 2.8014e-06 | 7.4929e-07 | 0.013028 | 0.013028 | 0.013028 | 0.97266 | -0.19233 | 0.97233 | -0.1947 | 4.8253
23 | 0.010138 | 0.0025402 | -0.010133 | -0.0025398 | 5.8183e-06 | 3.1469e-07 | 0.01551 | 0.015511 | 0.015511 | 0.97266 | -0.19233 | 0.97208 | -0.19648 | 2.8723
24 | 0.0054766 | 0.001372 | -0.0054744 | -0.0013717 | 2.2551e-06 | 2.2348e-07 | 0.0083614 | 0.0083616 | 0.0083616 | 0.97461 | -0.17832 | 0.97419 | -0.18129 | 3.0969
25 | 0.010133 | 0.0025398 | -0.01012 | -0.0025361 | 1.2431e-05 | 3.7559e-06 | 0.015511 | 0.015511 | 0.015511 | 0.97208 | -0.19648 | 0.97085 | -0.20534 | 5.7448
26 | 0.003048 | 0.00076364 | -0.0030477 | -0.00076382 | 3.409e-07 | -1.8267e-07 | 0.0046556 | 0.0046557 | 0.0046557 | 0.97419 | -0.18129 | 0.97408 | -0.1821 | 1.7243
27 | 0.0091837 | 0.0023014 | -0.0091821 | -0.0023009 | 1.5994e-06 | 4.552e-07 | 0.014076 | 0.014076 | 0.014076 | 0.97085 | -0.20534 | 0.97068 | -0.2066 | 5.2133
28 | -0.031515 | -0.0079139 | 0.03155 | 0.0079273 | 3.5745e-05 | 1.3432e-05 | 0.047841 | 0.047841 | 0.047841 | 0.98033 | -0.13791 | 0.98148 | -0.12976 | 17.7188
29 | 0.03092 | 0.0077649 | -0.030795 | -0.007718 | 0.00012486 | 4.6881e-05 | 0.046938 | 0.046939 | 0.046939 | 0.98033 | -0.13791 | 0.97625 | -0.16708 | 17.3847
30 | 0.0077924 | 0.0019507 | -0.0077806 | -0.0019479 | 1.1844e-05 | 2.8393e-06 | 0.011813 | 0.011814 | 0.011814 | 0.98148 | -0.12976 | 0.97994 | -0.14077 | 4.3755
31 | -0.039343 | -0.009878 | 0.039429 | 0.0099109 | 8.6635e-05 | 3.2827e-05 | 0.059654 | 0.059654 | 0.059654 | 0.98148 | -0.12976 | 0.98371 | -0.11394 | 22.0941
32 | 0.011017 | 0.0027601 | -0.011011 | -0.0027584 | 5.5337e-06 | 1.7353e-06 | 0.016792 | 0.016792 | 0.016792 | 0.97625 | -0.16708 | 0.97574 | -0.17071 | 6.2193
33 | 0.019778 | 0.0049579 | -0.019736 | -0.0049427 | 4.188e-05 | 1.5186e-05 | 0.030147 | 0.030147 | 0.030147 | 0.97625 | -0.16708 | 0.97411 | -0.1824 | 11.1656
34 | -0.039955 | -0.010043 | 0.040014 | 0.010065 | 5.8466e-05 | 2.2161e-05 | 0.06045 | 0.060449 | 0.06045 | 0.98371 | -0.11394 | 0.98519 | -0.10345 | 22.3887
35 | 0.008556 | 0.002143 | -0.0085556 | -0.0021429 | 4.2743e-07 | 1.1414e-07 | 0.013048 | 0.013048 | 0.013048 | 0.97574 | -0.17071 | 0.97569 | -0.17107 | 4.8324
36 | 0.014402 | 0.0036058 | -0.0144 | -0.003605 | 2.1852e-06 | 7.5038e-07 | 0.021998 | 0.021998 | 0.021998 | 0.97411 | -0.1824 | 0.97396 | -0.1835 | 8.1475
37 | 0.0053346 | 0.0013369 | -0.0053342 | -0.0013369 | 3.421e-07 | 2.8806e-08 | 0.0081489 | 0.0081489 | 0.0081489 | 0.97411 | -0.1824 | 0.97405 | -0.18286 | 3.0181
38 | -0.040014 | -0.010065 | 0.040159 | 0.010117 | 0.00014504 | 5.2532e-05 | 0.060449 | 0.060448 | 0.060449 | 0.98519 | -0.10345 | 0.98887 | -0.077544 | 11.1943
39 | 0.0062772 | 0.001572 | -0.006275 | -0.0015716 | 2.2271e-06 | 3.7035e-07 | 0.0095729 | 0.0095731 | 0.0095731 | 0.97569 | -0.17107 | 0.97533 | -0.17364 | 3.5456
40 | 0.0022784 | 0.00057088 | -0.0022783 | -0.00057096 | 6.3726e-08 | -8.1127e-08 | 0.0034747 | 0.0034747 | 0.0034747 | 0.97569 | -0.17107 | 0.97566 | -0.17127 | 1.2869
41 | 0.012998 | 0.0032538 | -0.012998 | -0.0032536 | 5.3306e-07 | 1.7806e-07 | 0.019857 | 0.019857 | 0.019857 | 0.97396 | -0.1835 | 0.97392 | -0.18379 | 7.3546
42 | 0.0040749 | 0.0010213 | -0.0040749 | -0.0010213 | 5.136e-08 | -6.6833e-09 | 0.0062251 | 0.0062251 | 0.0062251 | 0.97405 | -0.18286 | 0.97404 | -0.18295 | 2.3056
43 | 0.0005063 | 0.00012613 | -0.00050629 | -0.00012654 | 1.1675e-08 | -4.0926e-07 | 0.00076159 | 0.00076174 | 0.00076174 | 0.98887 | -0.077544 | 0.98885 | -0.077712 | 0.28213
44 | -0.049501 | -0.012454 | 0.04966 | 0.012512 | 0.00015901 | 5.8795e-05 | 0.074504 | 0.074503 | 0.074504 | 0.98887 | -0.077544 | 0.99215 | -0.054588 | 13.797
45 | 0.0088358 | 0.00221 | -0.0088244 | -0.002207 | 1.1397e-05 | 3.0594e-06 | 0.013294 | 0.013295 | 0.013295 | 0.98887 | -0.077544 | 0.98756 | -0.086905 | 4.924
46 | 0.00070854 | 0.00017744 | -0.00070854 | -0.00017758 | 7.8922e-09 | -1.3205e-07 | 0.0010809 | 0.001081 | 0.001081 | 0.97533 | -0.17364 | 0.97532 | -0.17372 | 0.40037
47 | 0.0055664 | 0.0013942 | -0.0055658 | -0.0013941 | 6.3891e-07 | 6.8567e-08 | 0.0084921 | 0.0084922 | 0.0084922 | 0.97533 | -0.17364 | 0.97522 | -0.17447 | 3.1453
48 | 0.0012729 | 0.00031898 | -0.0012729 | -0.00031902 | 8.181e-09 | -4.0295e-08 | 0.0019414 | 0.0019414 | 0.0019414 | 0.97566 | -0.17127 | 0.97565 | -0.17132 | 0.71904
49 | 0.0072777 | 0.0018201 | -0.007277 | -0.0018199 | 6.7331e-07 | 1.5035e-07 | 0.011118 | 0.011118 | 0.011118 | 0.97392 | -0.18379 | 0.97383 | -0.18446 | 4.1178
50 | 0.0046838 | 0.0011731 | -0.0046836 | -0.0011731 | 2.3215e-07 | -1.5961e-09 | 0.0071465 | 0.0071465 | 0.0071465 | 0.97522 | -0.17447 | 0.97517 | -0.17483 | 2.6469
51 | 0.00066577 | 0.00016667 | -0.00066576 | -0.00016686 | 9.6737e-09 | -1.8369e-07 | 0.0010158 | 0.0010159 | 0.0010159 | 0.97517 | -0.17483 | 0.97515 | -0.17493 | 0.37626
52 | 0.0040178 | 0.0010064 | -0.0040174 | -0.0010065 | 4.4282e-07 | -6.5212e-08 | 0.0061307 | 0.0061307 | 0.0061307 | 0.97517 | -0.17483 | 0.97506 | -0.17562 | 2.2706
53 | 0.0045116 | 0.0011304 | -0.004511 | -0.0011304 | 5.2932e-07 | -1.8468e-08 | 0.0068936 | 0.0068937 | 0.0068937 | 0.97383 | -0.18446 | 0.97371 | -0.18531 | 2.5532
54 | 0.002022 | 0.00050319 | -0.0020201 | -0.00050629 | 1.8244e-06 | -3.107e-06 | 0.0030883 | 0.0030897 | 0.0030897 | 0.97383 | -0.18446 | 0.97292 | -0.19103 | 1.1443
55 | 0.0021663 | 0.00054277 | -0.0021662 | -0.00054291 | 9.516e-08 | -1.3647e-07 | 0.0033105 | 0.0033106 | 0.0033106 | 0.97371 | -0.18531 | 0.97366 | -0.18563 | 1.2261
56 | 0.00216 | 0.00054128 | -0.00216 | -0.00054134 | 4.3602e-08 | -6.3422e-08 | 0.0032965 | 0.0032965 | 0.0032965 | 0.97501 | -0.17598 | 0.97499 | -0.17612 | 1.2209
57 | -0.0033132 | -0.0008303 | 0.0033134 | 0.00083023 | 1.6152e-07 | -6.4148e-08 | 0.0050565 | 0.0050564 | 0.0050565 | 0.97501 | -0.17598 | 0.97506 | -0.17562 | 1.8728
58 | 0.00070401 | 0.00017626 | -0.000704 | -0.00017644 | 1.0526e-08 | -1.7824e-07 | 0.0010743 | 0.0010744 | 0.0010744 | 0.97506 | -0.17562 | 0.97504 | -0.17573 | 0.39792
59 | 0.01125 | 0.0028152 | -0.011248 | -0.0028145 | 2.1118e-06 | 6.5928e-07 | 0.016886 | 0.016886 | 0.016886 | 0.99125 | -0.061253 | 0.99106 | -0.062614 | 6.2541
60 | 0.010294 | 0.0025755 | -0.010252 | -0.0025629 | 4.2417e-05 | 1.2663e-05 | 0.015454 | 0.015456 | 0.015456 | 0.99106 | -0.062614 | 0.98684 | -0.092564 | 5.7243
61 | 0.0092399 | 0.0023093 | -0.0092381 | -0.0023088 | 1.8129e-06 | 5.0603e-07 | 0.01393 | 0.01393 | 0.01393 | 0.98684 | -0.092564 | 0.98664 | -0.093989 | 5.1593
62 | 0.0082065 | 0.0020531 | -0.0082038 | -0.0020524 | 2.6428e-06 | 6.634e-07 | 0.012375 | 0.012375 | 0.012375 | 0.98664 | -0.093989 | 0.98632 | -0.096324 | 4.5835
63 | 0.00048646 | 0.00011913 | -0.0004864 | -0.00012161 | 6.5987e-08 | -2.487e-06 | 0.00073268 | 0.00073357 | 0.00073357 | 0.98664 | -0.093989 | 0.98651 | -0.094993 | 0.27169
64 | 0.0004864 | 0.00012161 | -0.00048639 | -0.0001219 | 7.6426e-09 | -2.8761e-07 | 0.00073357 | 0.00073367 | 0.00073367 | 0.98651 | -0.094993 | 0.98649 | -0.095107 | 0.27173
65 | 0.0085281 | 0.0021372 | -0.0085273 | -0.002137 | 7.6587e-07 | 1.9769e-07 | 0.01279 | 0.01279 | 0.01279 | 0.99215 | -0.054588 | 0.99206 | -0.055236 | 4.7372
66 | -0.0068096 | -0.0017067 | 0.0068112 | 0.001707 | 1.5569e-06 | 3.144e-07 | 0.010427 | 0.010427 | 0.010427 | 0.9718 | -0.19845 | 0.97203 | -0.1968 | 3.8618
67 | 0.0025367 | 0.0006353 | -0.0025363 | -0.00063567 | 3.9361e-07 | -3.6704e-07 | 0.0038832 | 0.0038833 | 0.0038833 | 0.97203 | -0.1968 | 0.97187 | -0.19792 | 1.4383
68 | -0.010925 | -0.0027376 | 0.01094 | 0.0027422 | 1.4765e-05 | 4.6289e-06 | 0.016725 | 0.016724 | 0.016725 | 0.97203 | -0.1968 | 0.97338 | -0.18704 | 6.1943
69 | 0.023989 | 0.0060119 | -0.023979 | -0.0060085 | 9.3254e-06 | 3.4486e-06 | 0.036672 | 0.036672 | 0.036672 | 0.97338 | -0.18704 | 0.97299 | -0.18985 | 13.5822
70 | -0.048869 | -0.012248 | 0.048957 | 0.012281 | 8.7354e-05 | 3.3285e-05 | 0.074707 | 0.074707 | 0.074707 | 0.97338 | -0.18704 | 0.97518 | -0.17416 | 27.6693
71 | -0.0049755 | -0.001247 | 0.0049763 | 0.001247 | 7.5331e-07 | 1.4906e-08 | 0.0074972 | 0.0074971 | 0.0074972 | 0.98752 | -0.086604 | 0.98767 | -0.085511 | 2.7768
72 | -0.12379 | -0.031187 | 0.12407 | 0.031292 | 0.00027856 | 0.00010566 | 0.18656 | 0.18656 | 0.18656 | 0.98767 | -0.085511 | 0.98997 | -0.069461 | 23.0322
73 | 0.11882 | 0.02994 | -0.11856 | -0.029843 | 0.00025496 | 9.6598e-05 | 0.17906 | 0.17906 | 0.17906 | 0.98767 | -0.085511 | 0.98549 | -0.10088 | 22.1067
74 | -0.12711 | -0.032053 | 0.12728 | 0.032119 | 0.00017438 | 6.6183e-05 | 0.19112 | 0.19112 | 0.19112 | 0.98997 | -0.069461 | 0.99137 | -0.059686 | 23.5956
75 | 0.11725 | 0.029515 | -0.11709 | -0.029453 | 0.00016354 | 6.1945e-05 | 0.17709 | 0.17709 | 0.17709 | 0.98549 | -0.10088 | 0.98407 | -0.11088 | 21.863
76 | 0.036937 | 0.009264 | -0.036932 | -0.0092626 | 4.1877e-06 | 1.3702e-06 | 0.056172 | 0.056172 | 0.056172 | 0.97851 | -0.15035 | 0.97839 | -0.15117 | 6.9348
77 | -0.038303 | -0.0096066 | 0.038312 | 0.0096092 | 8.0955e-06 | 2.6813e-06 | 0.05825 | 0.05825 | 0.05825 | 0.97851 | -0.15035 | 0.97872 | -0.14883 | 7.1914
78 | -0.092961 | -0.023339 | 0.093118 | 0.023398 | 0.0001573 | 5.9071e-05 | 0.14135 | 0.14135 | 0.14135 | 0.97872 | -0.14883 | 0.98043 | -0.13667 | 17.4505
79 | 0.054649 | 0.01373 | -0.054598 | -0.013711 | 5.1608e-05 | 1.8496e-05 | 0.083099 | 0.083099 | 0.083099 | 0.97872 | -0.14883 | 0.97777 | -0.15562 | 10.2592
80 | -0.095452 | -0.023983 | 0.095497 | 0.024 | 4.4162e-05 | 1.6602e-05 | 0.14489 | 0.14489 | 0.14489 | 0.98043 | -0.13667 | 0.9809 | -0.13334 | 17.8878
81 | 0.053357 | 0.0134 | -0.053343 | -0.013395 | 1.4589e-05 | 5.2112e-06 | 0.081211 | 0.081212 | 0.081212 | 0.97777 | -0.15562 | 0.97749 | -0.15759 | 10.0261
82 | -0.095497 | -0.024 | 0.095558 | 0.024023 | 6.1951e-05 | 2.329e-05 | 0.14489 | 0.14489 | 0.14489 | 0.9809 | -0.13334 | 0.98156 | -0.12869 | 17.8878
83 | 0.051106 | 0.012835 | -0.051095 | -0.012831 | 1.0924e-05 | 4.1654e-06 | 0.077806 | 0.077807 | 0.077807 | 0.97749 | -0.15759 | 0.97728 | -0.15913 | 28.8172
84 | 0.002237 | 0.00056017 | -0.0022367 | -0.00056056 | 2.9193e-07 | -3.9342e-07 | 0.0034051 | 0.0034053 | 0.0034053 | 0.97749 | -0.15759 | 0.97736 | -0.15853 | 1.2612
85 | 0.11474 | 0.028864 | -0.11459 | -0.028807 | 0.00014883 | 5.6338e-05 | 0.17353 | 0.17353 | 0.17353 | 0.98407 | -0.11088 | 0.98275 | -0.12019 | 21.4238
86 | 0.015137 | 0.0037943 | -0.015134 | -0.0037929 | 3.8003e-06 | 1.3148e-06 | 0.02292 | 0.02292 | 0.02292 | 0.98275 | -0.12019 | 0.9825 | -0.122 | 8.4889
87 | 0.099451 | 0.025013 | -0.099417 | -0.025 | 3.3384e-05 | 1.2571e-05 | 0.15061 | 0.15061 | 0.15061 | 0.98275 | -0.12019 | 0.98241 | -0.1226 | 18.5942
88 | 0.013664 | 0.0034245 | -0.013662 | -0.0034241 | 1.3546e-06 | 4.5682e-07 | 0.020694 | 0.020694 | 0.020694 | 0.9825 | -0.122 | 0.9824 | -0.12272 | 7.6644
89 | 0.097612 | 0.024548 | -0.097529 | -0.024517 | 8.2748e-05 | 3.1136e-05 | 0.14788 | 0.14788 | 0.14788 | 0.98241 | -0.1226 | 0.98156 | -0.12869 | 18.2566
90 | -0.13015 | -0.032838 | 0.13015 | 0.03284 | 5.9939e-06 | 2.2762e-06 | 0.19543 | 0.19543 | 0.19543 | 0.99137 | -0.059686 | 0.99142 | -0.059358 | 24.1266
91 | 0.050364 | 0.012648 | -0.050259 | -0.012608 | 0.00010498 | 4.0019e-05 | 0.076693 | 0.076693 | 0.076693 | 0.97728 | -0.15913 | 0.97518 | -0.17416 | 28.405
92 | 0.010022 | 0.0025105 | -0.010008 | -0.0025062 | 1.4326e-05 | 4.2979e-06 | 0.015327 | 0.015327 | 0.015327 | 0.97299 | -0.18985 | 0.97156 | -0.2002 | 5.6768
93 | 0.0068368 | 0.0017114 | -0.0068349 | -0.001711 | 1.9418e-06 | 3.9544e-07 | 0.01047 | 0.01047 | 0.01047 | 0.97156 | -0.2002 | 0.97127 | -0.20226 | 3.878
94 | 0.0028037 | 0.00070073 | -0.0028023 | -0.00070172 | 1.4443e-06 | -9.9656e-07 | 0.0042947 | 0.0042953 | 0.0042953 | 0.97127 | -0.20226 | 0.97076 | -0.20599 | 1.5908
95 | 0.0028023 | 0.00070172 | -0.0028017 | -0.00070216 | 6.3484e-07 | -4.3739e-07 | 0.0042953 | 0.0042955 | 0.0042955 | 0.97076 | -0.20599 | 0.97053 | -0.20763 | 1.5909
96 | 0.010544 | 0.0026426 | -0.01054 | -0.0026414 | 3.8758e-06 | 1.1825e-06 | 0.015971 | 0.015971 | 0.015971 | 0.9824 | -0.12272 | 0.98203 | -0.12538 | 5.9151
97 | 0.0074219 | 0.0018599 | -0.0074218 | -0.0018599 | 7.5061e-08 | 1.6836e-08 | 0.011246 | 0.011246 | 0.011246 | 0.98203 | -0.12538 | 0.98202 | -0.12545 | 4.1652
98 | 0.0045955 | 0.0011515 | -0.0045948 | -0.0011516 | 7.5528e-07 | -2.5267e-08 | 0.0069633 | 0.0069634 | 0.0069634 | 0.98202 | -0.12545 | 0.98185 | -0.12664 | 2.5791
99 | -0.1324 | -0.033404 | 0.13247 | 0.033428 | 6.5035e-05 | 2.4707e-05 | 0.1988 | 0.1988 | 0.1988 | 0.99142 | -0.059358 | 0.99192 | -0.055859 | 24.5435
100 | -0.13455 | -0.033951 | 0.13474 | 0.034022 | 0.00018619 | 7.0759e-05 | 0.20193 | 0.20193 | 0.20193 | 0.99192 | -0.055859 | 0.99333 | -0.046012 | 24.9297
101 | -0.00085395 | -0.00021402 | 0.00085397 | 0.00021386 | 1.3975e-08 | -1.5617e-07 | 0.0013091 | 0.001309 | 0.0013091 | 0.97066 | -0.20672 | 0.97068 | -0.2066 | 0.48485
102 | 0.0083282 | 0.0020871 | -0.0083265 | -0.0020866 | 1.6576e-06 | 4.3611e-07 | 0.012767 | 0.012767 | 0.012767 | 0.97068 | -0.2066 | 0.97048 | -0.20804 | 4.7284
103 | 0.0062733 | 0.0015721 | -0.0062731 | -0.001572 | 2.2266e-07 | 3.7984e-08 | 0.0096186 | 0.0096187 | 0.0096187 | 0.97048 | -0.20804 | 0.97044 | -0.2083 | 3.5625
104 | 0.0053175 | 0.0013325 | -0.0053165 | -0.0013324 | 9.6461e-07 | 8.3759e-08 | 0.0081534 | 0.0081535 | 0.0081535 | 0.97044 | -0.2083 | 0.97026 | -0.20961 | 3.0198
105 | 0.0059609 | 0.0014938 | -0.0059606 | -0.0014938 | 3.2472e-07 | 4.0846e-08 | 0.0089409 | 0.0089409 | 0.0089409 | 0.99206 | -0.055236 | 0.992 | -0.05563 | 3.3115
106 | 0.004117 | 0.0010274 | -0.0041168 | -0.0010274 | 2.0114e-07 | -2.9612e-08 | 0.0062054 | 0.0062055 | 0.0062055 | 0.98698 | -0.091008 | 0.98693 | -0.091364 | 2.2983
107 | -0.0055259 | -0.0013805 | 0.0055267 | 0.0013806 | 7.7703e-07 | 6.9452e-08 | 0.0083296 | 0.0083295 | 0.0083296 | 0.98698 | -0.091008 | 0.98713 | -0.089986 | 3.085
108 | 0.0028489 | 0.00070965 | -0.0028489 | -0.00070966 | 1.0345e-08 | -7.5124e-09 | 0.0042937 | 0.0042937 | 0.0042937 | 0.98693 | -0.091364 | 0.98693 | -0.091391 | 1.5903
109 | -0.0063229 | -0.0015801 | 0.0063239 | 0.0015803 | 9.0853e-07 | 1.4445e-07 | 0.0095297 | 0.0095297 | 0.0095297 | 0.98713 | -0.089986 | 0.98727 | -0.088942 | 3.5295
110 | 0.0019137 | 0.00047529 | -0.0019135 | -0.00047559 | 1.4535e-07 | -3.0198e-07 | 0.0028838 | 0.0028839 | 0.0028839 | 0.98693 | -0.091391 | 0.98685 | -0.091949 | 1.0681
111 | -0.0081431 | -0.0020362 | 0.0081453 | 0.0020368 | 2.2872e-06 | 5.6835e-07 | 0.012272 | 0.012271 | 0.012272 | 0.98727 | -0.088942 | 0.98756 | -0.086905 | 4.545
112 | 0.00044921 | 0.00010859 | -0.00044918 | -0.00011001 | 3.1938e-08 | -1.4178e-06 | 0.00067594 | 0.00067644 | 0.00067644 | 0.98685 | -0.091949 | 0.98678 | -0.092492 | 0.25053
113 | 0.00044918 | 0.00011001 | -0.00044916 | -0.00011076 | 1.7021e-08 | -7.5465e-07 | 0.00067644 | 0.0006767 | 0.0006767 | 0.98678 | -0.092492 | 0.98674 | -0.092777 | 0.25063
114 | 0.00044916 | 0.00011076 | -0.00044912 | -0.00011256 | 4.0575e-08 | -1.7963e-06 | 0.0006767 | 0.00067734 | 0.00067734 | 0.98674 | -0.092777 | 0.98665 | -0.09344 | 0.25087
115 | 0.00050629 | 0.00012654 | -0.00050628 | -0.00012689 | 1.0014e-08 | -3.5089e-07 | 0.00076174 | 0.00076187 | 0.00076187 | 0.98885 | -0.077712 | 0.98883 | -0.077855 | 0.28217
116 | 0.0032806 | 0.0008221 | -0.0032804 | -0.00082215 | 1.1486e-07 | -5.3957e-08 | 0.0049208 | 0.0049209 | 0.0049209 | 0.992 | -0.05563 | 0.99197 | -0.055883 | 1.8225

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21446 | 0.054044

## res_load
| p_mw | q_mvar
0 | 0.00036258 | 9.087e-05
1 | 0.0012111 | 0.00030353
2 | 0.00047738 | 0.00011964
3 | 0.00049692 | 0.00012454
4 | 0.0071791 | 0.0017992
5 | 0.0015705 | 0.0003936
6 | 0.00092964 | 0.00023299
7 | 0.0024961 | 0.00062557
8 | 0.0021739 | 0.00054483
9 | 0.00079163 | 0.0001984
10 | 0.0013405 | 0.00033597
11 | 0.0023431 | 0.00058724
12 | 0.0042867 | 0.0010743
13 | 0.0085133 | 0.0021336
14 | 0.0024263 | 0.0006081
15 | 0.00093643 | 0.00023469
16 | 0.0030477 | 0.00076382
17 | 0.00059456 | 0.00014901
18 | 0.0062066 | 0.0015555
19 | 0.00052598 | 0.00013182
20 | 0.0024554 | 0.00061538
21 | 0.0014014 | 0.00035122
22 | 0.0012593 | 0.00031561
23 | 0.0010054 | 0.00025198
24 | 0.00572 | 0.0014336
25 | 0.0040749 | 0.0010213
26 | 0.0012729 | 0.00031902
27 | 0.00070854 | 0.00017758
28 | 0.00088196 | 0.00022104
29 | 0.00074348 | 0.00018633
30 | 0.0023447 | 0.00058764
31 | 0.0020201 | 0.00050629
32 | 0.0021662 | 0.00054291
33 | 0.0011532 | 0.00028902
34 | 0.00216 | 0.00054134
35 | 0.000704 | 0.00017644
36 | 0.00066576 | 0.00016686
37 | 0.0012009 | 0.00030098
38 | 0.00095363 | 0.000239
39 | 0.0010117 | 0.00025356
40 | 0.00054514 | 0.00013663
41 | 0.00048639 | 0.0001219
42 | 0.0068096 | 0.0017067
43 | 0.0015774 | 0.00039533
44 | 0.0025363 | 0.00063567
45 | 0.013941 | 0.0034938
46 | 0.0049755 | 0.001247
47 | 0.0030361 | 0.00076091
48 | 0.0013076 | 0.00032772
49 | 0.0013669 | 0.00034258
50 | 0.0013848 | 0.00034708
51 | 0.0023341 | 0.00058498
52 | 0.0012406 | 0.00031093
53 | 0.002353 | 0.00058973
54 | 0.00147 | 0.00036843
55 | 0.0018052 | 0.00045242
56 | 0.0028659 | 0.00071825
57 | 0.0019709 | 0.00049396
58 | 0.0022367 | 0.00056056
59 | 0.00073109 | 0.00018323
60 | 0.0013019 | 0.00032628
61 | 0.013957 | 0.003498
62 | 0.0031712 | 0.00079478
63 | 0.0040311 | 0.0010103
64 | 0.0031182 | 0.00078149
65 | 0.0031182 | 0.00078149
66 | 0.0028263 | 0.00070835
67 | 0.0045948 | 0.0011516
68 | 0.0022498 | 0.00056386
69 | 0.0020853 | 0.00052263
70 | 0.0028017 | 0.00070216
71 | 0.0021287 | 0.0005335
72 | 0.00085395 | 0.00021402
73 | 0.0020532 | 0.00051459
74 | 0.00095559 | 0.00023949
75 | 0.0053165 | 0.0013324
76 | 0.0025664 | 0.0006432
77 | 0.0014089 | 0.00035311
78 | 0.001268 | 0.00031778
79 | 0.00079623 | 0.00019955
80 | 0.00093516 | 0.00023437
81 | 0.0018192 | 0.00045594
82 | 0.0014643 | 0.000367
83 | 0.00067907 | 0.00017019
84 | 0.00044912 | 0.00011256
85 | 0.00050628 | 0.00012689
86 | 0.0026801 | 0.00067168
87 | 0.0032804 | 0.00082215

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1