## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1402-28_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1402-28_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1402-28_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1402-28_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1402-28_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1402-28_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1402-28_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1402-28_0_4_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_1402-28_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1402-28_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1402-28_0_4_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1402-28_0_4_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1402-28_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1402-28_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1402-28_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1402-28_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_1402-28_0_4_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_1402-28_0_4_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1402-28_0_4_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_1402-28_0_4_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_1402-28_0_4_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1402-28_0_4_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_1402-28_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1402-28_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1402-28_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1402-28_0_4_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_1402-28_0_4_node_38 | 0.4 | n |  | TRUE
27 | bus_LV_1402-28_0_4_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1402-28_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1402-28_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1402-28_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1402-28_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1402-28_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1402-28_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1402-28_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1402-28_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1402-28_0_4_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_1402-28_0_4_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_1402-28_0_4_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_1402-28_0_4_node_39 | 0.4 | n |  | TRUE
40 | bus_MV_137_0_node_58 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1402-28_0_4_load_0 | 0 | 0.0048937 | 0.0012265 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1402-28_0_4_load_1 | 1 | 0.0088881 | 0.0022276 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1402-28_0_4_load_3 | 3 | 0.0081981 | 0.0020546 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1402-28_0_4_load_4 | 4 | 0.004895 | 0.0012268 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1402-28_0_4_load_5 | 5 | 0.019808 | 0.0049643 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1402-28_0_4_load_6 | 6 | 0.0032249 | 0.00080824 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1402-28_0_4_load_12 | 7 | 0.0057692 | 0.0014459 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1402-28_0_4_load_7 | 8 | 0.0025531 | 0.00063987 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1402-28_0_4_load_10 | 9 | 0.0046969 | 0.0011772 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1402-28_0_4_load_13 | 10 | 0.0024776 | 0.00062095 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1402-28_0_4_load_14 | 11 | 0.0024759 | 0.00062053 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1402-28_0_4_load_8 | 12 | 0.003245 | 0.00081327 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1402-28_0_4_load_9 | 13 | 0.013321 | 0.0033386 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1402-28_0_4_load_26 | 15 | 0.019807 | 0.0049641 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1402-28_0_4_load_34 | 16 | 0.0033795 | 0.00084699 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1402-28_0_4_load_24 | 17 | 0.0054398 | 0.0013633 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1402-28_0_4_load_32 | 18 | 0.015397 | 0.0038589 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1402-28_0_4_load_33 | 19 | 0.0033814 | 0.00084745 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1402-28_0_4_load_28 | 20 | 0.0025526 | 0.00063974 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1402-28_0_4_load_29 | 21 | 0.0025526 | 0.00063974 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1402-28_0_4_load_15 | 22 | 0.0038164 | 0.00095647 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1402-28_0_4_load_16 | 23 | 0.014302 | 0.0035845 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1402-28_0_4_load_17 | 24 | 0.0060674 | 0.0015206 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1402-28_0_4_load_31 | 25 | 0.0025039 | 0.00062754 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1402-28_0_4_load_38 | 26 | 0.0027074 | 0.00067854 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1402-28_0_4_load_30 | 27 | 0.0025035 | 0.00062743 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1402-28_0_4_load_27 | 28 | 0.0060711 | 0.0015216 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1402-28_0_4_load_25 | 29 | 0.005215 | 0.001307 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1402-28_0_4_load_23 | 30 | 0.0052095 | 0.0013056 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1402-28_0_4_load_18 | 31 | 0.0025039 | 0.00062754 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1402-28_0_4_load_19 | 32 | 0.0025057 | 0.00062798 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1402-28_0_4_load_20 | 33 | 0.002708 | 0.00067868 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1402-28_0_4_load_22 | 35 | 0.0027064 | 0.0006783 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1402-28_0_4_load_37 | 36 | 0.0024745 | 0.00062018 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1402-28_0_4_load_36 | 37 | 0.0024727 | 0.00061972 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1402-28_0_4_load_35 | 38 | 0.019807 | 0.0049641 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1402-28_0_4_load_39 | 39 | 0.0027035 | 0.00067755 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1402-28_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0075839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1402-28_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.014362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1402-28_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.023158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1402-28_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0075449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1402-28_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.015269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1402-28_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.028983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1402-28_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0031084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1402-28_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 5.7459e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1402-28_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.022357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1402-28_0_4_line_9 | NAYY 4x150 SE | 8 | 10 | 0.0026579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1402-28_0_4_line_10 | NAYY 4x150 SE | 9 | 12 | 0.00012621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1402-28_0_4_line_11 | NAYY 4x150 SE | 10 | 11 | 0.00074167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1402-28_0_4_line_12 | NAYY 4x150 SE | 11 | 20 | 0.0040438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1402-28_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.023714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1402-28_0_4_line_14 | NAYY 4x150 SE | 13 | 14 | 0.0057302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1402-28_0_4_line_15 | NAYY 4x150 SE | 14 | 15 | 0.018194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1402-28_0_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.038204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1402-28_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1402-28_0_4_line_18 | NAYY 4x150 SE | 16 | 18 | 0.033742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1402-28_0_4_line_19 | NAYY 4x150 SE | 16 | 19 | 0.0087822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1402-28_0_4_line_20 | NAYY 4x150 SE | 17 | 30 | 0.0033256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1402-28_0_4_line_21 | NAYY 4x150 SE | 17 | 24 | 0.043172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1402-28_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 5.7465e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1402-28_0_4_line_23 | NAYY 4x150 SE | 21 | 38 | 0.00032005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1402-28_0_4_line_24 | NAYY 4x150 SE | 22 | 23 | 0.025816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1402-28_0_4_line_25 | NAYY 4x150 SE | 23 | 24 | 0.020262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1402-28_0_4_line_26 | NAYY 4x150 SE | 24 | 28 | 0.0011471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1402-28_0_4_line_27 | NAYY 4x150 SE | 25 | 26 | 0.0010726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1402-28_0_4_line_28 | NAYY 4x150 SE | 25 | 27 | 0.00044139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1402-28_0_4_line_29 | NAYY 4x150 SE | 26 | 39 | 0.0007833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1402-28_0_4_line_30 | NAYY 4x150 SE | 27 | 35 | 0.0055677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1402-28_0_4_line_31 | NAYY 4x150 SE | 29 | 30 | 0.0036193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1402-28_0_4_line_32 | NAYY 4x150 SE | 31 | 32 | 0.000442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1402-28_0_4_line_33 | NAYY 4x150 SE | 31 | 33 | 0.0008736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1402-28_0_4_line_34 | NAYY 4x150 SE | 32 | 34 | 0.012353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1402-28_0_4_line_35 | NAYY 4x150 SE | 33 | 35 | 0.00078425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1402-28_0_4_line_36 | NAYY 4x150 SE | 34 | 36 | 0.021687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1402-28_0_4_line_37 | NAYY 4x150 SE | 36 | 37 | 0.00074091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1402-28_0_4_line_38 | NAYY 4x150 SE | 37 | 38 | 0.0022889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1402-28_0_4_trafo_10 | 0.25 MVA 20/0.4 kV | 40 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2675089.4254 | 1185432.2135 | 2675082.3654 | 1185434.9833
1 | 2675102.7956 | 1185426.9681 | 2675089.4254 | 1185432.2135
2 | 2675082.3654 | 1185434.9833 | 2675060.8068 | 1185443.4412
3 | 2675102.7956 | 1185426.9681 | 2675109.6287 | 1185423.7689
4 | 2675102.7956 | 1185426.9681 | 2675107.4135 | 1185441.5223
5 | 2675109.6287 | 1185423.7689 | 2675127.1715 | 1185415.5557 | 2675135.655 | 1185411.0363
6 | 2675108.3535 | 1185444.4852 | 2675107.4135 | 1185441.5223
7 | 2675135.655 | 1185411.0363 | 2675135.7057 | 1185411.0093
8 | 2675108.3535 | 1185444.4852 | 2675115.115 | 1185465.7953
9 | 2675138.0515 | 1185409.7597 | 2675135.7057 | 1185411.0093
10 | 2675115.115 | 1185465.7953 | 2675115.1532 | 1185465.9156
11 | 2675138.0515 | 1185409.7597 | 2675138.7061 | 1185409.4109
12 | 2675138.7061 | 1185409.4109 | 2675142.275 | 1185407.5097
13 | 2675122.325 | 1185488.519 | 2675115.1532 | 1185465.9156
14 | 2675125.127 | 1185493.3652 | 2675123.1846 | 1185491.2285 | 2675122.325 | 1185488.519
15 | 2675125.127 | 1185493.3652 | 2675129.5016 | 1185493.8648 | 2675143.0056 | 1185491.068
16 | 2675125.127 | 1185493.3652 | 2675125.9081 | 1185498.6337 | 2675131.4685 | 1185518.9933 | 2675130.5603 | 1185522.0281 | 2675127.9228 | 1185523.596 | 2675122.6334 | 1185525.2328
17 | 2675143.0056 | 1185491.068 | 2675156.9347 | 1185488.1832 | 2675163.2818 | 1185490.5521
18 | 2675122.6334 | 1185525.2328 | 2675134.9595 | 1185556.6425
19 | 2675114.2438 | 1185527.8291 | 2675122.6334 | 1185525.2328
20 | 2675166.3976 | 1185491.715 | 2675163.2818 | 1185490.5521
21 | 2675163.2818 | 1185490.5521 | 2675177.5995 | 1185449.8238
22 | 2675142.275 | 1185407.5097 | 2675142.3257 | 1185407.4826
23 | 2675142.3257 | 1185407.4826 | 2675142.6082 | 1185407.3322
24 | 2675192.6317 | 1185452.6108 | 2675216.2344 | 1185442.1515
25 | 2675192.6317 | 1185452.6108 | 2675184.8755 | 1185456.0479 | 2675180.7871 | 1185456.4524 | 2675178.8467 | 1185454.7715 | 2675177.5995 | 1185449.8238
26 | 2675177.3191 | 1185448.7115 | 2675177.5995 | 1185449.8238
27 | 2675182.0109 | 1185385.2553 | 2675182.9329 | 1185384.7072
28 | 2675182.0109 | 1185385.2553 | 2675181.6314 | 1185385.4808
29 | 2675183.6062 | 1185384.3069 | 2675182.9329 | 1185384.7072
30 | 2675176.8455 | 1185388.3259 | 2675181.6314 | 1185385.4808
31 | 2675169.7884 | 1185492.9806 | 2675169.7884 | 1185492.9806 | 2675166.3976 | 1185491.715
32 | 2675175.4204 | 1185389.1731 | 2675175.0405 | 1185389.399
33 | 2675176.1714 | 1185388.7267 | 2675175.4204 | 1185389.1731
34 | 2675164.4225 | 1185395.7111 | 2675175.0405 | 1185389.399
35 | 2675176.8455 | 1185388.3259 | 2675176.1714 | 1185388.7267
36 | 2675164.4225 | 1185395.7111 | 2675145.2822 | 1185405.9076
37 | 2675144.6283 | 1185406.256 | 2675145.2822 | 1185405.9076
38 | 2675142.6082 | 1185407.3322 | 2675144.6283 | 1185406.256

## bus_geodata
| x | y | coords
0 | 2675089.4254 | 1185432.2135
1 | 2675082.3654 | 1185434.9833
2 | 2675102.7956 | 1185426.9681
3 | 2675060.8068 | 1185443.4412
4 | 2675109.6287 | 1185423.7689
5 | 2675107.4135 | 1185441.5223
6 | 2675135.655 | 1185411.0363
7 | 2675108.3535 | 1185444.4852
8 | 2675135.7057 | 1185411.0093
9 | 2675115.115 | 1185465.7953
10 | 2675138.0515 | 1185409.7597
11 | 2675138.7061 | 1185409.4109
12 | 2675115.1532 | 1185465.9156
13 | 2675122.325 | 1185488.519
14 | 2675125.127 | 1185493.3652
15 | 2675143.0056 | 1185491.068
16 | 2675122.6334 | 1185525.2328
17 | 2675163.2818 | 1185490.5521
18 | 2675134.9595 | 1185556.6425
19 | 2675114.2438 | 1185527.8291
20 | 2675142.275 | 1185407.5097
21 | 2675142.3257 | 1185407.4826
22 | 2675216.2344 | 1185442.1515
23 | 2675192.6317 | 1185452.6108
24 | 2675177.5995 | 1185449.8238
25 | 2675182.0109 | 1185385.2553
26 | 2675182.9329 | 1185384.7072
27 | 2675181.6314 | 1185385.4808
28 | 2675177.3191 | 1185448.7115
29 | 2675169.7884 | 1185492.9806
30 | 2675166.3976 | 1185491.715
31 | 2675175.4204 | 1185389.1731
32 | 2675175.0405 | 1185389.399
33 | 2675176.1714 | 1185388.7267
34 | 2675164.4225 | 1185395.7111
35 | 2675176.8455 | 1185388.3259
36 | 2675145.2822 | 1185405.9076
37 | 2675144.6283 | 1185406.256
38 | 2675142.6082 | 1185407.3322
39 | 2675183.6062 | 1185384.3069
40 | 2675125.127 | 1185493.3652

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99555 | -0.031134 | 0.0048937 | 0.0012265
1 | 0.99536 | -0.03244 | 0.0088881 | 0.0022276
2 | 0.996 | -0.027956 | 0 | 0
3 | 0.99509 | -0.034353 | 0.0081981 | 0.0020546
4 | 0.99528 | -0.032995 | 0.004895 | 0.0012268
5 | 0.99793 | -0.014415 | 0.019808 | 0.0049643
6 | 0.99272 | -0.050982 | 0.0032249 | 0.00080824
7 | 0.99817 | -0.012731 | 0.0057692 | 0.0014459
8 | 0.99271 | -0.051016 | 0.0025531 | 0.00063987
9 | 1 | 0 | -0.22069 | -0.055284
10 | 0.9925 | -0.052515 | 0.0024776 | 0.00062095
11 | 0.99245 | -0.052915 | 0.0024759 | 0.00062053
12 | 0.99999 | -6.5925e-05 | 0.003245 | 0.00081327
13 | 0.99654 | -0.024155 | 0.013321 | 0.0033386
14 | 0.99581 | -0.029233 | 0 | 0
15 | 0.99409 | -0.041328 | 0.019807 | 0.0049641
16 | 0.9946 | -0.037765 | 0.0033795 | 0.00084699
17 | 0.9927 | -0.051125 | 0.0054398 | 0.0013633
18 | 0.99386 | -0.043011 | 0.015397 | 0.0038589
19 | 0.99456 | -0.038065 | 0.0033814 | 0.00084745
20 | 0.99215 | -0.054993 | 0.0025526 | 0.00063974
21 | 0.99215 | -0.055021 | 0.0025526 | 0.00063974
22 | 0.99015 | -0.069121 | 0.0038164 | 0.00095647
23 | 0.99029 | -0.068118 | 0.014302 | 0.0035845
24 | 0.99082 | -0.064383 | 0.0060674 | 0.0015206
25 | 0.99086 | -0.064099 | 0.0025039 | 0.00062754
26 | 0.99085 | -0.064158 | 0.0027074 | 0.00067854
27 | 0.99087 | -0.064063 | 0.0025035 | 0.00062743
28 | 0.99081 | -0.064454 | 0.0060711 | 0.0015216
29 | 0.99262 | -0.051668 | 0.005215 | 0.001307
30 | 0.99265 | -0.051477 | 0.0052095 | 0.0013056
31 | 0.99098 | -0.063229 | 0.0025039 | 0.00062754
32 | 0.991 | -0.063146 | 0.0025057 | 0.00062798
33 | 0.99096 | -0.063369 | 0.002708 | 0.00067868
34 | 0.99137 | -0.060531 | 0 | 0
35 | 0.99095 | -0.063474 | 0.0027064 | 0.0006783
36 | 0.99202 | -0.055943 | 0.0024745 | 0.00062018
37 | 0.99204 | -0.055768 | 0.0024727 | 0.00061972
38 | 0.99213 | -0.055169 | 0.019807 | 0.0049641
39 | 0.99085 | -0.064179 | 0.0027035 | 0.00067755
40 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.017091 | 0.0042838 | -0.017088 | -0.0042827 | 3.0884e-06 | 1.0893e-06 | 0.025546 | 0.025546 | 0.025546 | 0.99555 | -0.031134 | 0.99536 | -0.03244 | 9.4616
1 | -0.021985 | -0.0055103 | 0.021995 | 0.0055138 | 9.6775e-06 | 3.5353e-06 | 0.032861 | 0.032861 | 0.032861 | 0.99555 | -0.031134 | 0.996 | -0.027956 | 12.1707
2 | 0.0082003 | 0.0020552 | -0.0081981 | -0.0020546 | 2.1717e-06 | 5.3436e-07 | 0.012259 | 0.012259 | 0.012259 | 0.99536 | -0.03244 | 0.99509 | -0.034353 | 4.5404
3 | 0.066584 | 0.016721 | -0.066538 | -0.016703 | 4.66e-05 | 1.7825e-05 | 0.099488 | 0.099488 | 0.099488 | 0.996 | -0.027956 | 0.99528 | -0.032995 | 36.8475
4 | -0.088579 | -0.022235 | 0.088746 | 0.022299 | 0.0001669 | 6.3991e-05 | 0.13235 | 0.13235 | 0.13235 | 0.996 | -0.027956 | 0.99793 | -0.014415 | 49.0182
5 | 0.061643 | 0.015476 | -0.061489 | -0.015417 | 0.00015364 | 5.8716e-05 | 0.09217 | 0.09217 | 0.09217 | 0.99528 | -0.032995 | 0.99272 | -0.050982 | 34.1371
6 | -0.10855 | -0.027263 | 0.10858 | 0.027273 | 2.5416e-05 | 9.6941e-06 | 0.16188 | 0.16188 | 0.16188 | 0.99793 | -0.014415 | 0.99817 | -0.012731 | 29.9786
7 | 0.058264 | 0.014609 | -0.058264 | -0.014609 | 2.7348e-07 | 1.0444e-07 | 0.087336 | 0.087336 | 0.087336 | 0.99272 | -0.050982 | 0.99271 | -0.051016 | 32.3467
8 | -0.11435 | -0.028718 | 0.11455 | 0.028796 | 0.00020274 | 7.7391e-05 | 0.17048 | 0.17048 | 0.17048 | 0.99817 | -0.012731 | 1 | 0 | 31.5713
9 | 0.055711 | 0.013969 | -0.055699 | -0.013965 | 1.1566e-05 | 4.4142e-06 | 0.083509 | 0.083509 | 0.083509 | 0.99271 | -0.051016 | 0.9925 | -0.052515 | 30.9294
10 | 0.10534 | 0.026488 | -0.10533 | -0.026487 | 9.6777e-07 | 3.6891e-07 | 0.15677 | 0.15677 | 0.15677 | 1 | 0 | 0.99999 | -6.5925e-05 | 29.0318
11 | 0.053222 | 0.013344 | -0.053219 | -0.013343 | 2.9468e-06 | 1.1238e-06 | 0.079795 | 0.079795 | 0.079795 | 0.9925 | -0.052515 | 0.99245 | -0.052915 | 29.5536
12 | 0.050743 | 0.012722 | -0.050728 | -0.012717 | 1.4606e-05 | 5.5656e-06 | 0.076082 | 0.076082 | 0.076082 | 0.99245 | -0.052915 | 0.99215 | -0.054993 | 28.1787
13 | 0.10209 | 0.025674 | -0.10175 | -0.025543 | 0.00034163 | 0.00013108 | 0.15194 | 0.15194 | 0.15194 | 0.99999 | -6.5925e-05 | 0.99654 | -0.024155 | 56.2752
14 | 0.088427 | 0.022204 | -0.088364 | -0.022181 | 6.2351e-05 | 2.3907e-05 | 0.13205 | 0.13205 | 0.13205 | 0.99654 | -0.024155 | 0.99581 | -0.029233 | 48.9083
15 | 0.066169 | 0.016614 | -0.066058 | -0.016571 | 0.00011101 | 4.246e-05 | 0.098885 | 0.098885 | 0.098885 | 0.99581 | -0.029233 | 0.99409 | -0.041328 | 36.6239
16 | 0.022196 | 0.0055668 | -0.022169 | -0.0055572 | 2.6226e-05 | 9.5905e-06 | 0.033168 | 0.033168 | 0.033168 | 0.99581 | -0.029233 | 0.9946 | -0.037765 | 12.2844
17 | 0.046251 | 0.011607 | -0.046188 | -0.011583 | 6.2815e-05 | 2.3888e-05 | 0.069236 | 0.069237 | 0.069237 | 0.99409 | -0.041328 | 0.9927 | -0.051125 | 25.6431
18 | 0.015408 | 0.0038628 | -0.015397 | -0.0038589 | 1.1189e-05 | 3.866e-06 | 0.023053 | 0.023053 | 0.023053 | 0.9946 | -0.037765 | 0.99386 | -0.043011 | 8.5382
19 | 0.0033815 | 0.00084739 | -0.0033814 | -0.00084745 | 1.4026e-07 | -6.0026e-08 | 0.005059 | 0.0050591 | 0.0050591 | 0.9946 | -0.037765 | 0.99456 | -0.038065 | 1.8737
20 | 0.010425 | 0.0026128 | -0.010425 | -0.0026126 | 5.0676e-07 | 1.5192e-07 | 0.015627 | 0.015627 | 0.015627 | 0.9927 | -0.051125 | 0.99265 | -0.051477 | 5.7877
21 | 0.030323 | 0.0076073 | -0.030267 | -0.0075864 | 5.5662e-05 | 2.0852e-05 | 0.045456 | 0.045456 | 0.045456 | 0.9927 | -0.051125 | 0.99082 | -0.064383 | 16.8355
22 | 0.048175 | 0.012077 | -0.048175 | -0.012077 | 1.872e-07 | 7.1259e-08 | 0.072254 | 0.072254 | 0.072254 | 0.99215 | -0.054993 | 0.99215 | -0.055021 | 26.7608
23 | 0.045623 | 0.011437 | -0.045622 | -0.011437 | 9.3506e-07 | 3.5551e-07 | 0.068426 | 0.068426 | 0.068426 | 0.99215 | -0.055021 | 0.99213 | -0.055169 | 25.3428
24 | -0.0038164 | -0.00095647 | 0.0038169 | 0.00095635 | 5.2989e-07 | -1.2829e-07 | 0.0057353 | 0.0057352 | 0.0057353 | 0.99015 | -0.069121 | 0.99029 | -0.068118 | 2.1242
25 | -0.018119 | -0.0045409 | 0.018129 | 0.0045442 | 9.372e-06 | 3.3438e-06 | 0.027226 | 0.027226 | 0.027226 | 0.99029 | -0.068118 | 0.99082 | -0.064383 | 10.0838
26 | 0.0060712 | 0.0015216 | -0.0060711 | -0.0015216 | 5.9507e-08 | 8.1131e-09 | 0.0091177 | 0.0091177 | 0.0091177 | 0.99082 | -0.064383 | 0.99081 | -0.064454 | 3.3769
27 | 0.0054109 | 0.0013561 | -0.0054109 | -0.0013561 | 4.4194e-08 | 3.1818e-09 | 0.0081258 | 0.0081258 | 0.0081258 | 0.99086 | -0.064099 | 0.99085 | -0.064158 | 3.0096
28 | -0.0079148 | -0.0019836 | 0.0079149 | 0.0019836 | 3.8912e-08 | 9.2808e-09 | 0.011886 | 0.011886 | 0.011886 | 0.99086 | -0.064099 | 0.99087 | -0.064063 | 4.4022
29 | 0.0027035 | 0.00067754 | -0.0027035 | -0.00067755 | 8.0566e-09 | -6.9906e-09 | 0.0040599 | 0.0040599 | 0.0040599 | 0.99085 | -0.064158 | 0.99085 | -0.064179 | 1.5037
30 | -0.010418 | -0.0026111 | 0.010419 | 0.0026113 | 8.5044e-07 | 2.5537e-07 | 0.015646 | 0.015646 | 0.015646 | 0.99087 | -0.064063 | 0.99095 | -0.063474 | 5.7947
31 | -0.005215 | -0.001307 | 0.0052151 | 0.001307 | 1.3803e-07 | 6.3019e-09 | 0.0078177 | 0.0078177 | 0.0078177 | 0.99262 | -0.051668 | 0.99265 | -0.051477 | 2.8954
32 | -0.018338 | -0.004596 | 0.018338 | 0.0045961 | 2.0912e-07 | 7.4736e-08 | 0.027536 | 0.027536 | 0.027536 | 0.99098 | -0.063229 | 0.991 | -0.063146 | 10.1983
33 | 0.015834 | 0.0039685 | -0.015834 | -0.0039684 | 3.0815e-07 | 1.0727e-07 | 0.023776 | 0.023776 | 0.023776 | 0.99098 | -0.063229 | 0.99096 | -0.063369 | 8.8058
34 | -0.020844 | -0.0052241 | 0.020851 | 0.0052268 | 7.5504e-06 | 2.7448e-06 | 0.031298 | 0.031298 | 0.031298 | 0.991 | -0.063146 | 0.99137 | -0.060531 | 11.5918
35 | 0.013126 | 0.0032897 | -0.013126 | -0.0032896 | 1.901e-07 | 6.3013e-08 | 0.01971 | 0.01971 | 0.01971 | 0.99096 | -0.063369 | 0.99095 | -0.063474 | 7.2998
36 | -0.020851 | -0.0052268 | 0.020865 | 0.0052316 | 1.3256e-05 | 4.8186e-06 | 0.031298 | 0.031298 | 0.031298 | 0.99137 | -0.060531 | 0.99202 | -0.055943 | 11.5918
37 | -0.023339 | -0.0058518 | 0.02334 | 0.005852 | 5.6666e-07 | 2.0838e-07 | 0.03501 | 0.03501 | 0.03501 | 0.99202 | -0.055943 | 0.99204 | -0.055768 | 12.9665
38 | -0.025812 | -0.0064717 | 0.025815 | 0.0064725 | 2.1411e-06 | 7.9395e-07 | 0.038718 | 0.038718 | 0.038718 | 0.99204 | -0.055768 | 0.99213 | -0.055169 | 14.3402

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22538 | 0.056461

## res_load
| p_mw | q_mvar
0 | 0.0048937 | 0.0012265
1 | 0.0088881 | 0.0022276
2 | 0.0081981 | 0.0020546
3 | 0.004895 | 0.0012268
4 | 0.019808 | 0.0049643
5 | 0.0032249 | 0.00080824
6 | 0.0057692 | 0.0014459
7 | 0.0025531 | 0.00063987
8 | 0.0046969 | 0.0011772
9 | 0.0024776 | 0.00062095
10 | 0.0024759 | 0.00062053
11 | 0.003245 | 0.00081327
12 | 0.013321 | 0.0033386
13 | 0.019807 | 0.0049641
14 | 0.0033795 | 0.00084699
15 | 0.0054398 | 0.0013633
16 | 0.015397 | 0.0038589
17 | 0.0033814 | 0.00084745
18 | 0.0025526 | 0.00063974
19 | 0.0025526 | 0.00063974
20 | 0.0038164 | 0.00095647
21 | 0.014302 | 0.0035845
22 | 0.0060674 | 0.0015206
23 | 0.0025039 | 0.00062754
24 | 0.0027074 | 0.00067854
25 | 0.0025035 | 0.00062743
26 | 0.0060711 | 0.0015216
27 | 0.005215 | 0.001307
28 | 0.0052095 | 0.0013056
29 | 0.0025039 | 0.00062754
30 | 0.0025057 | 0.00062798
31 | 0.002708 | 0.00067868
32 | 0.0027064 | 0.0006783
33 | 0.0024745 | 0.00062018
34 | 0.0024727 | 0.00061972
35 | 0.019807 | 0.0049641
36 | 0.0027035 | 0.00067755

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1