## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1402-31_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1402-31_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1402-31_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1402-31_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1402-31_0_3_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_1402-31_0_3_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1402-31_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1402-31_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1402-31_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1402-31_0_3_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_1402-31_0_3_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1402-31_0_3_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_1402-31_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1402-31_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1402-31_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1402-31_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1402-31_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1402-31_0_3_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1402-31_0_3_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_1402-31_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1402-31_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1402-31_0_3_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_1402-31_0_3_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1402-31_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1402-31_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1402-31_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1402-31_0_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1402-31_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1402-31_0_3_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1402-31_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1402-31_0_3_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_1402-31_0_3_node_48 | 0.4 | n |  | TRUE
32 | bus_LV_1402-31_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1402-31_0_3_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_1402-31_0_3_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_1402-31_0_3_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_1402-31_0_3_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1402-31_0_3_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_1402-31_0_3_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_1402-31_0_3_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_1402-31_0_3_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_1402-31_0_3_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1402-31_0_3_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_1402-31_0_3_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_1402-31_0_3_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_1402-31_0_3_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_1402-31_0_3_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_1402-31_0_3_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_1402-31_0_3_node_46 | 0.4 | n |  | TRUE
49 | bus_MV_137_0_node_65 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1402-31_0_3_load_0 | 0 | 0.018359 | 0.0046011 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1402-31_0_3_load_1 | 1 | 0.0092767 | 0.002325 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1402-31_0_3_load_2 | 2 | 0.0086461 | 0.0021669 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1402-31_0_3_load_3 | 3 | 0.01413 | 0.0035413 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1402-31_0_3_load_12 | 4 | 0.0090637 | 0.0022716 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1402-31_0_3_load_13 | 5 | 0.0097007 | 0.0024312 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1402-31_0_3_load_4 | 6 | 0.0033638 | 0.00084304 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1402-31_0_3_load_5 | 7 | 0.0022565 | 0.00056552 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1402-31_0_3_load_6 | 8 | 0.0024332 | 0.00060982 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1402-31_0_3_load_23 | 10 | 0.0033205 | 0.00083219 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1402-31_0_3_load_21 | 11 | 0.0039203 | 0.00098252 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1402-31_0_3_load_7 | 12 | 0.0031419 | 0.00078744 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1402-31_0_3_load_9 | 14 | 0.0084814 | 0.0021256 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1402-31_0_3_load_10 | 15 | 0.0016175 | 0.00040538 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1402-31_0_3_load_11 | 16 | 0.0056022 | 0.001404 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1402-31_0_3_load_19 | 17 | 0.0016192 | 0.0004058 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1402-31_0_3_load_32 | 18 | 0.0061428 | 0.0015395 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1402-31_0_3_load_14 | 20 | 0.0074149 | 0.0018584 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1402-31_0_3_load_31 | 21 | 0.011646 | 0.0029188 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1402-31_0_3_load_26 | 22 | 0.0052791 | 0.0013231 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1402-31_0_3_load_15 | 23 | 0.0028533 | 0.0007151 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1402-31_0_3_load_16 | 24 | 0.008258 | 0.0020696 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1402-31_0_3_load_18 | 25 | 0.010776 | 0.0027008 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1402-31_0_3_load_20 | 26 | 0.0024315 | 0.00060938 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1402-31_0_3_load_25 | 28 | 0.0045344 | 0.0011364 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1402-31_0_3_load_27 | 29 | 0.005908 | 0.0014807 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1402-31_0_3_load_48 | 31 | 0.002466 | 0.00061805 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1402-31_0_3_load_29 | 32 | 0.0089614 | 0.002246 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1402-31_0_3_load_47 | 33 | 0.00020474 | 5.1312e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1402-31_0_3_load_30 | 34 | 0.011782 | 0.0029528 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1402-31_0_3_load_33 | 35 | 0.011871 | 0.0029752 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1402-31_0_3_load_34 | 36 | 0.0034396 | 0.00086206 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1402-31_0_3_load_35 | 37 | 0.0036246 | 0.0009084 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1402-31_0_3_load_39 | 38 | 0.0034396 | 0.00086204 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1402-31_0_3_load_38 | 39 | 0.0036891 | 0.00092457 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1402-31_0_3_load_36 | 40 | 0.0034396 | 0.00086204 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1402-31_0_3_load_37 | 41 | 0.0026203 | 0.0006567 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1402-31_0_3_load_40 | 42 | 0.0014699 | 0.0003684 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1402-31_0_3_load_41 | 43 | 0.00014819 | 3.714e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1402-31_0_3_load_43 | 45 | 9.0838e-05 | 2.2766e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1402-31_0_3_load_44 | 46 | 0.00014782 | 3.7047e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1402-31_0_3_load_45 | 47 | 9.4001e-05 | 2.3559e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1402-31_0_3_load_46 | 48 | 0.00010241 | 2.5665e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1402-31_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.016403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1402-31_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0056343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1402-31_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.015572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1402-31_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0075918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1402-31_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.020962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1402-31_0_3_line_5 | NAYY 4x150 SE | 5 | 20 | 0.00038439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1402-31_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.0055218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1402-31_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.017601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1402-31_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.013956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1402-31_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.036742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1402-31_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.016004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1402-31_0_3_line_11 | NAYY 4x150 SE | 10 | 30 | 0.01115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1402-31_0_3_line_12 | NAYY 4x150 SE | 10 | 31 | 0.041904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1402-31_0_3_line_13 | NAYY 4x150 SE | 11 | 26 | 0.020767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1402-31_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.014703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1402-31_0_3_line_15 | NAYY 4x150 SE | 12 | 14 | 0.056797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1402-31_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.02396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1402-31_0_3_line_17 | NAYY 4x150 SE | 13 | 16 | 0.0074918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1402-31_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.0015184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1402-31_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.033973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1402-31_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.010084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1402-31_0_3_line_21 | NAYY 4x150 SE | 19 | 26 | 0.018471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1402-31_0_3_line_22 | NAYY 4x150 SE | 19 | 23 | 0.016442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1402-31_0_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.0021551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1402-31_0_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.02715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1402-31_0_3_line_25 | NAYY 4x150 SE | 22 | 27 | 0.01381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_1402-31_0_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.021878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1402-31_0_3_line_27 | NAYY 4x150 SE | 24 | 25 | 0.00046691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1402-31_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.037796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1402-31_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.016603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1402-31_0_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.013395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1402-31_0_3_line_31 | NAYY 4x150 SE | 28 | 34 | 0.035726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1402-31_0_3_line_32 | NAYY 4x150 SE | 29 | 35 | 0.0035002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1402-31_0_3_line_33 | NAYY 4x150 SE | 30 | 32 | 0.018274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1402-31_0_3_line_34 | NAYY 4x150 SE | 31 | 33 | 0.30161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1402-31_0_3_line_35 | NAYY 4x150 SE | 33 | 48 | 0.021609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1402-31_0_3_line_36 | NAYY 4x150 SE | 35 | 36 | 0.023541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1402-31_0_3_line_37 | NAYY 4x150 SE | 36 | 37 | 0.036638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1402-31_0_3_line_38 | NAYY 4x150 SE | 37 | 38 | 0.026569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1402-31_0_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.016714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1402-31_0_3_line_40 | NAYY 4x150 SE | 39 | 40 | 0.023427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1402-31_0_3_line_41 | NAYY 4x150 SE | 40 | 41 | 0.016715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1402-31_0_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.022101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1402-31_0_3_line_43 | NAYY 4x150 SE | 43 | 44 | 0.034066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1402-31_0_3_line_44 | NAYY 4x150 SE | 44 | 45 | 0.016537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1402-31_0_3_line_45 | NAYY 4x150 SE | 45 | 46 | 0.025245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1402-31_0_3_line_46 | NAYY 4x150 SE | 46 | 47 | 0.010628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1402-31_0_3_line_47 | NAYY 4x150 SE | 47 | 48 | 0.021731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1402-31_0_3_trafo_26 | 0.25 MVA 20/0.4 kV | 49 | 22 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2675079.9909 | 1185515.794 | 2675064.4 | 1185520.8923
1 | 2675079.9909 | 1185515.794 | 2675085.3461 | 1185514.0428
2 | 2675049.5995 | 1185525.7322 | 2675064.4 | 1185520.8923
3 | 2675049.5995 | 1185525.7322 | 2675042.3837 | 1185528.0918
4 | 2675022.4598 | 1185534.6071 | 2675042.3837 | 1185528.0918
5 | 2675022.4598 | 1185534.6071 | 2675022.0944 | 1185534.7266
6 | 2674911.4209 | 1185526.21 | 2674909.5111 | 1185521.029
7 | 2674909.5111 | 1185521.029 | 2674906.6036 | 1185513.1414 | 2674904.2139 | 1185504.2631
8 | 2674900.5866 | 1185490.7862 | 2674904.2139 | 1185504.2631
9 | 2674900.5866 | 1185490.7862 | 2674865.0898 | 1185500.2706
10 | 2674900.5866 | 1185490.7862 | 2674916.0476 | 1185486.654
11 | 2674854.3177 | 1185503.1488 | 2674865.0898 | 1185500.2706
12 | 2674865.0898 | 1185500.2706 | 2674855.9945 | 1185459.3659
13 | 2674936.1101 | 1185481.292 | 2674916.0476 | 1185486.654
14 | 2674988.1329 | 1185466.7002 | 2674985.8212 | 1185452.1801
15 | 2674985.8212 | 1185452.1801 | 2674992.5623 | 1185395.7842
16 | 2674988.1329 | 1185466.7002 | 2674965.1052 | 1185473.3182
17 | 2674988.1329 | 1185466.7002 | 2674995.3339 | 1185464.6331
18 | 2674963.6459 | 1185473.7376 | 2674965.1052 | 1185473.3182
19 | 2674995.3339 | 1185464.6331 | 2675022.8322 | 1185456.7397 | 2675027.9074 | 1185455.0032
20 | 2674953.9545 | 1185476.5228 | 2674963.6459 | 1185473.7376
21 | 2674953.9545 | 1185476.5228 | 2674936.1101 | 1185481.292
22 | 2674953.9545 | 1185476.5228 | 2674959.7856 | 1185491.8957
23 | 2675020.046 | 1185535.3964 | 2675022.0944 | 1185534.7266
24 | 2675020.046 | 1185535.3964 | 2674994.2403 | 1185543.8351
25 | 2674981.1144 | 1185548.1273 | 2674994.2403 | 1185543.8351
26 | 2674967.5444 | 1185512.3512 | 2674959.7856 | 1185491.8957
27 | 2674967.71 | 1185512.7878 | 2674967.5444 | 1185512.3512
28 | 2674981.1144 | 1185548.1273 | 2674967.71 | 1185512.7878
29 | 2674981.1144 | 1185548.1273 | 2674965.2468 | 1185553.013
30 | 2674981.1144 | 1185548.1273 | 2674985.932 | 1185560.6256
31 | 2674930.6841 | 1185559.4477 | 2674941.1431 | 1185560.4346 | 2674965.2468 | 1185553.013
32 | 2674987.1909 | 1185563.8916 | 2674985.932 | 1185560.6256
33 | 2674854.3177 | 1185503.1488 | 2674836.6911 | 1185507.9686
34 | 2674855.9945 | 1185459.3659 | 2674797.5262 | 1185163.4733
35 | 2674777.1634 | 1185160.5881 | 2674780.1814 | 1185163.5995 | 2674797.5262 | 1185163.4733
36 | 2674987.1909 | 1185563.8916 | 2674995.6577 | 1185585.8568
37 | 2674995.6577 | 1185585.8568 | 2674997.9905 | 1185591.909 | 2675003.516 | 1185596.8033 | 2675009.1057 | 1185597.1734 | 2675025.4478 | 1185591.9105
38 | 2675050.7373 | 1185583.7661 | 2675025.4478 | 1185591.9105
39 | 2675050.7373 | 1185583.7661 | 2675066.6466 | 1185578.6425
40 | 2675088.9456 | 1185571.4612 | 2675066.6466 | 1185578.6425
41 | 2675088.9456 | 1185571.4612 | 2675104.8561 | 1185566.3373
42 | 2674698.7814 | 1185158.0587 | 2674708.9723 | 1185138.4474
43 | 2674724.6804 | 1185108.2189 | 2674708.9723 | 1185138.4474
44 | 2674724.6804 | 1185108.2189 | 2674736.3866 | 1185119.8997
45 | 2674754.2571 | 1185137.7315 | 2674736.3866 | 1185119.8997
46 | 2674754.2571 | 1185137.7315 | 2674761.7803 | 1185145.2384
47 | 2674761.7803 | 1185145.2384 | 2674777.1634 | 1185160.5881

## bus_geodata
| x | y | coords
0 | 2675079.9909 | 1185515.794
1 | 2675064.4 | 1185520.8923
2 | 2675085.3461 | 1185514.0428
3 | 2675049.5995 | 1185525.7322
4 | 2675042.3837 | 1185528.0918
5 | 2675022.4598 | 1185534.6071
6 | 2674911.4209 | 1185526.21
7 | 2674909.5111 | 1185521.029
8 | 2674904.2139 | 1185504.2631
9 | 2674900.5866 | 1185490.7862
10 | 2674865.0898 | 1185500.2706
11 | 2674916.0476 | 1185486.654
12 | 2674985.8212 | 1185452.1801
13 | 2674988.1329 | 1185466.7002
14 | 2674992.5623 | 1185395.7842
15 | 2674965.1052 | 1185473.3182
16 | 2674995.3339 | 1185464.6331
17 | 2674963.6459 | 1185473.7376
18 | 2675027.9074 | 1185455.0032
19 | 2674953.9545 | 1185476.5228
20 | 2675022.0944 | 1185534.7266
21 | 2675020.046 | 1185535.3964
22 | 2674994.2403 | 1185543.8351
23 | 2674959.7856 | 1185491.8957
24 | 2674967.5444 | 1185512.3512
25 | 2674967.71 | 1185512.7878
26 | 2674936.1101 | 1185481.292
27 | 2674981.1144 | 1185548.1273
28 | 2674965.2468 | 1185553.013
29 | 2674985.932 | 1185560.6256
30 | 2674854.3177 | 1185503.1488
31 | 2674855.9945 | 1185459.3659
32 | 2674836.6911 | 1185507.9686
33 | 2674797.5262 | 1185163.4733
34 | 2674930.6841 | 1185559.4477
35 | 2674987.1909 | 1185563.8916
36 | 2674995.6577 | 1185585.8568
37 | 2675025.4478 | 1185591.9105
38 | 2675050.7373 | 1185583.7661
39 | 2675066.6466 | 1185578.6425
40 | 2675088.9456 | 1185571.4612
41 | 2675104.8561 | 1185566.3373
42 | 2674698.7814 | 1185158.0587
43 | 2674708.9723 | 1185138.4474
44 | 2674724.6804 | 1185108.2189
45 | 2674736.3866 | 1185119.8997
46 | 2674754.2571 | 1185137.7315
47 | 2674761.7803 | 1185145.2384
48 | 2674777.1634 | 1185160.5881
49 | 2674981.1144 | 1185548.1273

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9925 | -0.052542 | 0.018359 | 0.0046011
1 | 0.99314 | -0.048057 | 0.0092767 | 0.002325
2 | 0.99243 | -0.053036 | 0.0086461 | 0.0021669
3 | 0.99395 | -0.042344 | 0.01413 | 0.0035413
4 | 0.9945 | -0.03848 | 0.0090637 | 0.0022716
5 | 0.99629 | -0.025921 | 0.0097007 | 0.0024312
6 | 0.98837 | -0.081671 | 0.0033638 | 0.00084304
7 | 0.98839 | -0.081481 | 0.0022565 | 0.00056552
8 | 0.98853 | -0.080471 | 0.0024332 | 0.00060982
9 | 0.9887 | -0.079323 | 0 | 0
10 | 0.98779 | -0.085727 | 0.0033205 | 0.00083219
11 | 0.98928 | -0.075221 | 0.0039203 | 0.00098252
12 | 0.98949 | -0.073724 | 0.0031419 | 0.00078744
13 | 0.98973 | -0.071982 | 0 | 0
14 | 0.98879 | -0.07864 | 0.0084814 | 0.0021256
15 | 0.99054 | -0.066279 | 0.0016175 | 0.00040538
16 | 0.98961 | -0.072878 | 0.0056022 | 0.001404
17 | 0.99059 | -0.065893 | 0.0016192 | 0.0004058
18 | 0.98931 | -0.075006 | 0.0061428 | 0.0015395
19 | 0.99098 | -0.063164 | 0 | 0
20 | 0.99633 | -0.025653 | 0.0074149 | 0.0018584
21 | 0.99657 | -0.023994 | 0.011646 | 0.0029188
22 | 1 | 0 | -0.22471 | -0.05629
23 | 0.99236 | -0.05347 | 0.0028533 | 0.0007151
24 | 0.99428 | -0.039983 | 0.008258 | 0.0020696
25 | 0.99432 | -0.039656 | 0.010776 | 0.0027008
26 | 0.99014 | -0.069077 | 0.0024315 | 0.00060938
27 | 0.99867 | -0.0092714 | 0 | 0
28 | 0.99828 | -0.011984 | 0.0045344 | 0.0011364
29 | 0.99794 | -0.014375 | 0.005908 | 0.0014807
30 | 0.98765 | -0.08675 | 0 | 0
31 | 0.98751 | -0.087772 | 0.002466 | 0.00061805
32 | 0.98741 | -0.088426 | 0.0089614 | 0.002246
33 | 0.98653 | -0.094838 | 0.00020474 | 5.1312e-05
34 | 0.99768 | -0.016202 | 0.011782 | 0.0029528
35 | 0.99778 | -0.015502 | 0.011871 | 0.0029752
36 | 0.9971 | -0.020288 | 0.0034396 | 0.00086206
37 | 0.99622 | -0.026481 | 0.0036246 | 0.0009084
38 | 0.99571 | -0.030008 | 0.0034396 | 0.00086204
39 | 0.99548 | -0.03165 | 0.0036891 | 0.00092457
40 | 0.99528 | -0.03308 | 0.0034396 | 0.00086204
41 | 0.99521 | -0.033522 | 0.0026203 | 0.0006567
42 | 0.98614 | -0.097558 | 0.0014699 | 0.0003684
43 | 0.98619 | -0.097224 | 0.00014819 | 3.714e-05
44 | 0.98627 | -0.096657 | 0 | 0
45 | 0.98631 | -0.096381 | 9.0838e-05 | 2.2766e-05
46 | 0.98637 | -0.095937 | 0.00014782 | 3.7047e-05
47 | 0.9864 | -0.095733 | 9.4001e-05 | 2.3559e-05
48 | 0.98646 | -0.095296 | 0.00010241 | 2.5665e-05
49 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.027005 | -0.0067682 | 0.027022 | 0.0067744 | 1.6779e-05 | 6.2413e-06 | 0.040488 | 0.040488 | 0.040488 | 0.9925 | -0.052542 | 0.99314 | -0.048057 | 14.9955
1 | 0.0086467 | 0.0021671 | -0.0086461 | -0.0021669 | 5.9085e-07 | 1.5444e-07 | 0.012964 | 0.012964 | 0.012964 | 0.9925 | -0.052542 | 0.99243 | -0.053036 | 4.8013
2 | -0.036299 | -0.0090994 | 0.036328 | 0.0091102 | 2.8742e-05 | 1.0853e-05 | 0.054387 | 0.054387 | 0.054387 | 0.99314 | -0.048057 | 0.99395 | -0.042344 | 20.1433
3 | -0.050458 | -0.012652 | 0.050485 | 0.012662 | 2.7033e-05 | 1.0299e-05 | 0.075541 | 0.075541 | 0.075541 | 0.99395 | -0.042344 | 0.9945 | -0.03848 | 27.978
4 | -0.059548 | -0.014933 | 0.059652 | 0.014973 | 0.00010385 | 3.9669e-05 | 0.089102 | 0.089102 | 0.089102 | 0.9945 | -0.03848 | 0.99629 | -0.025921 | 33.0008
5 | -0.069353 | -0.017404 | 0.069355 | 0.017405 | 2.574e-06 | 9.8498e-07 | 0.10359 | 0.10359 | 0.10359 | 0.99629 | -0.025921 | 0.99633 | -0.025653 | 38.3669
6 | -0.0033638 | -0.00084304 | 0.0033638 | 0.000843 | 8.8367e-08 | -3.6781e-08 | 0.0050642 | 0.0050642 | 0.0050642 | 0.98837 | -0.081671 | 0.98839 | -0.081481 | 1.8756
7 | -0.0056203 | -0.0014085 | 0.0056211 | 0.0014086 | 7.8629e-07 | 7.6809e-08 | 0.0084613 | 0.0084612 | 0.0084613 | 0.98839 | -0.081481 | 0.98853 | -0.080471 | 3.1338
8 | -0.0080543 | -0.0020184 | 0.0080556 | 0.0020187 | 1.2801e-06 | 3.1339e-07 | 0.012124 | 0.012124 | 0.012124 | 0.98853 | -0.080471 | 0.9887 | -0.079323 | 4.4903
9 | 0.017028 | 0.0042636 | -0.017013 | -0.0042583 | 1.5057e-05 | 5.3204e-06 | 0.025627 | 0.025627 | 0.025627 | 0.9887 | -0.079323 | 0.98779 | -0.085727 | 9.4915
10 | -0.025084 | -0.0062823 | 0.025098 | 0.0062876 | 1.4232e-05 | 5.2683e-06 | 0.037751 | 0.037751 | 0.037751 | 0.9887 | -0.079323 | 0.98928 | -0.075221 | 13.9817
11 | 0.0089648 | 0.0022469 | -0.0089635 | -0.0022465 | 1.2689e-06 | 3.4532e-07 | 0.013505 | 0.013505 | 0.013505 | 0.98779 | -0.085727 | 0.98765 | -0.08675 | 5.0017
12 | 0.0047281 | 0.0011792 | -0.0047268 | -0.0011792 | 1.3257e-06 | -2.6355e-08 | 0.0071204 | 0.0071206 | 0.0071206 | 0.98779 | -0.085727 | 0.98751 | -0.087772 | 2.6373
13 | -0.029019 | -0.0072701 | 0.029043 | 0.0072793 | 2.4687e-05 | 9.228e-06 | 0.043647 | 0.043647 | 0.043647 | 0.98928 | -0.075221 | 0.99014 | -0.069077 | 16.1657
14 | -0.011629 | -0.0029146 | 0.011632 | 0.0029155 | 2.8059e-06 | 8.903e-07 | 0.017488 | 0.017488 | 0.017488 | 0.98949 | -0.073724 | 0.98973 | -0.071982 | 6.4771
15 | 0.0084872 | 0.0021271 | -0.0084814 | -0.0021256 | 5.7736e-06 | 1.4916e-06 | 0.012763 | 0.012764 | 0.012764 | 0.98949 | -0.073724 | 0.98879 | -0.07864 | 4.7272
16 | -0.02338 | -0.0058598 | 0.023399 | 0.0058666 | 1.8473e-05 | 6.797e-06 | 0.035151 | 0.035151 | 0.035151 | 0.98973 | -0.071982 | 0.99054 | -0.066279 | 13.0189
17 | 0.011748 | 0.0029443 | -0.011747 | -0.0029438 | 1.4585e-06 | 4.6469e-07 | 0.017663 | 0.017663 | 0.017663 | 0.98973 | -0.071982 | 0.98961 | -0.072878 | 6.5419
18 | -0.025016 | -0.006272 | 0.025018 | 0.0062724 | 1.3381e-06 | 4.9512e-07 | 0.037581 | 0.037581 | 0.037581 | 0.99054 | -0.066279 | 0.99059 | -0.065893 | 13.9188
19 | 0.0061447 | 0.0015398 | -0.0061428 | -0.0015395 | 1.8097e-06 | 2.5968e-07 | 0.0092393 | 0.0092395 | 0.0092395 | 0.98961 | -0.072878 | 0.98931 | -0.075006 | 3.422
20 | -0.026637 | -0.0066783 | 0.026647 | 0.006682 | 1.0074e-05 | 3.7448e-06 | 0.040013 | 0.040013 | 0.040013 | 0.99059 | -0.065893 | 0.99098 | -0.063164 | 14.8197
21 | 0.0315 | 0.0078984 | -0.031475 | -0.0078887 | 2.5788e-05 | 9.6806e-06 | 0.047301 | 0.047301 | 0.047301 | 0.99098 | -0.063164 | 0.99014 | -0.069077 | 17.519
22 | -0.058147 | -0.01458 | 0.058225 | 0.01461 | 7.8217e-05 | 2.9871e-05 | 0.087314 | 0.087314 | 0.087314 | 0.99098 | -0.063164 | 0.99236 | -0.05347 | 32.3386
23 | -0.07677 | -0.019264 | 0.076788 | 0.01927 | 1.7681e-05 | 6.7725e-06 | 0.11466 | 0.11466 | 0.11466 | 0.99633 | -0.025653 | 0.99657 | -0.023994 | 42.4684
24 | -0.088434 | -0.022189 | 0.08873 | 0.022303 | 0.00029544 | 0.00011327 | 0.13205 | 0.13205 | 0.13205 | 0.99657 | -0.023994 | 1 | 0 | 48.9089
25 | 0.13518 | 0.033988 | -0.135 | -0.033921 | 0.00017439 | 6.6712e-05 | 0.20118 | 0.20118 | 0.20118 | 1 | 0 | 0.99867 | -0.0092714 | 37.2561
26 | -0.061079 | -0.015325 | 0.061193 | 0.015369 | 0.00011453 | 4.3765e-05 | 0.091593 | 0.091592 | 0.091593 | 0.99236 | -0.05347 | 0.99428 | -0.039983 | 33.9232
27 | -0.069451 | -0.017439 | 0.069454 | 0.01744 | 3.1483e-06 | 1.2048e-06 | 0.10395 | 0.10395 | 0.10395 | 0.99428 | -0.039983 | 0.99432 | -0.039656 | 38.5004
28 | -0.080231 | -0.020141 | 0.080571 | 0.020271 | 0.00034007 | 0.0001303 | 0.12008 | 0.12008 | 0.12008 | 0.99432 | -0.039656 | 0.99867 | -0.0092714 | 44.4735
29 | 0.016329 | 0.0040935 | -0.016323 | -0.0040914 | 6.1331e-06 | 2.1417e-06 | 0.024331 | 0.024331 | 0.024331 | 0.99867 | -0.0092714 | 0.99828 | -0.011984 | 9.0114
30 | 0.038102 | 0.0095565 | -0.038075 | -0.0095463 | 2.6941e-05 | 1.0187e-05 | 0.056774 | 0.056774 | 0.056774 | 0.99867 | -0.0092714 | 0.99794 | -0.014375 | 21.0275
31 | 0.011789 | 0.002955 | -0.011782 | -0.0029528 | 6.8836e-06 | 2.1807e-06 | 0.017572 | 0.017572 | 0.017572 | 0.99828 | -0.011984 | 0.99768 | -0.016202 | 6.5082
32 | 0.032167 | 0.0080656 | -0.032162 | -0.0080637 | 5.0249e-06 | 1.8869e-06 | 0.047965 | 0.047965 | 0.047965 | 0.99794 | -0.014375 | 0.99778 | -0.015502 | 17.7648
33 | 0.0089635 | 0.0022465 | -0.0089614 | -0.002246 | 2.0796e-06 | 5.6605e-07 | 0.013505 | 0.013505 | 0.013505 | 0.98765 | -0.08675 | 0.98741 | -0.088426 | 5.0018
34 | 0.0022608 | 0.00056119 | -0.0022586 | -0.0005642 | 2.1826e-06 | -3.0154e-06 | 0.0034047 | 0.0034061 | 0.0034061 | 0.98751 | -0.087772 | 0.98653 | -0.094838 | 1.2615
35 | 0.0020538 | 0.00051289 | -0.0020537 | -0.00051312 | 1.2935e-07 | -2.2613e-07 | 0.0030972 | 0.0030973 | 0.0030973 | 0.98653 | -0.094838 | 0.98646 | -0.095296 | 1.1472
36 | 0.020291 | 0.0050885 | -0.020277 | -0.0050837 | 1.3452e-05 | 4.8664e-06 | 0.030261 | 0.030261 | 0.030261 | 0.99778 | -0.015502 | 0.9971 | -0.020288 | 11.2079
37 | 0.016838 | 0.0042216 | -0.016823 | -0.0042165 | 1.4436e-05 | 5.0748e-06 | 0.025128 | 0.025128 | 0.025128 | 0.9971 | -0.020288 | 0.99622 | -0.026481 | 9.3068
38 | 0.013199 | 0.0033081 | -0.013192 | -0.003306 | 6.4435e-06 | 2.1325e-06 | 0.019714 | 0.019714 | 0.019714 | 0.99622 | -0.026481 | 0.99571 | -0.030008 | 7.3016
39 | 0.0097525 | 0.0024439 | -0.0097503 | -0.0024433 | 2.2153e-06 | 6.347e-07 | 0.014574 | 0.014574 | 0.014574 | 0.99571 | -0.030008 | 0.99548 | -0.03165 | 5.3979
40 | 0.0060612 | 0.0015187 | -0.00606 | -0.0015186 | 1.2e-06 | 1.5701e-07 | 0.00906 | 0.0090601 | 0.0090601 | 0.99548 | -0.03165 | 0.99528 | -0.03308 | 3.3556
41 | 0.0026204 | 0.00065655 | -0.0026203 | -0.0006567 | 1.6009e-07 | -1.5564e-07 | 0.0039177 | 0.0039178 | 0.0039178 | 0.99528 | -0.03308 | 0.99521 | -0.033522 | 1.451
42 | -0.0014699 | -0.0003684 | 0.00147 | 0.00036814 | 6.7843e-08 | -2.5589e-07 | 0.002218 | 0.0022179 | 0.002218 | 0.98614 | -0.097558 | 0.98619 | -0.097224 | 0.82148
43 | -0.0016182 | -0.00040528 | 0.0016183 | 0.0004049 | 1.2671e-07 | -3.8597e-07 | 0.0024415 | 0.0024414 | 0.0024415 | 0.98619 | -0.097224 | 0.98627 | -0.096657 | 0.90426
44 | -0.0016183 | -0.0004049 | 0.0016184 | 0.00040471 | 6.1502e-08 | -1.8739e-07 | 0.0024414 | 0.0024413 | 0.0024414 | 0.98627 | -0.096657 | 0.98631 | -0.096381 | 0.9042
45 | -0.0017092 | -0.00042748 | 0.0017093 | 0.00042719 | 1.0472e-07 | -2.8194e-07 | 0.0025783 | 0.0025782 | 0.0025783 | 0.98631 | -0.096381 | 0.98637 | -0.095937 | 0.95493
46 | -0.0018571 | -0.00046424 | 0.0018572 | 0.00046413 | 5.2037e-08 | -1.1565e-07 | 0.0028012 | 0.0028012 | 0.0028012 | 0.98637 | -0.095937 | 0.9864 | -0.095733 | 1.0375
47 | -0.0019512 | -0.00048768 | 0.0019513 | 0.00048745 | 1.1744e-07 | -2.3225e-07 | 0.002943 | 0.0029429 | 0.002943 | 0.9864 | -0.095733 | 0.98646 | -0.095296 | 1.09

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22999 | 0.057614

## res_load
| p_mw | q_mvar
0 | 0.018359 | 0.0046011
1 | 0.0092767 | 0.002325
2 | 0.0086461 | 0.0021669
3 | 0.01413 | 0.0035413
4 | 0.0090637 | 0.0022716
5 | 0.0097007 | 0.0024312
6 | 0.0033638 | 0.00084304
7 | 0.0022565 | 0.00056552
8 | 0.0024332 | 0.00060982
9 | 0.0033205 | 0.00083219
10 | 0.0039203 | 0.00098252
11 | 0.0031419 | 0.00078744
12 | 0.0084814 | 0.0021256
13 | 0.0016175 | 0.00040538
14 | 0.0056022 | 0.001404
15 | 0.0016192 | 0.0004058
16 | 0.0061428 | 0.0015395
17 | 0.0074149 | 0.0018584
18 | 0.011646 | 0.0029188
19 | 0.0052791 | 0.0013231
20 | 0.0028533 | 0.0007151
21 | 0.008258 | 0.0020696
22 | 0.010776 | 0.0027008
23 | 0.0024315 | 0.00060938
24 | 0.0045344 | 0.0011364
25 | 0.005908 | 0.0014807
26 | 0.002466 | 0.00061805
27 | 0.0089614 | 0.002246
28 | 0.00020474 | 5.1312e-05
29 | 0.011782 | 0.0029528
30 | 0.011871 | 0.0029752
31 | 0.0034396 | 0.00086206
32 | 0.0036246 | 0.0009084
33 | 0.0034396 | 0.00086204
34 | 0.0036891 | 0.00092457
35 | 0.0034396 | 0.00086204
36 | 0.0026203 | 0.0006567
37 | 0.0014699 | 0.0003684
38 | 0.00014819 | 3.714e-05
39 | 9.0838e-05 | 2.2766e-05
40 | 0.00014782 | 3.7047e-05
41 | 9.4001e-05 | 2.3559e-05
42 | 0.00010241 | 2.5665e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1