## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1402-33_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1402-33_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1402-33_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1402-33_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1402-33_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1402-33_0_4_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_1402-33_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1402-33_0_4_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_1402-33_0_4_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1402-33_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1402-33_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1402-33_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1402-33_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1402-33_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1402-33_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1402-33_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1402-33_0_4_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1402-33_0_4_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_1402-33_0_4_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_1402-33_0_4_node_44 | 0.4 | n |  | TRUE
20 | bus_LV_1402-33_0_4_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_1402-33_0_4_node_46 | 0.4 | n |  | TRUE
22 | bus_LV_1402-33_0_4_node_50 | 0.4 | n |  | TRUE
23 | bus_LV_1402-33_0_4_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_1402-33_0_4_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_1402-33_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1402-33_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_1402-33_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1402-33_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1402-33_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1402-33_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1402-33_0_4_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1402-33_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1402-33_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_1402-33_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_1402-33_0_4_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1402-33_0_4_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1402-33_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1402-33_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1402-33_0_4_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_1402-33_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1402-33_0_4_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1402-33_0_4_node_48 | 0.4 | n |  | TRUE
43 | bus_LV_1402-33_0_4_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_1402-33_0_4_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_1402-33_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_1402-33_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1402-33_0_4_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_1402-33_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_1402-33_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_1402-33_0_4_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_1402-33_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_MV_137_0_node_136 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1402-33_0_4_load_0 | 0 | 0.0028428 | 0.00071248 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1402-33_0_4_load_1 | 1 | 0.0029816 | 0.00074725 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1402-33_0_4_load_2 | 2 | 0.0030917 | 0.00077486 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1402-33_0_4_load_3 | 3 | 0.0041558 | 0.0010415 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1402-33_0_4_load_4 | 4 | 0.0056421 | 0.001414 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1402-33_0_4_load_26 | 5 | 0.0058442 | 0.0014647 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1402-33_0_4_load_15 | 7 | 0.003812 | 0.00095537 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1402-33_0_4_load_18 | 8 | 0.00988 | 0.0024762 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1402-33_0_4_load_19 | 9 | 0.0050812 | 0.0012735 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1402-33_0_4_load_5 | 10 | 0.0033237 | 0.00083301 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1402-33_0_4_load_6 | 11 | 0.0066118 | 0.0016571 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1402-33_0_4_load_9 | 14 | 0.00068149 | 0.0001708 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1402-33_0_4_load_10 | 15 | 0.0024527 | 0.0006147 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1402-33_0_4_load_20 | 16 | 0.00097716 | 0.0002449 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1402-33_0_4_load_49 | 17 | 0.0032042 | 0.00080304 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1402-33_0_4_load_47 | 18 | 0.00094558 | 0.00023698 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1402-33_0_4_load_44 | 19 | 0.0016511 | 0.0004138 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1402-33_0_4_load_46 | 21 | 0.00078502 | 0.00019674 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1402-33_0_4_load_50 | 22 | 0.0062719 | 0.0015719 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1402-33_0_4_load_28 | 23 | 0.005096 | 0.0012772 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1402-33_0_4_load_11 | 25 | 0.0037143 | 0.00093089 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1402-33_0_4_load_12 | 26 | 0.0048769 | 0.0012223 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1402-33_0_4_load_14 | 28 | 0.0031658 | 0.00079343 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1402-33_0_4_load_16 | 29 | 0.010584 | 0.0026527 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1402-33_0_4_load_27 | 30 | 0.0044555 | 0.0011167 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1402-33_0_4_load_32 | 32 | 0.0041713 | 0.0010454 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1402-33_0_4_load_51 | 33 | 0.0072232 | 0.0018103 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1402-33_0_4_load_30 | 34 | 0.0019722 | 0.00049428 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1402-33_0_4_load_21 | 35 | 0.0074514 | 0.0018675 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1402-33_0_4_load_22 | 36 | 0.00339 | 0.00084963 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1402-33_0_4_load_23 | 37 | 0.0075842 | 0.0019008 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1402-33_0_4_load_24 | 38 | 0.0058119 | 0.0014566 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1402-33_0_4_load_35 | 39 | 0.0038679 | 0.00096939 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1402-33_0_4_load_37 | 40 | 0.00443 | 0.0011103 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1402-33_0_4_load_48 | 42 | 0.013077 | 0.0032774 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1402-33_0_4_load_42 | 43 | 0.019247 | 0.0048237 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1402-33_0_4_load_29 | 44 | 0.0070219 | 0.0017598 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1402-33_0_4_load_34 | 47 | 0.0061165 | 0.0015329 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1402-33_0_4_load_38 | 48 | 0.0050166 | 0.0012573 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1402-33_0_4_load_39 | 49 | 0.0032202 | 0.00080707 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1402-33_0_4_load_43 | 50 | 0.0070347 | 0.0017631 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1402-33_0_4_load_40 | 51 | 0.0060599 | 0.0015188 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1402-33_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1402-33_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.008132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1402-33_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.017551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1402-33_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0010025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1402-33_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0012699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1402-33_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.016024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1402-33_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.027787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1402-33_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.010812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1402-33_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.033129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1402-33_0_4_line_9 | NAYY 4x150 SE | 7 | 27 | 0.0037165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1402-33_0_4_line_10 | NAYY 4x150 SE | 8 | 32 | 0.0097474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1402-33_0_4_line_11 | NAYY 4x150 SE | 9 | 33 | 0.032107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1402-33_0_4_line_12 | NAYY 4x150 SE | 10 | 11 | 0.0017923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1402-33_0_4_line_13 | NAYY 4x150 SE | 10 | 12 | 0.089727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1402-33_0_4_line_14 | NAYY 4x150 SE | 11 | 13 | 0.038699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1402-33_0_4_line_15 | NAYY 4x150 SE | 12 | 14 | 0.066601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1402-33_0_4_line_16 | NAYY 4x150 SE | 12 | 15 | 0.081361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1402-33_0_4_line_17 | NAYY 4x150 SE | 13 | 23 | 0.0051643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1402-33_0_4_line_18 | NAYY 4x150 SE | 14 | 16 | 0.013269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1402-33_0_4_line_19 | NAYY 4x150 SE | 15 | 17 | 0.016643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1402-33_0_4_line_20 | NAYY 4x150 SE | 15 | 18 | 0.54253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1402-33_0_4_line_21 | NAYY 4x150 SE | 17 | 22 | 0.054916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1402-33_0_4_line_22 | NAYY 4x150 SE | 18 | 21 | 0.41817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1402-33_0_4_line_23 | NAYY 4x150 SE | 19 | 20 | 0.021865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1402-33_0_4_line_24 | NAYY 4x150 SE | 20 | 21 | 0.059193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1402-33_0_4_line_25 | NAYY 4x150 SE | 23 | 24 | 0.030293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1402-33_0_4_line_26 | NAYY 4x150 SE | 24 | 43 | 0.017403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1402-33_0_4_line_27 | NAYY 4x150 SE | 24 | 41 | 0.020645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1402-33_0_4_line_28 | NAYY 4x150 SE | 25 | 26 | 0.025387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1402-33_0_4_line_29 | NAYY 4x150 SE | 25 | 27 | 0.022873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1402-33_0_4_line_30 | NAYY 4x150 SE | 26 | 28 | 0.0035442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1402-33_0_4_line_31 | NAYY 4x150 SE | 27 | 29 | 0.0284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1402-33_0_4_line_32 | NAYY 4x150 SE | 28 | 30 | 0.018026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1402-33_0_4_line_33 | NAYY 4x150 SE | 30 | 31 | 0.036865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_1402-33_0_4_line_34 | NAYY 4x150 SE | 31 | 40 | 0.082489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1402-33_0_4_line_35 | NAYY 4x150 SE | 31 | 37 | 0.011266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1402-33_0_4_line_36 | NAYY 4x150 SE | 32 | 34 | 0.0039731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1402-33_0_4_line_37 | NAYY 4x150 SE | 34 | 44 | 0.018778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1402-33_0_4_line_38 | NAYY 4x150 SE | 35 | 36 | 0.020373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1402-33_0_4_line_39 | NAYY 4x150 SE | 35 | 37 | 0.041531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1402-33_0_4_line_40 | NAYY 4x150 SE | 36 | 38 | 0.00033844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1402-33_0_4_line_41 | NAYY 4x150 SE | 38 | 39 | 0.018505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1402-33_0_4_line_42 | NAYY 4x150 SE | 39 | 41 | 0.019192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1402-33_0_4_line_43 | NAYY 4x150 SE | 40 | 42 | 0.055524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1402-33_0_4_line_44 | NAYY 4x150 SE | 41 | 50 | 0.027064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1402-33_0_4_line_45 | NAYY 4x150 SE | 44 | 45 | 0.010213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1402-33_0_4_line_46 | NAYY 4x150 SE | 45 | 46 | 0.014064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1402-33_0_4_line_47 | NAYY 4x150 SE | 45 | 47 | 0.013153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1402-33_0_4_line_48 | NAYY 4x150 SE | 46 | 48 | 0.051109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1402-33_0_4_line_49 | NAYY 4x150 SE | 48 | 49 | 0.017024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1402-33_0_4_line_50 | NAYY 4x150 SE | 49 | 51 | 0.010754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1402-33_0_4_trafo_25 | 0.25 MVA 20/0.4 kV | 52 | 31 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2674976.4172 | 1185786.6398 | 2674979.2232 | 1185785.1333 | 2674986.09 | 1185782.5432
1 | 2674976.4172 | 1185786.6398 | 2674969.2525 | 1185790.4864
2 | 2675002.5117 | 1185776.349 | 2674986.09 | 1185782.5432
3 | 2674968.3693 | 1185790.9606 | 2674969.2525 | 1185790.4864
4 | 2675002.5117 | 1185776.349 | 2675003.6999 | 1185775.9008
5 | 2674954.2516 | 1185798.54 | 2674968.3693 | 1185790.9606
6 | 2675030.9501 | 1185770.4664 | 2675003.6999 | 1185775.9008 | 2675003.6999 | 1185775.9008
7 | 2674954.2516 | 1185798.54 | 2674945.8357 | 1185805.327
8 | 2674954.2516 | 1185798.54 | 2674964.376 | 1185823.7927 | 2674966.8761 | 1185827.0927 | 2674968.4297 | 1185827.9656
9 | 2675034.5949 | 1185769.7395 | 2675030.9501 | 1185770.4664
10 | 2674945.8357 | 1185805.327 | 2674938.2482 | 1185811.4459
11 | 2674990.4652 | 1185850.0456 | 2674985.8077 | 1185841.9606 | 2674982.3153 | 1185836.8472 | 2674979.7976 | 1185834.3475 | 2674970.5593 | 1185829.1622 | 2674968.4297 | 1185827.9656
12 | 2675323.0915 | 1185656.7697 | 2675321.3207 | 1185657.0461
13 | 2675323.0915 | 1185656.7697 | 2675412.6727 | 1185651.66
14 | 2675289.5862 | 1185678.6505 | 2675294.5553 | 1185674.3548 | 2675305.4999 | 1185665.8428 | 2675316.106 | 1185658.7608 | 2675319.9944 | 1185657.2532 | 2675321.3207 | 1185657.0461
15 | 2675412.6727 | 1185651.66 | 2675434.3045 | 1185619.3575 | 2675446.7252 | 1185604.5606 | 2675450.6797 | 1185597.144
16 | 2675412.6727 | 1185651.66 | 2675413.9094 | 1185661.3369 | 2675408.5104 | 1185688.2516 | 2675396.6465 | 1185730.7826
17 | 2675289.5862 | 1185678.6505 | 2675285.337 | 1185681.5854
18 | 2675456.9226 | 1185585.4356 | 2675450.6797 | 1185597.144
19 | 2675391.5113 | 1185746.6106 | 2675395.8737 | 1185733.5529 | 2675396.6465 | 1185730.7826
20 | 2675396.6465 | 1185730.7826 | 2675920.1119 | 1185873.3305
21 | 2675362.0299 | 1185792.6623 | 2675380.144 | 1185768.1311 | 2675389.9335 | 1185751.3331 | 2675391.5113 | 1185746.6106
22 | 2676311.6775 | 1186020.0945 | 2675920.1119 | 1185873.3305
23 | 2676300.54 | 1186077.5538 | 2676302.9 | 1186078.0064 | 2676306.5993 | 1186082.3561 | 2676319.7318 | 1186078.2765
24 | 2676300.54 | 1186077.5538 | 2676308.6216 | 1186057.8116 | 2676311.1727 | 1186033.6853 | 2676311.6775 | 1186020.0945
25 | 2675257.7318 | 1185693.0811 | 2675259.8585 | 1185691.4736 | 2675268.1743 | 1185689.8993 | 2675274.1238 | 1185687.7505 | 2675281.2868 | 1185684.3829 | 2675285.337 | 1185681.5854
26 | 2675264.6748 | 1185709.0445 | 2675257.7318 | 1185693.0811
27 | 2675240.7786 | 1185704.8197 | 2675248.2928 | 1185700.2224 | 2675257.7318 | 1185693.0811
28 | 2675082.3419 | 1185762.7252 | 2675057.2248 | 1185766.415
29 | 2675034.5949 | 1185769.7395 | 2675057.2248 | 1185766.415
30 | 2675085.8484 | 1185762.21 | 2675082.3419 | 1185762.7252
31 | 2675028.853 | 1185741.9289 | 2675034.5949 | 1185769.7395
32 | 2675085.8484 | 1185762.21 | 2675103.6832 | 1185759.59
33 | 2675139.1943 | 1185749.9829 | 2675125.0072 | 1185754.7968 | 2675110.39 | 1185758.6047 | 2675103.6832 | 1185759.59
34 | 2675139.1943 | 1185749.9829 | 2675170.4939 | 1185826.303
35 | 2675139.1943 | 1185749.9829 | 2675149.5305 | 1185745.5002
36 | 2674935.1555 | 1185813.94 | 2674938.2482 | 1185811.4459
37 | 2674920.5385 | 1185825.7277 | 2674935.1555 | 1185813.94
38 | 2675206.3237 | 1185720.8693 | 2675187.6326 | 1185728.9755
39 | 2675149.5305 | 1185745.5002 | 2675187.6326 | 1185728.9755
40 | 2675206.3237 | 1185720.8693 | 2675206.6342 | 1185720.7346
41 | 2675206.6342 | 1185720.7346 | 2675223.6108 | 1185713.3719
42 | 2675240.7786 | 1185704.8197 | 2675228.9085 | 1185711.0743 | 2675223.6108 | 1185713.3719
43 | 2675188.4286 | 1185870.3054 | 2675193.1396 | 1185859.8027 | 2675187.0199 | 1185845.7398 | 2675174.7654 | 1185841.3056 | 2675172.3849 | 1185830.914 | 2675170.4939 | 1185826.303
44 | 2675240.7786 | 1185704.8197 | 2675252.4309 | 1185729.2583
45 | 2674912.5885 | 1185832.1389 | 2674920.5385 | 1185825.7277
46 | 2674912.5885 | 1185832.1389 | 2674901.5803 | 1185840.9288
47 | 2674912.5885 | 1185832.1389 | 2674917.1623 | 1185838.0552 | 2674920.1642 | 1185842.8715
48 | 2674901.5803 | 1185840.9288 | 2674893.4527 | 1185828.6977 | 2674882.3226 | 1185811.8375 | 2674881.8497 | 1185806.9286 | 2674883.3893 | 1185803.4347 | 2674889.8045 | 1185799.6042
49 | 2674889.8045 | 1185799.6042 | 2674894.9156 | 1185796.5524 | 2674898.8094 | 1185792.7655 | 2674899.282 | 1185789.1471 | 2674898.8892 | 1185787.1955
50 | 2674896.7671 | 1185776.6526 | 2674898.8892 | 1185787.1955

## bus_geodata
| x | y | coords
0 | 2674976.4172 | 1185786.6398
1 | 2674986.09 | 1185782.5432
2 | 2674969.2525 | 1185790.4864
3 | 2675002.5117 | 1185776.349
4 | 2674968.3693 | 1185790.9606
5 | 2675003.6999 | 1185775.9008
6 | 2674954.2516 | 1185798.54
7 | 2675030.9501 | 1185770.4664
8 | 2674945.8357 | 1185805.327
9 | 2674968.4297 | 1185827.9656
10 | 2675323.0915 | 1185656.7697
11 | 2675321.3207 | 1185657.0461
12 | 2675412.6727 | 1185651.66
13 | 2675289.5862 | 1185678.6505
14 | 2675450.6797 | 1185597.144
15 | 2675396.6465 | 1185730.7826
16 | 2675456.9226 | 1185585.4356
17 | 2675391.5113 | 1185746.6106
18 | 2675920.1119 | 1185873.3305
19 | 2676319.7318 | 1186078.2765
20 | 2676300.54 | 1186077.5538
21 | 2676311.6775 | 1186020.0945
22 | 2675362.0299 | 1185792.6623
23 | 2675285.337 | 1185681.5854
24 | 2675257.7318 | 1185693.0811
25 | 2675057.2248 | 1185766.415
26 | 2675082.3419 | 1185762.7252
27 | 2675034.5949 | 1185769.7395
28 | 2675085.8484 | 1185762.21
29 | 2675028.853 | 1185741.9289
30 | 2675103.6832 | 1185759.59
31 | 2675139.1943 | 1185749.9829
32 | 2674938.2482 | 1185811.4459
33 | 2674990.4652 | 1185850.0456
34 | 2674935.1555 | 1185813.94
35 | 2675187.6326 | 1185728.9755
36 | 2675206.3237 | 1185720.8693
37 | 2675149.5305 | 1185745.5002
38 | 2675206.6342 | 1185720.7346
39 | 2675223.6108 | 1185713.3719
40 | 2675170.4939 | 1185826.303
41 | 2675240.7786 | 1185704.8197
42 | 2675188.4286 | 1185870.3054
43 | 2675264.6748 | 1185709.0445
44 | 2674920.5385 | 1185825.7277
45 | 2674912.5885 | 1185832.1389
46 | 2674901.5803 | 1185840.9288
47 | 2674920.1642 | 1185842.8715
48 | 2674889.8045 | 1185799.6042
49 | 2674898.8892 | 1185787.1955
50 | 2675252.4309 | 1185729.2583
51 | 2674896.7671 | 1185776.6526
52 | 2675034.5949 | 1185769.7395

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98192 | -0.12643 | 0.0028428 | 0.00071248
1 | 0.98296 | -0.1191 | 0.0029816 | 0.00074725
2 | 0.98116 | -0.13187 | 0.0030917 | 0.00077486
3 | 0.98475 | -0.10637 | 0.0041558 | 0.0010415
4 | 0.98107 | -0.13251 | 0.0056421 | 0.001414
5 | 0.98489 | -0.1054 | 0.0058442 | 0.0014647
6 | 0.97977 | -0.14179 | 0 | 0
7 | 0.98814 | -0.082502 | 0.003812 | 0.00095537
8 | 0.97908 | -0.14668 | 0.00988 | 0.0024762
9 | 0.97917 | -0.14603 | 0.0050812 | 0.0012735
10 | 0.98373 | -0.11428 | 0.0033237 | 0.00083301
11 | 0.98378 | -0.1139 | 0.0066118 | 0.0016571
12 | 0.98152 | -0.13013 | 0 | 0
13 | 0.9853 | -0.10313 | 0 | 0
14 | 0.98135 | -0.13128 | 0.00068149 | 0.0001708
15 | 0.9797 | -0.14315 | 0.0024527 | 0.0006147
16 | 0.98134 | -0.13141 | 0.00097716 | 0.0002449
17 | 0.97947 | -0.14479 | 0.0032042 | 0.00080304
18 | 0.97702 | -0.16269 | 0.00094558 | 0.00023698
19 | 0.97534 | -0.17488 | 0.0016511 | 0.0004138
20 | 0.97539 | -0.1745 | 0 | 0
21 | 0.97554 | -0.17347 | 0.00078502 | 0.00019674
22 | 0.97897 | -0.14838 | 0.0062719 | 0.0015719
23 | 0.9855 | -0.1017 | 0.005096 | 0.0012772
24 | 0.98691 | -0.091706 | 0 | 0
25 | 0.99174 | -0.057245 | 0.0037143 | 0.00093089
26 | 0.99538 | -0.031972 | 0.0048769 | 0.0012223
27 | 0.9886 | -0.079306 | 0 | 0
28 | 0.99564 | -0.030128 | 0.0031658 | 0.00079343
29 | 0.98816 | -0.082378 | 0.010584 | 0.0026527
30 | 0.99703 | -0.020476 | 0.0044555 | 0.0011167
31 | 1 | 0 | -0.21865 | -0.054976
32 | 0.9786 | -0.15009 | 0.0041713 | 0.0010454
33 | 0.97884 | -0.14844 | 0.0072232 | 0.0018103
34 | 0.97843 | -0.15131 | 0.0019722 | 0.00049428
35 | 0.99386 | -0.042718 | 0.0074514 | 0.0018675
36 | 0.99176 | -0.057467 | 0.00339 | 0.00084963
37 | 0.99859 | -0.0097444 | 0.0075842 | 0.0019008
38 | 0.99173 | -0.057701 | 0.0058119 | 0.0014566
39 | 0.99006 | -0.069418 | 0.0038679 | 0.00096939
40 | 0.99794 | -0.01445 | 0.00443 | 0.0011103
41 | 0.98844 | -0.080853 | 0 | 0
42 | 0.9969 | -0.021736 | 0.013077 | 0.0032774
43 | 0.98642 | -0.09514 | 0.019247 | 0.0048237
44 | 0.97768 | -0.15668 | 0.0070219 | 0.0017598
45 | 0.97738 | -0.15886 | 0 | 0
46 | 0.97708 | -0.16096 | 0 | 0
47 | 0.97726 | -0.1597 | 0.0061165 | 0.0015329
48 | 0.97602 | -0.16861 | 0.0050166 | 0.0012573
49 | 0.97579 | -0.17027 | 0.0032202 | 0.00080707
50 | 0.98817 | -0.082799 | 0.0070347 | 0.0017631
51 | 0.97569 | -0.17095 | 0.0060599 | 0.0015188
52 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.067575 | -0.016964 | 0.067644 | 0.016991 | 6.8878e-05 | 2.6358e-05 | 0.10241 | 0.10241 | 0.10241 | 0.98192 | -0.12643 | 0.98296 | -0.1191 | 37.9312
1 | 0.064732 | 0.016252 | -0.064684 | -0.016233 | 4.884e-05 | 1.8682e-05 | 0.098106 | 0.098106 | 0.098106 | 0.98192 | -0.12643 | 0.98116 | -0.13187 | 36.3357
2 | -0.070626 | -0.017738 | 0.070751 | 0.017786 | 0.00012522 | 4.7938e-05 | 0.10693 | 0.10693 | 0.10693 | 0.98296 | -0.1191 | 0.98475 | -0.10637 | 39.6029
3 | 0.061592 | 0.015458 | -0.061586 | -0.015456 | 5.459e-06 | 2.0869e-06 | 0.093417 | 0.093417 | 0.093417 | 0.98116 | -0.13187 | 0.98107 | -0.13251 | 34.599
4 | -0.074907 | -0.018827 | 0.074917 | 0.018831 | 1.0156e-05 | 3.8899e-06 | 0.11321 | 0.11321 | 0.11321 | 0.98475 | -0.10637 | 0.98489 | -0.1054 | 41.9286
5 | 0.055944 | 0.014042 | -0.055872 | -0.014015 | 7.2003e-05 | 2.7491e-05 | 0.08486 | 0.08486 | 0.08486 | 0.98107 | -0.13251 | 0.97977 | -0.14179 | 31.4296
6 | -0.080761 | -0.020296 | 0.081019 | 0.020395 | 0.00025823 | 9.8964e-05 | 0.12204 | 0.12204 | 0.12204 | 0.98489 | -0.1054 | 0.98814 | -0.082502 | 45.1989
7 | 0.043558 | 0.010928 | -0.043529 | -0.010917 | 2.9528e-05 | 1.1221e-05 | 0.066158 | 0.066158 | 0.066158 | 0.97977 | -0.14179 | 0.97908 | -0.14668 | 24.503
8 | 0.012314 | 0.0030866 | -0.012307 | -0.0030843 | 7.2305e-06 | 2.364e-06 | 0.018702 | 0.018702 | 0.018702 | 0.97977 | -0.14179 | 0.97917 | -0.14603 | 6.9267
9 | -0.084831 | -0.02135 | 0.084869 | 0.021365 | 3.7864e-05 | 1.4516e-05 | 0.12778 | 0.12778 | 0.12778 | 0.98814 | -0.082502 | 0.9886 | -0.079306 | 47.3249
10 | 0.033649 | 0.0084407 | -0.033633 | -0.0084347 | 1.5909e-05 | 5.9962e-06 | 0.051142 | 0.051142 | 0.051142 | 0.97908 | -0.14668 | 0.9786 | -0.15009 | 18.9417
11 | 0.0072256 | 0.0018108 | -0.0072232 | -0.0018103 | 2.4156e-06 | 5.2537e-07 | 0.01098 | 0.010981 | 0.010981 | 0.97917 | -0.14603 | 0.97884 | -0.14844 | 4.0669
12 | -0.020376 | -0.0051007 | 0.020377 | 0.0051011 | 1.0623e-06 | 3.8581e-07 | 0.030819 | 0.030819 | 0.030819 | 0.98373 | -0.11428 | 0.98378 | -0.1139 | 11.4145
13 | 0.017052 | 0.0042677 | -0.017015 | -0.0042546 | 3.7245e-05 | 1.3188e-05 | 0.025792 | 0.025792 | 0.025792 | 0.98373 | -0.11428 | 0.98152 | -0.13013 | 9.5526
14 | -0.026989 | -0.0067582 | 0.027029 | 0.0067732 | 4.0237e-05 | 1.4984e-05 | 0.04082 | 0.04082 | 0.04082 | 0.98378 | -0.1139 | 0.9853 | -0.10313 | 15.1185
15 | 0.0016589 | 0.0004148 | -0.0016587 | -0.00041554 | 2.6283e-07 | -7.4052e-07 | 0.0025147 | 0.002515 | 0.002515 | 0.98152 | -0.13013 | 0.98135 | -0.13128 | 0.93146
16 | 0.015356 | 0.0038398 | -0.015329 | -0.0038302 | 2.7509e-05 | 9.554e-06 | 0.023277 | 0.023278 | 0.023278 | 0.98152 | -0.13013 | 0.9797 | -0.14315 | 8.6214
17 | -0.027029 | -0.0067732 | 0.027035 | 0.0067752 | 5.3695e-06 | 1.9994e-06 | 0.04082 | 0.04082 | 0.04082 | 0.9853 | -0.10313 | 0.9855 | -0.1017 | 15.1184
18 | 0.00097718 | 0.00024474 | -0.00097716 | -0.0002449 | 1.8176e-08 | -1.6065e-07 | 0.0014816 | 0.0014817 | 0.0014817 | 0.98135 | -0.13128 | 0.98134 | -0.13141 | 0.54877
19 | 0.0094814 | 0.0023761 | -0.0094792 | -0.0023754 | 2.1537e-06 | 6.1883e-07 | 0.014401 | 0.014401 | 0.014401 | 0.9797 | -0.14315 | 0.97947 | -0.14479 | 5.3336
20 | 0.0033946 | 0.00083944 | -0.0033856 | -0.0008428 | 8.9894e-06 | -3.3554e-06 | 0.0051518 | 0.0051542 | 0.0051542 | 0.9797 | -0.14315 | 0.97702 | -0.16269 | 1.909
21 | 0.006275 | 0.0015724 | -0.0062719 | -0.0015719 | 3.1142e-06 | 5.0695e-07 | 0.009533 | 0.0095332 | 0.0095332 | 0.97947 | -0.14479 | 0.97897 | -0.14838 | 3.5308
22 | 0.00244 | 0.00060581 | -0.0024364 | -0.00060966 | 3.6014e-06 | -3.8437e-06 | 0.0037141 | 0.003716 | 0.003716 | 0.97702 | -0.16269 | 0.97554 | -0.17347 | 1.3763
23 | -0.0016511 | -0.0004138 | 0.0016512 | 0.00041356 | 8.6567e-08 | -2.396e-07 | 0.002519 | 0.0025189 | 0.002519 | 0.97534 | -0.17488 | 0.97539 | -0.1745 | 0.93295
24 | -0.0016512 | -0.00041356 | 0.0016514 | 0.00041291 | 2.3432e-07 | -6.4881e-07 | 0.0025189 | 0.0025186 | 0.0025189 | 0.97539 | -0.1745 | 0.97554 | -0.17347 | 0.93291
25 | -0.032131 | -0.0080524 | 0.032175 | 0.0080691 | 4.4489e-05 | 1.6725e-05 | 0.048514 | 0.048514 | 0.048514 | 0.9855 | -0.1017 | 0.98691 | -0.091706 | 17.9682
26 | 0.019256 | 0.004827 | -0.019247 | -0.0048237 | 9.154e-06 | 3.2985e-06 | 0.029034 | 0.029034 | 0.029034 | 0.98691 | -0.091706 | 0.98642 | -0.09514 | 10.7532
27 | -0.051431 | -0.012896 | 0.051508 | 0.012926 | 7.7471e-05 | 2.9532e-05 | 0.077548 | 0.077548 | 0.077548 | 0.98691 | -0.091706 | 0.98844 | -0.080853 | 28.7213
28 | -0.099467 | -0.025063 | 0.09982 | 0.025198 | 0.00035305 | 0.00013546 | 0.14929 | 0.14929 | 0.14929 | 0.99174 | -0.057245 | 0.99538 | -0.031972 | 55.292
29 | 0.095753 | 0.024132 | -0.095458 | -0.024019 | 0.00029479 | 0.00011309 | 0.14372 | 0.14372 | 0.14372 | 0.99174 | -0.057245 | 0.9886 | -0.079306 | 53.228
30 | -0.1047 | -0.026421 | 0.10472 | 0.026431 | 2.711e-05 | 1.0335e-05 | 0.15658 | 0.15658 | 0.15658 | 0.99538 | -0.031972 | 0.99564 | -0.030128 | 28.9961
31 | 0.010589 | 0.0026541 | -0.010584 | -0.0026527 | 4.5019e-06 | 1.3675e-06 | 0.015938 | 0.015939 | 0.015939 | 0.9886 | -0.079306 | 0.98816 | -0.082378 | 5.9032
32 | -0.10789 | -0.027224 | 0.10804 | 0.02728 | 0.00014635 | 5.5818e-05 | 0.16131 | 0.16131 | 0.16131 | 0.99564 | -0.030128 | 0.99703 | -0.020476 | 29.8723
33 | -0.11249 | -0.028397 | 0.11282 | 0.028521 | 0.00032448 | 0.00012383 | 0.16796 | 0.16796 | 0.16796 | 0.99703 | -0.020476 | 1 | 0 | 31.1037
34 | 0.017555 | 0.0044044 | -0.01752 | -0.004392 | 3.5129e-05 | 1.2431e-05 | 0.026124 | 0.026124 | 0.026124 | 1 | 0 | 0.99794 | -0.01445 | 9.6757
35 | 0.087481 | 0.022051 | -0.087362 | -0.022005 | 0.00011921 | 4.5702e-05 | 0.13022 | 0.13022 | 0.13022 | 1 | 0 | 0.99859 | -0.0097444 | 48.2288
36 | 0.029462 | 0.0073893 | -0.029457 | -0.0073875 | 4.9758e-06 | 1.8639e-06 | 0.0448 | 0.0448 | 0.0448 | 0.9786 | -0.15009 | 0.97843 | -0.15131 | 16.5925
37 | 0.027484 | 0.0068932 | -0.027464 | -0.0068855 | 2.0474e-05 | 7.6388e-06 | 0.041801 | 0.041801 | 0.041801 | 0.97843 | -0.15131 | 0.97768 | -0.15668 | 15.4817
38 | 0.07196 | 0.018097 | -0.071812 | -0.01804 | 0.00014763 | 5.6516e-05 | 0.10776 | 0.10776 | 0.10776 | 0.99386 | -0.042718 | 0.99176 | -0.057467 | 39.9113
39 | -0.079411 | -0.019964 | 0.079778 | 0.020105 | 0.00036647 | 0.00014041 | 0.11892 | 0.11892 | 0.11892 | 0.99386 | -0.042718 | 0.99859 | -0.0097444 | 44.0432
40 | 0.068422 | 0.01719 | -0.06842 | -0.01719 | 2.2263e-06 | 8.519e-07 | 0.10267 | 0.10267 | 0.10267 | 0.99176 | -0.057467 | 0.99173 | -0.057701 | 38.0275
41 | 0.062608 | 0.015733 | -0.062506 | -0.015694 | 0.00010193 | 3.8964e-05 | 0.093954 | 0.093954 | 0.093954 | 0.99173 | -0.057701 | 0.99006 | -0.069418 | 34.7977
42 | 0.058638 | 0.014725 | -0.058545 | -0.014689 | 9.3035e-05 | 3.5536e-05 | 0.088141 | 0.088141 | 0.088141 | 0.99006 | -0.069418 | 0.98844 | -0.080853 | 32.6447
43 | 0.01309 | 0.0032817 | -0.013077 | -0.0032774 | 1.32e-05 | 4.3523e-06 | 0.019519 | 0.019519 | 0.019519 | 0.99794 | -0.01445 | 0.9969 | -0.021736 | 7.2293
44 | 0.0070366 | 0.0017635 | -0.0070347 | -0.0017631 | 1.8951e-06 | 3.8207e-07 | 0.010593 | 0.010593 | 0.010593 | 0.98844 | -0.080853 | 0.98817 | -0.082799 | 3.9234
45 | 0.020442 | 0.0051257 | -0.020436 | -0.0051235 | 6.1693e-06 | 2.2448e-06 | 0.031113 | 0.031113 | 0.031113 | 0.97768 | -0.15668 | 0.97738 | -0.15886 | 11.5235
46 | 0.014319 | 0.0035904 | -0.014315 | -0.003589 | 4.1708e-06 | 1.428e-06 | 0.0218 | 0.0218 | 0.0218 | 0.97738 | -0.15886 | 0.97708 | -0.16096 | 8.0742
47 | 0.0061172 | 0.001533 | -0.0061165 | -0.0015329 | 7.1189e-07 | 1.0898e-07 | 0.0093131 | 0.0093132 | 0.0093132 | 0.97738 | -0.15886 | 0.97726 | -0.1597 | 3.4493
48 | 0.014315 | 0.003589 | -0.014299 | -0.0035838 | 1.5157e-05 | 5.1903e-06 | 0.0218 | 0.021801 | 0.021801 | 0.97708 | -0.16096 | 0.97602 | -0.16861 | 8.0743
49 | 0.0092829 | 0.0023265 | -0.0092807 | -0.0023259 | 2.1278e-06 | 6.0566e-07 | 0.014152 | 0.014153 | 0.014153 | 0.97602 | -0.16861 | 0.97579 | -0.17027 | 5.2417
50 | 0.0060605 | 0.0015188 | -0.0060599 | -0.0015188 | 5.7317e-07 | 8.6127e-08 | 0.0092419 | 0.0092419 | 0.0092419 | 0.97579 | -0.17027 | 0.97569 | -0.17095 | 3.4229

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21865 | 0.054976

## res_load
| p_mw | q_mvar
0 | 0.0028428 | 0.00071248
1 | 0.0029816 | 0.00074725
2 | 0.0030917 | 0.00077486
3 | 0.0041558 | 0.0010415
4 | 0.0056421 | 0.001414
5 | 0.0058442 | 0.0014647
6 | 0.003812 | 0.00095537
7 | 0.00988 | 0.0024762
8 | 0.0050812 | 0.0012735
9 | 0.0033237 | 0.00083301
10 | 0.0066118 | 0.0016571
11 | 0.00068149 | 0.0001708
12 | 0.0024527 | 0.0006147
13 | 0.00097716 | 0.0002449
14 | 0.0032042 | 0.00080304
15 | 0.00094558 | 0.00023698
16 | 0.0016511 | 0.0004138
17 | 0.00078502 | 0.00019674
18 | 0.0062719 | 0.0015719
19 | 0.005096 | 0.0012772
20 | 0.0037143 | 0.00093089
21 | 0.0048769 | 0.0012223
22 | 0.0031658 | 0.00079343
23 | 0.010584 | 0.0026527
24 | 0.0044555 | 0.0011167
25 | 0.0041713 | 0.0010454
26 | 0.0072232 | 0.0018103
27 | 0.0019722 | 0.00049428
28 | 0.0074514 | 0.0018675
29 | 0.00339 | 0.00084963
30 | 0.0075842 | 0.0019008
31 | 0.0058119 | 0.0014566
32 | 0.0038679 | 0.00096939
33 | 0.00443 | 0.0011103
34 | 0.013077 | 0.0032774
35 | 0.019247 | 0.0048237
36 | 0.0070219 | 0.0017598
37 | 0.0061165 | 0.0015329
38 | 0.0050166 | 0.0012573
39 | 0.0032202 | 0.00080707
40 | 0.0070347 | 0.0017631
41 | 0.0060599 | 0.0015188

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1