## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1402-37_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1402-37_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1402-37_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1402-37_0_3_node_34 | 0.4 | n |  | TRUE
4 | bus_LV_1402-37_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1402-37_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1402-37_0_3_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_1402-37_0_3_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1402-37_0_3_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_1402-37_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1402-37_0_3_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1402-37_0_3_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1402-37_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1402-37_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1402-37_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1402-37_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1402-37_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1402-37_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1402-37_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1402-37_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1402-37_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1402-37_0_3_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1402-37_0_3_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1402-37_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1402-37_0_3_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_1402-37_0_3_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1402-37_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1402-37_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1402-37_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1402-37_0_3_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1402-37_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1402-37_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1402-37_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1402-37_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_MV_137_0_node_162 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1402-37_0_3_load_0 | 0 | 0.008292 | 0.0020782 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1402-37_0_3_load_1 | 1 | 0.0037766 | 0.00094651 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1402-37_0_3_load_2 | 2 | 0.0033861 | 0.00084864 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1402-37_0_3_load_34 | 3 | 0.0098131 | 0.0024594 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1402-37_0_3_load_3 | 4 | 0.005129 | 0.0012855 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1402-37_0_3_load_4 | 5 | 0.0044233 | 0.0011086 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1402-37_0_3_load_31 | 6 | 0.0038122 | 0.00095543 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1402-37_0_3_load_32 | 7 | 0.0022725 | 0.00056954 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1402-37_0_3_load_33 | 8 | 0.002272 | 0.00056942 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1402-37_0_3_load_5 | 9 | 0.010407 | 0.0026084 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1402-37_0_3_load_6 | 10 | 0.0052432 | 0.0013141 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1402-37_0_3_load_10 | 11 | 0.0084522 | 0.0021183 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1402-37_0_3_load_7 | 13 | 0.0066006 | 0.0016543 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1402-37_0_3_load_13 | 17 | 0.0066258 | 0.0016606 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1402-37_0_3_load_14 | 18 | 0.0041969 | 0.0010518 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1402-37_0_3_load_15 | 19 | 0.0042961 | 0.0010767 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1402-37_0_3_load_16 | 20 | 0.002214 | 0.00055487 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1402-37_0_3_load_30 | 21 | 0.0032403 | 0.00081209 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1402-37_0_3_load_24 | 22 | 0.0080509 | 0.0020177 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1402-37_0_3_load_17 | 23 | 0.0033957 | 0.00085104 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1402-37_0_3_load_29 | 24 | 0.0030749 | 0.00077064 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1402-37_0_3_load_23 | 25 | 0.011536 | 0.0028912 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1402-37_0_3_load_18 | 26 | 0.0025491 | 0.00063885 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1402-37_0_3_load_19 | 27 | 0.0093428 | 0.0023415 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1402-37_0_3_load_20 | 28 | 0.0072512 | 0.0018173 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1402-37_0_3_load_21 | 29 | 0.0035399 | 0.00088718 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1402-37_0_3_load_25 | 31 | 0.0016712 | 0.00041883 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1402-37_0_3_load_26 | 32 | 0.0030749 | 0.00077064 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1402-37_0_3_load_27 | 33 | 0.0032376 | 0.00081143 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1402-37_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0051115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1402-37_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.030451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1402-37_0_3_line_2 | NAYY 4x150 SE | 0 | 3 | 0.051875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1402-37_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.013785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1402-37_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.00013099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1402-37_0_3_line_5 | NAYY 4x150 SE | 3 | 8 | 0.0026806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1402-37_0_3_line_6 | NAYY 4x150 SE | 4 | 9 | 0.0072793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1402-37_0_3_line_7 | NAYY 4x150 SE | 5 | 10 | 0.0011534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1402-37_0_3_line_8 | NAYY 4x150 SE | 6 | 7 | 0.012138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1402-37_0_3_line_9 | NAYY 4x150 SE | 7 | 8 | 7.6369e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1402-37_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.017417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1402-37_0_3_line_11 | NAYY 4x150 SE | 11 | 12 | 0.017088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1402-37_0_3_line_12 | NAYY 4x150 SE | 12 | 15 | 0.022292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1402-37_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0013355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1402-37_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.040281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1402-37_0_3_line_15 | NAYY 4x150 SE | 14 | 16 | 0.005811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1402-37_0_3_line_16 | NAYY 4x150 SE | 14 | 17 | 0.015224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1402-37_0_3_line_17 | NAYY 4x150 SE | 15 | 18 | 0.013322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1402-37_0_3_line_18 | NAYY 4x150 SE | 15 | 19 | 0.013024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1402-37_0_3_line_19 | NAYY 4x150 SE | 16 | 20 | 0.046341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1402-37_0_3_line_20 | NAYY 4x150 SE | 18 | 21 | 0.017174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1402-37_0_3_line_21 | NAYY 4x150 SE | 19 | 22 | 0.022887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1402-37_0_3_line_22 | NAYY 4x150 SE | 20 | 23 | 0.03017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1402-37_0_3_line_23 | NAYY 4x150 SE | 21 | 24 | 0.0012995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1402-37_0_3_line_24 | NAYY 4x150 SE | 22 | 25 | 0.013614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1402-37_0_3_line_25 | NAYY 4x150 SE | 23 | 26 | 0.02124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1402-37_0_3_line_26 | NAYY 4x150 SE | 24 | 33 | 0.0068492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1402-37_0_3_line_27 | NAYY 4x150 SE | 25 | 30 | 0.0050782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1402-37_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.049841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1402-37_0_3_line_29 | NAYY 4x150 SE | 27 | 29 | 0.0029253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1402-37_0_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.021113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1402-37_0_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.019316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1402-37_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.0010838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1402-37_0_3_trafo_11 | 0.25 MVA 20/0.4 kV | 34 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2675275.1476 | 1185399.6883 | 2675272.9371 | 1185395.0794
1 | 2675275.1476 | 1185399.6883 | 2675288.316 | 1185427.1445
2 | 2675275.1476 | 1185399.6883 | 2675235.792 | 1185433.4847
3 | 2675272.9371 | 1185395.0794 | 2675271.9737 | 1185393.0706 | 2675267.4213 | 1185382.4477
4 | 2675288.3727 | 1185427.2626 | 2675288.316 | 1185427.1445
5 | 2675235.792 | 1185433.4847 | 2675233.3412 | 1185434.5707
6 | 2675267.4213 | 1185382.4477 | 2675267.102 | 1185381.7026 | 2675264.9813 | 1185375.5915
7 | 2675288.8714 | 1185428.3025 | 2675288.3727 | 1185427.2626
8 | 2675233.2714 | 1185434.6016 | 2675222.1745 | 1185439.5192
9 | 2675233.2714 | 1185434.6016 | 2675233.3412 | 1185434.5707
10 | 2675259.2713 | 1185359.137 | 2675264.9813 | 1185375.5915
11 | 2675252.6075 | 1185343.4757 | 2675255.7367 | 1185348.9516 | 2675259.2713 | 1185359.137
12 | 2675233.3235 | 1185354.7514 | 2675252.6075 | 1185343.4757
13 | 2675252.6075 | 1185343.4757 | 2675253.7837 | 1185342.8433
14 | 2675289.2622 | 1185323.7688 | 2675253.7837 | 1185342.8433
15 | 2675294.1861 | 1185320.6622 | 2675289.2622 | 1185323.7688
16 | 2675289.2622 | 1185323.7688 | 2675284.2746 | 1185309.3847
17 | 2675233.3235 | 1185354.7514 | 2675221.8721 | 1185361.5589
18 | 2675233.3235 | 1185354.7514 | 2675231.8352 | 1185351.1083 | 2675230.6353 | 1185342.0988
19 | 2675294.1861 | 1185320.6622 | 2675298.0156 | 1185328.1036 | 2675311.8033 | 1185363.4839
20 | 2675221.8721 | 1185361.5589 | 2675207.1092 | 1185370.335
21 | 2675227.6141 | 1185319.4122 | 2675230.6353 | 1185342.0988
22 | 2675311.8033 | 1185363.4839 | 2675320.9737 | 1185387.016 | 2675322.8121 | 1185391.5729
23 | 2675205.9922 | 1185370.9991 | 2675207.1092 | 1185370.335
24 | 2675227.6141 | 1185319.4122 | 2675225.8168 | 1185305.9171
25 | 2675322.8121 | 1185391.5729 | 2675330.7585 | 1185411.2703
26 | 2675200.1048 | 1185374.499 | 2675205.9922 | 1185370.9991
27 | 2675225.1465 | 1185300.8834 | 2675225.8168 | 1185305.9171
28 | 2675181.2125 | 1185247.4559 | 2675186.2427 | 1185256.5577 | 2675203.1748 | 1185292.1802
29 | 2675203.1748 | 1185292.1802 | 2675205.5508 | 1185293.8867
30 | 2675225.1465 | 1185300.8834 | 2675210.2172 | 1185297.2383 | 2675205.5508 | 1185293.8867
31 | 2675225.1465 | 1185300.8834 | 2675224.4833 | 1185295.9499 | 2675225.6928 | 1185292.6298 | 2675229.0636 | 1185290.4263 | 2675235.4066 | 1185288.0399
32 | 2675200.1048 | 1185374.499 | 2675199.1732 | 1185375.0528

## bus_geodata
| x | y | coords
0 | 2675275.1476 | 1185399.6883
1 | 2675272.9371 | 1185395.0794
2 | 2675288.316 | 1185427.1445
3 | 2675235.792 | 1185433.4847
4 | 2675267.4213 | 1185382.4477
5 | 2675288.3727 | 1185427.2626
6 | 2675222.1745 | 1185439.5192
7 | 2675233.2714 | 1185434.6016
8 | 2675233.3412 | 1185434.5707
9 | 2675264.9813 | 1185375.5915
10 | 2675288.8714 | 1185428.3025
11 | 2675259.2713 | 1185359.137
12 | 2675252.6075 | 1185343.4757
13 | 2675253.7837 | 1185342.8433
14 | 2675289.2622 | 1185323.7688
15 | 2675233.3235 | 1185354.7514
16 | 2675294.1861 | 1185320.6622
17 | 2675284.2746 | 1185309.3847
18 | 2675221.8721 | 1185361.5589
19 | 2675230.6353 | 1185342.0988
20 | 2675311.8033 | 1185363.4839
21 | 2675207.1092 | 1185370.335
22 | 2675227.6141 | 1185319.4122
23 | 2675322.8121 | 1185391.5729
24 | 2675205.9922 | 1185370.9991
25 | 2675225.8168 | 1185305.9171
26 | 2675330.7585 | 1185411.2703
27 | 2675203.1748 | 1185292.1802
28 | 2675181.2125 | 1185247.4559
29 | 2675205.5508 | 1185293.8867
30 | 2675225.1465 | 1185300.8834
31 | 2675235.4066 | 1185288.0399
32 | 2675199.1732 | 1185375.0528
33 | 2675200.1048 | 1185374.499
34 | 2675252.6075 | 1185343.4757

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99239 | -0.053336 | 0.008292 | 0.0020782
1 | 0.99268 | -0.05129 | 0.0037766 | 0.00094651
2 | 0.99182 | -0.057367 | 0.0033861 | 0.00084864
3 | 0.99103 | -0.062904 | 0.0098131 | 0.0024594
4 | 0.99354 | -0.045249 | 0.005129 | 0.0012855
5 | 0.99181 | -0.05738 | 0.0044233 | 0.0011086
6 | 0.99093 | -0.063606 | 0.0038122 | 0.00095543
7 | 0.991 | -0.063136 | 0.0022725 | 0.00056954
8 | 0.991 | -0.063131 | 0.002272 | 0.00056942
9 | 0.99404 | -0.041687 | 0.010407 | 0.0026084
10 | 0.99181 | -0.057441 | 0.0052432 | 0.0013141
11 | 0.99551 | -0.031351 | 0.0084522 | 0.0021183
12 | 0.99716 | -0.01979 | 0 | 0
13 | 0.99712 | -0.020076 | 0.0066006 | 0.0016543
14 | 0.99627 | -0.026065 | 0 | 0
15 | 1 | 0 | -0.15268 | -0.038153
16 | 0.9962 | -0.026542 | 0 | 0
17 | 0.99613 | -0.027079 | 0.0066258 | 0.0016606
18 | 0.99968 | -0.0022381 | 0.0041969 | 0.0010518
19 | 0.99915 | -0.0059457 | 0.0042961 | 0.0010767
20 | 0.99566 | -0.03035 | 0.002214 | 0.00055487
21 | 0.99937 | -0.0044049 | 0.0032403 | 0.00081209
22 | 0.99779 | -0.015432 | 0.0080509 | 0.0020177
23 | 0.9954 | -0.032157 | 0.0033957 | 0.00085104
24 | 0.99935 | -0.0045269 | 0.0030749 | 0.00077064
25 | 0.99715 | -0.019987 | 0.011536 | 0.0028912
26 | 0.99533 | -0.032703 | 0.0025491 | 0.00063885
27 | 0.99631 | -0.025859 | 0.0093428 | 0.0023415
28 | 0.99579 | -0.029496 | 0.0072512 | 0.0018173
29 | 0.99638 | -0.025371 | 0.0035399 | 0.00088718
30 | 0.99699 | -0.021099 | 0 | 0
31 | 0.99694 | -0.021423 | 0.0016712 | 0.00041883
32 | 0.99929 | -0.0049923 | 0.0030749 | 0.00077064
33 | 0.99929 | -0.004959 | 0.0032376 | 0.00081143
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.039546 | -0.0099143 | 0.039558 | 0.0099185 | 1.1216e-05 | 4.2476e-06 | 0.059298 | 0.059298 | 0.059298 | 0.99239 | -0.053336 | 0.99268 | -0.05129 | 21.9623
1 | 0.01306 | 0.0032737 | -0.013053 | -0.0032713 | 7.2867e-06 | 2.4094e-06 | 0.019583 | 0.019583 | 0.019583 | 0.99239 | -0.053336 | 0.99182 | -0.057367 | 7.2529
2 | 0.018194 | 0.0045624 | -0.01817 | -0.0045538 | 2.4094e-05 | 8.5976e-06 | 0.027282 | 0.027282 | 0.027282 | 0.99239 | -0.053336 | 0.99103 | -0.062904 | 10.1046
3 | -0.043334 | -0.010865 | 0.043371 | 0.010879 | 3.6298e-05 | 1.3782e-05 | 0.064959 | 0.064959 | 0.064959 | 0.99268 | -0.05129 | 0.99354 | -0.045249 | 24.059
4 | 0.0096666 | 0.0024227 | -0.0096665 | -0.0024226 | 1.7191e-08 | 4.9218e-09 | 0.014503 | 0.014503 | 0.014503 | 0.99182 | -0.057367 | 0.99181 | -0.05738 | 5.3714
5 | 0.0083572 | 0.0020944 | -0.008357 | -0.0020943 | 2.6338e-07 | 6.676e-08 | 0.012548 | 0.012548 | 0.012548 | 0.99103 | -0.062904 | 0.991 | -0.063131 | 4.6475
6 | -0.0485 | -0.012164 | 0.048524 | 0.012173 | 2.3968e-05 | 9.1242e-06 | 0.072641 | 0.072641 | 0.072641 | 0.99354 | -0.045249 | 0.99404 | -0.041687 | 26.9041
7 | 0.0052432 | 0.0013141 | -0.0052432 | -0.0013141 | 4.4535e-08 | 2.2444e-09 | 0.0078664 | 0.0078664 | 0.0078664 | 0.99181 | -0.05738 | 0.99181 | -0.057441 | 2.9135
8 | -0.0038122 | -0.00095542 | 0.0038124 | 0.00095536 | 2.482e-07 | -6.0914e-08 | 0.0057245 | 0.0057245 | 0.0057245 | 0.99093 | -0.063606 | 0.991 | -0.063136 | 2.1202
9 | -0.0060849 | -0.0015249 | 0.0060849 | 0.0015249 | 3.9771e-09 | 5.4583e-10 | 0.0091367 | 0.0091367 | 0.0091367 | 0.991 | -0.063136 | 0.991 | -0.063131 | 3.384
10 | -0.058931 | -0.014782 | 0.059016 | 0.014814 | 8.4586e-05 | 3.2307e-05 | 0.08822 | 0.08822 | 0.08822 | 0.99404 | -0.041687 | 0.99551 | -0.031351 | 32.6742
11 | -0.067468 | -0.016932 | 0.067576 | 0.016974 | 0.00010846 | 4.1492e-05 | 0.10085 | 0.10085 | 0.10085 | 0.99551 | -0.031351 | 0.99716 | -0.01979 | 37.3533
12 | -0.088982 | -0.022339 | 0.089227 | 0.022433 | 0.00024531 | 9.4057e-05 | 0.1328 | 0.1328 | 0.1328 | 0.99716 | -0.01979 | 1 | 0 | 49.1839
13 | 0.021406 | 0.0053654 | -0.021405 | -0.0053651 | 8.5028e-07 | 3.0961e-07 | 0.031943 | 0.031943 | 0.031943 | 0.99716 | -0.01979 | 0.99712 | -0.020076 | 11.8307
14 | 0.014804 | 0.0037109 | -0.014792 | -0.0037067 | 1.2268e-05 | 4.1936e-06 | 0.022093 | 0.022093 | 0.022093 | 0.99712 | -0.020076 | 0.99627 | -0.026065 | 8.1825
15 | 0.0081653 | 0.0020459 | -0.0081647 | -0.0020458 | 5.3929e-07 | 1.3176e-07 | 0.012195 | 0.012195 | 0.012195 | 0.99627 | -0.026065 | 0.9962 | -0.026542 | 4.5168
16 | 0.0066267 | 0.0016607 | -0.0066258 | -0.0016606 | 9.3063e-07 | 1.5972e-07 | 0.0098975 | 0.0098976 | 0.0098976 | 0.99627 | -0.026065 | 0.99613 | -0.027079 | 3.6658
17 | 0.016834 | 0.0042198 | -0.016829 | -0.004218 | 5.2163e-06 | 1.8316e-06 | 0.02505 | 0.02505 | 0.02505 | 1 | 0 | 0.99968 | -0.0022381 | 9.2777
18 | 0.045822 | 0.0115 | -0.045784 | -0.011486 | 3.7789e-05 | 1.4364e-05 | 0.068189 | 0.068189 | 0.068189 | 1 | 0 | 0.99915 | -0.0059457 | 25.2552
19 | 0.0081647 | 0.0020458 | -0.0081604 | -0.0020447 | 4.3008e-06 | 1.0511e-06 | 0.012195 | 0.012196 | 0.012196 | 0.9962 | -0.026542 | 0.99566 | -0.03035 | 4.5169
20 | 0.012632 | 0.0031661 | -0.012628 | -0.0031649 | 3.7889e-06 | 1.2322e-06 | 0.018803 | 0.018803 | 0.018803 | 0.99968 | -0.0022381 | 0.99937 | -0.0044049 | 6.964
21 | 0.041488 | 0.010409 | -0.041433 | -0.010388 | 5.4528e-05 | 2.0673e-05 | 0.061791 | 0.061791 | 0.061791 | 0.99915 | -0.0059457 | 0.99779 | -0.015432 | 22.8856
22 | 0.0059464 | 0.0014899 | -0.005945 | -0.0014897 | 1.4868e-06 | 1.7957e-07 | 0.0088868 | 0.0088869 | 0.0088869 | 0.99566 | -0.03035 | 0.9954 | -0.032157 | 3.2915
23 | 0.009388 | 0.0023528 | -0.0093878 | -0.0023528 | 1.5844e-07 | 4.3911e-08 | 0.013978 | 0.013978 | 0.013978 | 0.99937 | -0.0044049 | 0.99935 | -0.0045269 | 5.1771
24 | 0.033382 | 0.0083705 | -0.033361 | -0.0083626 | 2.1056e-05 | 7.9206e-06 | 0.049785 | 0.049785 | 0.049785 | 0.99779 | -0.015432 | 0.99715 | -0.019987 | 18.4388
25 | 0.0025493 | 0.00063865 | -0.0025491 | -0.00063885 | 1.9247e-07 | -2.0205e-07 | 0.0038108 | 0.0038108 | 0.0038108 | 0.9954 | -0.032157 | 0.99533 | -0.032703 | 1.4114
26 | 0.0063129 | 0.0015821 | -0.0063125 | -0.0015821 | 3.7762e-07 | 5.5505e-08 | 0.0093998 | 0.0093998 | 0.0093998 | 0.99935 | -0.0045269 | 0.99929 | -0.004959 | 3.4814
27 | 0.021825 | 0.0054713 | -0.021822 | -0.0054701 | 3.3614e-06 | 1.2266e-06 | 0.03257 | 0.03257 | 0.03257 | 0.99715 | -0.019987 | 0.99699 | -0.021099 | 12.0629
28 | 0.0072548 | 0.0018181 | -0.0072512 | -0.0018173 | 3.6514e-06 | 7.5566e-07 | 0.010835 | 0.010835 | 0.010835 | 0.99631 | -0.025859 | 0.99579 | -0.029496 | 4.0131
29 | -0.016598 | -0.0041596 | 0.016599 | 0.00416 | 1.1217e-06 | 3.9333e-07 | 0.024789 | 0.024789 | 0.024789 | 0.99631 | -0.025859 | 0.99638 | -0.025371 | 9.1811
30 | -0.020139 | -0.0050472 | 0.020151 | 0.0050515 | 1.1917e-05 | 4.3083e-06 | 0.030076 | 0.030075 | 0.030076 | 0.99638 | -0.025371 | 0.99699 | -0.021099 | 11.1391
31 | 0.0016712 | 0.00041861 | -0.0016712 | -0.00041883 | 7.4987e-08 | -2.2303e-07 | 0.0024943 | 0.0024943 | 0.0024943 | 0.99699 | -0.021099 | 0.99694 | -0.021423 | 0.92383
32 | -0.0030749 | -0.00077064 | 0.0030749 | 0.00077063 | 1.4178e-08 | -8.7451e-09 | 0.0045788 | 0.0045787 | 0.0045788 | 0.99929 | -0.0049923 | 0.99929 | -0.004959 | 1.6958

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15268 | 0.038153

## res_load
| p_mw | q_mvar
0 | 0.008292 | 0.0020782
1 | 0.0037766 | 0.00094651
2 | 0.0033861 | 0.00084864
3 | 0.0098131 | 0.0024594
4 | 0.005129 | 0.0012855
5 | 0.0044233 | 0.0011086
6 | 0.0038122 | 0.00095543
7 | 0.0022725 | 0.00056954
8 | 0.002272 | 0.00056942
9 | 0.010407 | 0.0026084
10 | 0.0052432 | 0.0013141
11 | 0.0084522 | 0.0021183
12 | 0.0066006 | 0.0016543
13 | 0.0066258 | 0.0016606
14 | 0.0041969 | 0.0010518
15 | 0.0042961 | 0.0010767
16 | 0.002214 | 0.00055487
17 | 0.0032403 | 0.00081209
18 | 0.0080509 | 0.0020177
19 | 0.0033957 | 0.00085104
20 | 0.0030749 | 0.00077064
21 | 0.011536 | 0.0028912
22 | 0.0025491 | 0.00063885
23 | 0.0093428 | 0.0023415
24 | 0.0072512 | 0.0018173
25 | 0.0035399 | 0.00088718
26 | 0.0016712 | 0.00041883
27 | 0.0030749 | 0.00077064
28 | 0.0032376 | 0.00081143

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1