## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1402-38_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1402-38_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1402-38_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1402-38_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1402-38_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1402-38_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1402-38_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1402-38_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1402-38_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1402-38_0_3_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1402-38_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1402-38_0_3_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_1402-38_0_3_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1402-38_0_3_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1402-38_0_3_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_1402-38_0_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_1402-38_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1402-38_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1402-38_0_3_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1402-38_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1402-38_0_3_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1402-38_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1402-38_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1402-38_0_3_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1402-38_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1402-38_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1402-38_0_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1402-38_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1402-38_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1402-38_0_3_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_1402-38_0_3_node_33 | 0.4 | n |  | TRUE
31 | bus_MV_137_0_node_67 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1402-38_0_3_load_0 | 0 | 0.0069351 | 0.0017381 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1402-38_0_3_load_1 | 1 | 0.010234 | 0.0025648 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1402-38_0_3_load_2 | 2 | 0.0034966 | 0.00087633 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1402-38_0_3_load_3 | 3 | 0.0099368 | 0.0024904 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1402-38_0_3_load_4 | 4 | 0.0047498 | 0.0011904 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1402-38_0_3_load_5 | 6 | 0.0073133 | 0.0018329 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1402-38_0_3_load_6 | 7 | 0.0233 | 0.0058397 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1402-38_0_3_load_8 | 8 | 0.0076892 | 0.0019271 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1402-38_0_3_load_13 | 9 | 0.0048452 | 0.0012143 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1402-38_0_3_load_24 | 12 | 0.010198 | 0.0025559 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1402-38_0_3_load_32 | 14 | 0.031295 | 0.0078432 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1402-38_0_3_load_18 | 15 | 0.0054555 | 0.0013673 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1402-38_0_3_load_10 | 16 | 0.0027331 | 0.00068499 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1402-38_0_3_load_11 | 17 | 0.0050611 | 0.0012684 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1402-38_0_3_load_29 | 18 | 0.0061844 | 0.00155 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1402-38_0_3_load_12 | 19 | 0.0044058 | 0.0011042 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1402-38_0_3_load_16 | 22 | 0.0048933 | 0.0012264 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1402-38_0_3_load_23 | 23 | 0.0043792 | 0.0010975 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1402-38_0_3_load_20 | 26 | 0.0042668 | 0.0010694 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1402-38_0_3_load_27 | 27 | 0.0065807 | 0.0016493 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1402-38_0_3_load_28 | 28 | 0.0038175 | 0.00095676 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1402-38_0_3_load_33 | 30 | 0.0046424 | 0.0011635 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1402-38_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0056199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1402-38_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.04537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1402-38_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.029799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1402-38_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0023593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1402-38_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0063716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1402-38_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.010435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1402-38_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.010546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1402-38_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.000104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1402-38_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.030141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1402-38_0_3_line_9 | NAYY 4x150 SE | 9 | 13 | 0.004706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1402-38_0_3_line_10 | NAYY 4x150 SE | 10 | 11 | 0.075023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1402-38_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.033836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1402-38_0_3_line_12 | NAYY 4x150 SE | 11 | 14 | 0.014799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1402-38_0_3_line_13 | NAYY 4x150 SE | 12 | 15 | 0.022365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1402-38_0_3_line_14 | NAYY 4x150 SE | 13 | 21 | 0.006599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1402-38_0_3_line_15 | NAYY 4x150 SE | 13 | 22 | 0.013947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1402-38_0_3_line_16 | NAYY 4x150 SE | 14 | 29 | 0.017379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1402-38_0_3_line_17 | NAYY 4x150 SE | 15 | 20 | 0.05955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1402-38_0_3_line_18 | NAYY 4x150 SE | 16 | 17 | 0.001181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1402-38_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.053829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1402-38_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.031375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1402-38_0_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.013921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1402-38_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.047448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1402-38_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.022624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1402-38_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.017259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1402-38_0_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.019107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1402-38_0_3_line_26 | NAYY 4x150 SE | 24 | 27 | 0.01342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1402-38_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.010486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1402-38_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.022583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1402-38_0_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.052963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1402-38_0_3_trafo_18 | 0.25 MVA 20/0.4 kV | 31 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2672796.3416 | 1185933.4516 | 2672794.3228 | 1185933.1243 | 2672790.7574 | 1185932.8659
1 | 2672796.3416 | 1185933.4516 | 2672805.367 | 1185934.915 | 2672816.9477 | 1185939.6474 | 2672823.1772 | 1185943.8701 | 2672829.5651 | 1185948.2503 | 2672829.9949 | 1185950.5569 | 2672827.7499 | 1185951.9193 | 2672824.2962 | 1185951.5595
2 | 2672761.1755 | 1185934.333 | 2672769.168 | 1185932.5628 | 2672774.5646 | 1185932.4839 | 2672782.893 | 1185932.296 | 2672790.7574 | 1185932.8659
3 | 2672821.9496 | 1185951.3151 | 2672824.2962 | 1185951.5595
4 | 2672755.2081 | 1185933.9497 | 2672757.4142 | 1185935.1661 | 2672761.1755 | 1185934.333
5 | 2672755.2081 | 1185933.9497 | 2672744.8178 | 1185932.9897
6 | 2672744.8178 | 1185932.9897 | 2672734.3166 | 1185932.0195
7 | 2672734.3166 | 1185932.0195 | 2672734.213 | 1185932.0099
8 | 2672734.213 | 1185932.0099 | 2672704.1997 | 1185929.237
9 | 2672699.5137 | 1185928.804 | 2672704.1997 | 1185929.237
10 | 2672784.5831 | 1185820.2394 | 2672793.2808 | 1185817.9326 | 2672799.3833 | 1185837.6405 | 2672799.4749 | 1185839.5205 | 2672799.2998 | 1185843.2539 | 2672799.4049 | 1185845.2786 | 2672801.9366 | 1185856.7495 | 2672802.0582 | 1185858.0517 | 2672801.4784 | 1185859.2899 | 2672800.5609 | 1185860.0569 | 2672804.4854 | 1185876.2253 | 2672805.3353 | 1185881.6499
11 | 2672805.3353 | 1185881.6499 | 2672771.7039 | 1185885.3678
12 | 2672784.5831 | 1185820.2394 | 2672770.2782 | 1185824.0299
13 | 2672771.7039 | 1185885.3678 | 2672749.4746 | 1185887.8252
14 | 2672699.5137 | 1185928.804 | 2672692.9449 | 1185928.0016
15 | 2672699.5137 | 1185928.804 | 2672698.3897 | 1185942.7057
16 | 2672753.2377 | 1185826.6514 | 2672760.4729 | 1185826.6281 | 2672770.2782 | 1185824.0299
17 | 2672690.2416 | 1185886.6445 | 2672703.776 | 1185888.8878 | 2672715.6179 | 1185889.7208 | 2672732.5759 | 1185889.6933 | 2672749.4746 | 1185887.8252
18 | 2672644.7602 | 1185877.1365 | 2672645.9256 | 1185877.3272
19 | 2672644.7602 | 1185877.1365 | 2672624.7002 | 1185827.1851
20 | 2672676.6503 | 1185883.635 | 2672654.4915 | 1185878.7284 | 2672645.9256 | 1185877.3272
21 | 2672690.2416 | 1185886.6445 | 2672676.6503 | 1185883.635
22 | 2672690.2416 | 1185886.6445 | 2672686.059 | 1185908.6845 | 2672691.5481 | 1185908.5288 | 2672692.9449 | 1185928.0016
23 | 2672692.9449 | 1185928.0016 | 2672670.3283 | 1185927.4138
24 | 2672692.7583 | 1185957.8392 | 2672697.5201 | 1185953.461 | 2672698.3897 | 1185942.7057
25 | 2672651.2281 | 1185926.9173 | 2672670.3283 | 1185927.4138
26 | 2672692.7583 | 1185957.8392 | 2672679.4395 | 1185956.194
27 | 2672651.2281 | 1185926.9173 | 2672640.7659 | 1185927.6222
28 | 2672657.0271 | 1185953.4254 | 2672679.4395 | 1185956.194
29 | 2672753.2377 | 1185826.6514 | 2672746.6001 | 1185860.4018 | 2672744.8981 | 1185862.9271 | 2672735.9645 | 1185865.8092 | 2672733.2681 | 1185867.8888 | 2672732.6595 | 1185870.5482

## bus_geodata
| x | y | coords
0 | 2672796.3416 | 1185933.4516
1 | 2672790.7574 | 1185932.8659
2 | 2672824.2962 | 1185951.5595
3 | 2672761.1755 | 1185934.333
4 | 2672821.9496 | 1185951.3151
5 | 2672755.2081 | 1185933.9497
6 | 2672744.8178 | 1185932.9897
7 | 2672734.3166 | 1185932.0195
8 | 2672734.213 | 1185932.0099
9 | 2672704.1997 | 1185929.237
10 | 2672805.3353 | 1185881.6499
11 | 2672784.5831 | 1185820.2394
12 | 2672771.7039 | 1185885.3678
13 | 2672699.5137 | 1185928.804
14 | 2672770.2782 | 1185824.0299
15 | 2672749.4746 | 1185887.8252
16 | 2672644.7602 | 1185877.1365
17 | 2672645.9256 | 1185877.3272
18 | 2672624.7002 | 1185827.1851
19 | 2672676.6503 | 1185883.635
20 | 2672690.2416 | 1185886.6445
21 | 2672692.9449 | 1185928.0016
22 | 2672698.3897 | 1185942.7057
23 | 2672670.3283 | 1185927.4138
24 | 2672692.7583 | 1185957.8392
25 | 2672651.2281 | 1185926.9173
26 | 2672640.7659 | 1185927.6222
27 | 2672679.4395 | 1185956.194
28 | 2672657.0271 | 1185953.4254
29 | 2672753.2377 | 1185826.6514
30 | 2672732.6595 | 1185870.5482
31 | 2672805.3353 | 1185881.6499

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98034 | -0.13808 | 0.0069351 | 0.0017381
1 | 0.98046 | -0.1372 | 0.010234 | 0.0025648
2 | 0.97979 | -0.14197 | 0.0034966 | 0.00087633
3 | 0.98156 | -0.12934 | 0.0099368 | 0.0024904
4 | 0.97977 | -0.14209 | 0.0047498 | 0.0011904
5 | 0.98189 | -0.12701 | 0 | 0
6 | 0.98242 | -0.12319 | 0.0073133 | 0.0018329
7 | 0.98308 | -0.11854 | 0.0233 | 0.0058397
8 | 0.98309 | -0.11847 | 0.0076892 | 0.0019271
9 | 0.98631 | -0.095613 | 0.0048452 | 0.0012143
10 | 0.99677 | -0.022516 | 0 | 0
11 | 0.9929 | -0.049714 | 0 | 0
12 | 0.99852 | -0.010317 | 0.010198 | 0.0025559
13 | 0.98685 | -0.091825 | 0 | 0
14 | 0.99213 | -0.055103 | 0.031295 | 0.0078432
15 | 1 | 0 | -0.16986 | -0.042644
16 | 0.99378 | -0.043227 | 0.0027331 | 0.00068499
17 | 0.9938 | -0.04312 | 0.0050611 | 0.0012684
18 | 0.9933 | -0.046594 | 0.0061844 | 0.00155
19 | 0.99443 | -0.038689 | 0.0044058 | 0.0011042
20 | 0.99479 | -0.036105 | 0 | 0
21 | 0.98775 | -0.085486 | 0 | 0
22 | 0.98654 | -0.094012 | 0.0048933 | 0.0012264
23 | 0.98746 | -0.087489 | 0.0043792 | 0.0010975
24 | 0.98628 | -0.095853 | 0 | 0
25 | 0.98735 | -0.088324 | 0 | 0
26 | 0.98728 | -0.088782 | 0.0042668 | 0.0010694
27 | 0.98608 | -0.097286 | 0.0065807 | 0.0016493
28 | 0.98595 | -0.098171 | 0.0038175 | 0.00095676
29 | 0.99202 | -0.055922 | 0 | 0
30 | 0.99167 | -0.058418 | 0.0046424 | 0.0011635
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.015186 | -0.003806 | 0.015188 | 0.0038066 | 1.8632e-06 | 6.4576e-07 | 0.02305 | 0.02305 | 0.02305 | 0.98034 | -0.13808 | 0.98046 | -0.1372 | 8.5372
1 | 0.0082509 | 0.0020679 | -0.0082465 | -0.0020667 | 4.4404e-06 | 1.1361e-06 | 0.012524 | 0.012524 | 0.012524 | 0.98034 | -0.13808 | 0.97979 | -0.14197 | 4.6385
2 | -0.025422 | -0.0063714 | 0.025449 | 0.0063817 | 2.7679e-05 | 1.0269e-05 | 0.038582 | 0.038581 | 0.038582 | 0.98046 | -0.1372 | 0.98156 | -0.12934 | 14.2895
3 | 0.0047499 | 0.0011904 | -0.0047498 | -0.0011904 | 7.6609e-08 | -2.4847e-10 | 0.0072137 | 0.0072137 | 0.0072137 | 0.97979 | -0.14197 | 0.97977 | -0.14209 | 2.6717
4 | -0.035386 | -0.0088721 | 0.035397 | 0.0088764 | 1.1442e-05 | 4.3201e-06 | 0.053645 | 0.053645 | 0.053645 | 0.98156 | -0.12934 | 0.98189 | -0.12701 | 19.8686
5 | -0.035397 | -0.0088764 | 0.035416 | 0.0088835 | 1.8738e-05 | 7.0749e-06 | 0.053645 | 0.053645 | 0.053645 | 0.98189 | -0.12701 | 0.98242 | -0.12319 | 19.8686
6 | -0.042729 | -0.010716 | 0.042757 | 0.010727 | 2.7566e-05 | 1.0469e-05 | 0.064722 | 0.064722 | 0.064722 | 0.98242 | -0.12319 | 0.98308 | -0.11854 | 23.9712
7 | -0.066058 | -0.016566 | 0.066058 | 0.016567 | 6.4882e-07 | 2.4823e-07 | 0.09999 | 0.09999 | 0.09999 | 0.98308 | -0.11854 | 0.98309 | -0.11847 | 37.0335
8 | -0.073747 | -0.018494 | 0.073982 | 0.018584 | 0.00023437 | 8.9758e-05 | 0.11163 | 0.11163 | 0.11163 | 0.98309 | -0.11847 | 0.98631 | -0.095613 | 41.344
9 | -0.078827 | -0.019798 | 0.078868 | 0.019814 | 4.1541e-05 | 1.5917e-05 | 0.11894 | 0.11894 | 0.11894 | 0.98631 | -0.095613 | 0.98685 | -0.091825 | 44.0513
10 | 0.036102 | 0.009068 | -0.035966 | -0.0090167 | 0.00013601 | 5.1339e-05 | 0.053901 | 0.053902 | 0.053902 | 0.99677 | -0.022516 | 0.9929 | -0.049714 | 19.9636
11 | -0.036102 | -0.009068 | 0.036163 | 0.0090912 | 6.1343e-05 | 2.3152e-05 | 0.053901 | 0.053901 | 0.053901 | 0.99677 | -0.022516 | 0.99852 | -0.010317 | 19.9634
12 | 0.035966 | 0.0090167 | -0.035939 | -0.0090066 | 2.6829e-05 | 1.0128e-05 | 0.053902 | 0.053902 | 0.053902 | 0.9929 | -0.049714 | 0.99213 | -0.055103 | 19.9636
13 | -0.046361 | -0.011647 | 0.046428 | 0.011672 | 6.6633e-05 | 2.5335e-05 | 0.069099 | 0.069099 | 0.069099 | 0.99852 | -0.010317 | 1 | 0 | 25.5921
14 | -0.09417 | -0.023649 | 0.094253 | 0.023681 | 8.3043e-05 | 3.1855e-05 | 0.14201 | 0.14201 | 0.14201 | 0.98685 | -0.091825 | 0.98775 | -0.085486 | 52.5966
15 | 0.015301 | 0.0038353 | -0.015297 | -0.0038337 | 4.6328e-06 | 1.6037e-06 | 0.023072 | 0.023072 | 0.023072 | 0.98685 | -0.091825 | 0.98654 | -0.094012 | 8.5453
16 | 0.0046446 | 0.0011634 | -0.004644 | -0.0011634 | 5.262e-07 | -2.2017e-08 | 0.0069658 | 0.0069658 | 0.0069658 | 0.99213 | -0.055103 | 0.99202 | -0.055922 | 2.5799
17 | 0.12264 | 0.030971 | -0.12202 | -0.030735 | 0.00061927 | 0.00023663 | 0.18257 | 0.18257 | 0.18257 | 1 | 0 | 0.99479 | -0.036105 | 33.8087
18 | -0.0089204 | -0.0022354 | 0.0089206 | 0.0022354 | 1.3147e-07 | 3.5263e-08 | 0.013357 | 0.013357 | 0.013357 | 0.99378 | -0.043227 | 0.9938 | -0.04312 | 4.9469
19 | 0.0061873 | 0.0015504 | -0.0061844 | -0.00155 | 2.8829e-06 | 4.1172e-07 | 0.0092643 | 0.0092645 | 0.0092645 | 0.99378 | -0.043227 | 0.9933 | -0.046594 | 3.4313
20 | -0.013982 | -0.0035038 | 0.01399 | 0.0035067 | 8.5803e-06 | 2.8933e-06 | 0.020935 | 0.020935 | 0.020935 | 0.9938 | -0.04312 | 0.99443 | -0.038689 | 7.7536
21 | -0.018396 | -0.0046109 | 0.018403 | 0.0046133 | 6.5821e-06 | 2.3509e-06 | 0.027527 | 0.027527 | 0.027527 | 0.99443 | -0.038689 | 0.99479 | -0.036105 | 10.1953
22 | 0.10361 | 0.026122 | -0.1029 | -0.025848 | 0.00071168 | 0.00027311 | 0.15504 | 0.15504 | 0.15504 | 0.99479 | -0.036105 | 0.98775 | -0.085486 | 57.4223
23 | 0.0086491 | 0.0021674 | -0.0086467 | -0.0021668 | 2.3968e-06 | 6.3233e-07 | 0.01303 | 0.01303 | 0.01303 | 0.98775 | -0.085486 | 0.98746 | -0.087489 | 4.8258
24 | 0.010403 | 0.0026074 | -0.010401 | -0.0026066 | 2.6518e-06 | 7.9962e-07 | 0.015692 | 0.015692 | 0.015692 | 0.98654 | -0.094012 | 0.98628 | -0.095853 | 5.8118
25 | 0.0042675 | 0.0010693 | -0.004267 | -0.0010693 | 4.9305e-07 | -5.4756e-08 | 0.0064307 | 0.0064308 | 0.0064308 | 0.98746 | -0.087489 | 0.98735 | -0.088324 | 2.3818
26 | 0.010401 | 0.0026066 | -0.010399 | -0.0026059 | 2.062e-06 | 6.2183e-07 | 0.015692 | 0.015692 | 0.015692 | 0.98628 | -0.095853 | 0.98608 | -0.097286 | 5.8118
27 | 0.004267 | 0.0010693 | -0.0042668 | -0.0010694 | 2.706e-07 | -3.0024e-08 | 0.0064308 | 0.0064308 | 0.0064308 | 0.98735 | -0.088324 | 0.98728 | -0.088782 | 2.3818
28 | 0.003818 | 0.00095665 | -0.0038175 | -0.00095676 | 4.6775e-07 | -1.0814e-07 | 0.0057613 | 0.0057614 | 0.0057614 | 0.98608 | -0.097286 | 0.98595 | -0.098171 | 2.1339
29 | 0.004644 | 0.0011634 | -0.0046424 | -0.0011635 | 1.6037e-06 | -6.6744e-08 | 0.0069658 | 0.0069661 | 0.0069661 | 0.99202 | -0.055922 | 0.99167 | -0.058418 | 2.58

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17532 | 0.044011

## res_load
| p_mw | q_mvar
0 | 0.0069351 | 0.0017381
1 | 0.010234 | 0.0025648
2 | 0.0034966 | 0.00087633
3 | 0.0099368 | 0.0024904
4 | 0.0047498 | 0.0011904
5 | 0.0073133 | 0.0018329
6 | 0.0233 | 0.0058397
7 | 0.0076892 | 0.0019271
8 | 0.0048452 | 0.0012143
9 | 0.010198 | 0.0025559
10 | 0.031295 | 0.0078432
11 | 0.0054555 | 0.0013673
12 | 0.0027331 | 0.00068499
13 | 0.0050611 | 0.0012684
14 | 0.0061844 | 0.00155
15 | 0.0044058 | 0.0011042
16 | 0.0048933 | 0.0012264
17 | 0.0043792 | 0.0010975
18 | 0.0042668 | 0.0010694
19 | 0.0065807 | 0.0016493
20 | 0.0038175 | 0.00095676
21 | 0.0046424 | 0.0011635

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1