## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1402-54_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1402-54_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1402-54_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1402-54_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1402-54_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1402-54_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1402-54_0_3_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1402-54_0_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1402-54_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1402-54_0_3_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1402-54_0_3_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1402-54_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1402-54_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1402-54_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1402-54_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1402-54_0_3_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1402-54_0_3_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_1402-54_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1402-54_0_3_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_1402-54_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1402-54_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1402-54_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_1402-54_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1402-54_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1402-54_0_3_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1402-54_0_3_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1402-54_0_3_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1402-54_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1402-54_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1402-54_0_3_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1402-54_0_3_node_29 | 0.4 | n |  | TRUE
31 | bus_MV_137_0_node_76 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1402-54_0_3_load_0 | 0 | 0.0032449 | 0.00081324 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1402-54_0_3_load_1 | 1 | 0.0033852 | 0.00084842 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1402-54_0_3_load_3 | 3 | 0.0031856 | 0.00079839 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1402-54_0_3_load_5 | 5 | 0.010635 | 0.0026655 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1402-54_0_3_load_18 | 6 | 0.0053313 | 0.0013361 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1402-54_0_3_load_16 | 7 | 0.0042577 | 0.0010671 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1402-54_0_3_load_6 | 8 | 0.0032982 | 0.0008266 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1402-54_0_3_load_7 | 11 | 0.0057791 | 0.0014484 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1402-54_0_3_load_9 | 13 | 0.0061737 | 0.0015473 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1402-54_0_3_load_22 | 15 | 0.0018395 | 0.00046103 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1402-54_0_3_load_21 | 16 | 0.0024024 | 0.00060209 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1402-54_0_3_load_10 | 17 | 0.011226 | 0.0028136 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1402-54_0_3_load_31 | 18 | 0.0038307 | 0.00096005 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1402-54_0_3_load_12 | 19 | 0.0048199 | 0.001208 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1402-54_0_3_load_14 | 20 | 0.0017449 | 0.0004373 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1402-54_0_3_load_25 | 21 | 0.0065651 | 0.0016454 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1402-54_0_3_load_13 | 22 | 0.0088854 | 0.0022269 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1402-54_0_3_load_15 | 23 | 0.0018988 | 0.00047589 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1402-54_0_3_load_24 | 24 | 0.0090371 | 0.0022649 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1402-54_0_3_load_27 | 25 | 0.0035251 | 0.00088348 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1402-54_0_3_load_23 | 26 | 0.0019112 | 0.00047898 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1402-54_0_3_load_19 | 27 | 0.0021544 | 0.00053995 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1402-54_0_3_load_20 | 28 | 0.0087305 | 0.0021881 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1402-54_0_3_load_30 | 29 | 0.0037421 | 0.00093786 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1402-54_0_3_load_29 | 30 | 0.012809 | 0.0032102 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1402-54_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1402-54_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.029491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1402-54_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0094983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1402-54_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.005667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1402-54_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.018523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1402-54_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.016442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1402-54_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0072042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1402-54_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.015229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1402-54_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.010363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1402-54_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.043649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1402-54_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.017445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1402-54_0_3_line_11 | NAYY 4x150 SE | 9 | 25 | 0.010496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1402-54_0_3_line_12 | NAYY 4x150 SE | 9 | 24 | 0.012411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1402-54_0_3_line_13 | NAYY 4x150 SE | 9 | 22 | 0.022027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1402-54_0_3_line_14 | NAYY 4x150 SE | 10 | 27 | 0.016447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1402-54_0_3_line_15 | NAYY 4x150 SE | 10 | 28 | 0.021235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1402-54_0_3_line_16 | NAYY 4x150 SE | 11 | 12 | 0.0089691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1402-54_0_3_line_17 | NAYY 4x150 SE | 12 | 13 | 0.017486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1402-54_0_3_line_18 | NAYY 4x150 SE | 13 | 17 | 0.021024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1402-54_0_3_line_19 | NAYY 4x150 SE | 14 | 15 | 0.013925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1402-54_0_3_line_20 | NAYY 4x150 SE | 14 | 16 | 0.0086067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1402-54_0_3_line_21 | NAYY 4x150 SE | 15 | 18 | 0.012619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1402-54_0_3_line_22 | NAYY 4x150 SE | 18 | 20 | 0.021864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1402-54_0_3_line_23 | NAYY 4x150 SE | 19 | 20 | 0.021395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1402-54_0_3_line_24 | NAYY 4x150 SE | 19 | 21 | 0.022714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1402-54_0_3_line_25 | NAYY 4x150 SE | 20 | 23 | 0.021565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1402-54_0_3_line_26 | NAYY 4x150 SE | 21 | 24 | 0.0033546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1402-54_0_3_line_27 | NAYY 4x150 SE | 23 | 26 | 0.020504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1402-54_0_3_line_28 | NAYY 4x150 SE | 25 | 30 | 0.00085482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1402-54_0_3_line_29 | NAYY 4x150 SE | 27 | 29 | 0.0047797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1402-54_0_3_trafo_2 | 0.25 MVA 20/0.4 kV | 31 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2
0 | 2675359.1856 | 1185322.3668 | 2675366.5153 | 1185341.3055
1 | 2675348.5413 | 1185294.8634 | 2675359.1856 | 1185322.3668
2 | 2675366.5153 | 1185341.3055 | 2675369.9435 | 1185350.1636
3 | 2675348.5413 | 1185294.8634 | 2675353.6557 | 1185292.3929
4 | 2675348.5413 | 1185294.8634 | 2675331.8073 | 1185302.8059
5 | 2675353.6557 | 1185292.3929 | 2675347.4614 | 1185277.1621
6 | 2675353.6557 | 1185292.3929 | 2675360.0352 | 1185289.0459
7 | 2675318.0491 | 1185309.336 | 2675331.8073 | 1185302.8059
8 | 2675343.5572 | 1185267.5623 | 2675347.4614 | 1185277.1621
9 | 2675398.6876 | 1185268.7675 | 2675360.0352 | 1185289.0459
10 | 2675318.0491 | 1185309.336 | 2675302.2888 | 1185316.8164
11 | 2675343.5572 | 1185267.5623 | 2675353.1735 | 1185263.3552
12 | 2675343.5572 | 1185267.5623 | 2675332.1897 | 1185272.5439
13 | 2675343.5572 | 1185267.5623 | 2675339.0842 | 1185245.9947
14 | 2675398.6876 | 1185268.7675 | 2675413.1583 | 1185260.9512
15 | 2675398.6876 | 1185268.7675 | 2675406.921 | 1185288.3413
16 | 2675294.1861 | 1185320.6622 | 2675302.2888 | 1185316.8164
17 | 2675294.1861 | 1185320.6622 | 2675298.0156 | 1185328.1036 | 2675301.3262 | 1185336.5988
18 | 2675301.3262 | 1185336.5988 | 2675308.9601 | 1185356.1882
19 | 2675279.989 | 1185297.0253 | 2675292.0435 | 1185290.054
20 | 2675279.989 | 1185297.0253 | 2675272.1459 | 1185300.5694
21 | 2675303.6538 | 1185285.1823 | 2675294.4203 | 1185288.6795 | 2675292.0435 | 1185290.054
22 | 2675303.6538 | 1185285.1823 | 2675294.5197 | 1185265.3178
23 | 2675314.149 | 1185256.8065 | 2675294.5197 | 1185265.3178
24 | 2675329.1172 | 1185273.8904 | 2675314.149 | 1185256.8065
25 | 2675274.5054 | 1185273.33 | 2675286.112 | 1185268.9634 | 2675294.5197 | 1185265.3178
26 | 2675332.1897 | 1185272.5439 | 2675329.1172 | 1185273.8904
27 | 2675255.3142 | 1185280.5502 | 2675274.5054 | 1185273.33
28 | 2675353.9566 | 1185263.0125 | 2675353.1735 | 1185263.3552
29 | 2675413.1583 | 1185260.9512 | 2675417.3638 | 1185258.6797

## bus_geodata
| x | y | coords
0 | 2675359.1856 | 1185322.3668
1 | 2675366.5153 | 1185341.3055
2 | 2675348.5413 | 1185294.8634
3 | 2675369.9435 | 1185350.1636
4 | 2675353.6557 | 1185292.3929
5 | 2675331.8073 | 1185302.8059
6 | 2675347.4614 | 1185277.1621
7 | 2675360.0352 | 1185289.0459
8 | 2675318.0491 | 1185309.336
9 | 2675343.5572 | 1185267.5623
10 | 2675398.6876 | 1185268.7675
11 | 2675302.2888 | 1185316.8164
12 | 2675294.1861 | 1185320.6622
13 | 2675301.3262 | 1185336.5988
14 | 2675279.989 | 1185297.0253
15 | 2675292.0435 | 1185290.054
16 | 2675272.1459 | 1185300.5694
17 | 2675308.9601 | 1185356.1882
18 | 2675303.6538 | 1185285.1823
19 | 2675314.149 | 1185256.8065
20 | 2675294.5197 | 1185265.3178
21 | 2675329.1172 | 1185273.8904
22 | 2675339.0842 | 1185245.9947
23 | 2675274.5054 | 1185273.33
24 | 2675332.1897 | 1185272.5439
25 | 2675353.1735 | 1185263.3552
26 | 2675255.3142 | 1185280.5502
27 | 2675413.1583 | 1185260.9512
28 | 2675406.921 | 1185288.3413
29 | 2675417.3638 | 1185258.6797
30 | 2675353.9566 | 1185263.0125
31 | 2675353.6557 | 1185292.3929

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99959 | -0.0028916 | 0.0032449 | 0.00081324
1 | 0.9994 | -0.0042251 | 0.0033852 | 0.00084842
2 | 1 | 0 | -0.13157 | -0.032814
3 | 0.99935 | -0.0045275 | 0.0031856 | 0.00079839
4 | 0.99932 | -0.0047267 | 0 | 0
5 | 0.99902 | -0.0068693 | 0.010635 | 0.0026655
6 | 0.9978 | -0.015361 | 0.0053313 | 0.0013361
7 | 0.99913 | -0.0060873 | 0.0042577 | 0.0010671
8 | 0.99844 | -0.010905 | 0.0032982 | 0.0008266
9 | 0.99692 | -0.021526 | 0 | 0
10 | 0.99822 | -0.012479 | 0 | 0
11 | 0.99786 | -0.014957 | 0.0057791 | 0.0014484
12 | 0.99764 | -0.016522 | 0 | 0
13 | 0.99721 | -0.019575 | 0.0061737 | 0.0015473
14 | 0.9948 | -0.036434 | 0 | 0
15 | 0.99485 | -0.036097 | 0.0018395 | 0.00046103
16 | 0.99477 | -0.036643 | 0.0024024 | 0.00060209
17 | 0.99687 | -0.021944 | 0.011226 | 0.0028136
18 | 0.99493 | -0.035557 | 0.0038307 | 0.00096005
19 | 0.9956 | -0.030837 | 0.0048199 | 0.001208
20 | 0.99518 | -0.033777 | 0.0017449 | 0.0004373
21 | 0.9962 | -0.026618 | 0.0065651 | 0.0016454
22 | 0.99664 | -0.023492 | 0.0088854 | 0.0022269
23 | 0.99506 | -0.034605 | 0.0018988 | 0.00047589
24 | 0.99632 | -0.025774 | 0.0090371 | 0.0022649
25 | 0.99668 | -0.023248 | 0.0035251 | 0.00088348
26 | 0.99501 | -0.035001 | 0.0019112 | 0.00047898
27 | 0.99808 | -0.013451 | 0.0021544 | 0.00053995
28 | 0.99795 | -0.014337 | 0.0087305 | 0.0021881
29 | 0.99805 | -0.01363 | 0.0037421 | 0.00093786
30 | 0.99666 | -0.023358 | 0.012809 | 0.0032102
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0065722 | 0.0016469 | -0.006571 | -0.0016467 | 1.2129e-06 | 2.0036e-07 | 0.0097835 | 0.0097836 | 0.0097836 | 0.99959 | -0.0028916 | 0.9994 | -0.0042251 | 3.6236
1 | -0.0098171 | -0.0024602 | 0.009821 | 0.0024613 | 3.9301e-06 | 1.1249e-06 | 0.014614 | 0.014614 | 0.014614 | 0.99959 | -0.0028916 | 1 | 0 | 5.4126
2 | 0.0031858 | 0.00079832 | -0.0031856 | -0.00079839 | 1.3335e-07 | -7.3167e-08 | 0.0047433 | 0.0047433 | 0.0047433 | 0.9994 | -0.0042251 | 0.99935 | -0.0045275 | 1.7568
3 | 0.083755 | 0.021023 | -0.0837 | -0.021002 | 5.4935e-05 | 2.1055e-05 | 0.12464 | 0.12464 | 0.12464 | 1 | 0 | 0.99932 | -0.0047267 | 46.1628
4 | 0.037191 | 0.0093301 | -0.037155 | -0.0093167 | 3.5403e-05 | 1.3374e-05 | 0.055344 | 0.055344 | 0.055344 | 1 | 0 | 0.99902 | -0.0068693 | 20.4978
5 | 0.064795 | 0.016262 | -0.0647 | -0.016226 | 9.5523e-05 | 3.6524e-05 | 0.09649 | 0.09649 | 0.09649 | 0.99932 | -0.0047267 | 0.9978 | -0.015361 | 35.737
6 | 0.018904 | 0.0047393 | -0.018901 | -0.004738 | 3.5622e-06 | 1.2757e-06 | 0.02815 | 0.02815 | 0.02815 | 0.99932 | -0.0047267 | 0.99913 | -0.0060873 | 10.4258
7 | 0.02652 | 0.0066512 | -0.026505 | -0.0066457 | 1.4829e-05 | 5.5042e-06 | 0.039503 | 0.039503 | 0.039503 | 0.99902 | -0.0068693 | 0.99844 | -0.010905 | 14.6306
8 | 0.059368 | 0.01489 | -0.059318 | -0.01487 | 5.0694e-05 | 1.9363e-05 | 0.088539 | 0.088539 | 0.088539 | 0.9978 | -0.015361 | 0.99692 | -0.021526 | 32.7924
9 | 0.014643 | 0.0036709 | -0.01463 | -0.0036665 | 1.2954e-05 | 4.4113e-06 | 0.021809 | 0.021809 | 0.021809 | 0.99913 | -0.0060873 | 0.99822 | -0.012479 | 8.0773
10 | 0.023207 | 0.0058191 | -0.023194 | -0.0058143 | 1.3023e-05 | 4.7807e-06 | 0.034587 | 0.034587 | 0.034587 | 0.99844 | -0.010905 | 0.99786 | -0.014957 | 12.8101
11 | 0.016338 | 0.0040951 | -0.016334 | -0.0040938 | 3.8951e-06 | 1.3613e-06 | 0.024387 | 0.024387 | 0.024387 | 0.99692 | -0.021526 | 0.99668 | -0.023248 | 9.0321
12 | 0.034092 | 0.0085478 | -0.034072 | -0.0085403 | 2.0054e-05 | 7.5515e-06 | 0.050887 | 0.050887 | 0.050887 | 0.99692 | -0.021526 | 0.99632 | -0.025774 | 18.847
13 | 0.0088878 | 0.0022275 | -0.0088854 | -0.0022269 | 2.4189e-06 | 6.4322e-07 | 0.013266 | 0.013266 | 0.013266 | 0.99692 | -0.021526 | 0.99664 | -0.023492 | 4.9134
14 | 0.0058974 | 0.0014779 | -0.0058966 | -0.0014778 | 7.9314e-07 | 9.0082e-08 | 0.008791 | 0.0087911 | 0.0087911 | 0.99822 | -0.012479 | 0.99808 | -0.013451 | 3.256
15 | 0.0087328 | 0.0021887 | -0.0087305 | -0.0021881 | 2.2455e-06 | 5.8613e-07 | 0.013018 | 0.013018 | 0.013018 | 0.99822 | -0.012479 | 0.99795 | -0.014337 | 4.8214
16 | 0.017415 | 0.004366 | -0.017411 | -0.0043646 | 3.7745e-06 | 1.3346e-06 | 0.02597 | 0.02597 | 0.02597 | 0.99786 | -0.014957 | 0.99764 | -0.016522 | 9.6184
17 | 0.017411 | 0.0043646 | -0.017404 | -0.004362 | 7.359e-06 | 2.6022e-06 | 0.02597 | 0.02597 | 0.02597 | 0.99764 | -0.016522 | 0.99721 | -0.019575 | 9.6184
18 | 0.01123 | 0.0028147 | -0.011226 | -0.0028136 | 3.6841e-06 | 1.1428e-06 | 0.016757 | 0.016758 | 0.016758 | 0.99721 | -0.019575 | 0.99687 | -0.021944 | 6.2065
19 | -0.0024024 | -0.00060201 | 0.0024026 | 0.00060187 | 1.1221e-07 | -1.3765e-07 | 0.0035935 | 0.0035934 | 0.0035935 | 0.9948 | -0.036434 | 0.99485 | -0.036097 | 1.3309
20 | 0.0024024 | 0.00060201 | -0.0024024 | -0.00060209 | 6.9352e-08 | -8.5066e-08 | 0.0035935 | 0.0035935 | 0.0035935 | 0.9948 | -0.036434 | 0.99477 | -0.036643 | 1.3309
21 | -0.0042421 | -0.0010629 | 0.0042424 | 0.0010629 | 3.17e-07 | -4.1946e-08 | 0.0063448 | 0.0063448 | 0.0063448 | 0.99485 | -0.036097 | 0.99493 | -0.035557 | 2.3499
22 | -0.0080731 | -0.0020229 | 0.008075 | 0.0020234 | 1.9889e-06 | 4.8094e-07 | 0.012074 | 0.012074 | 0.012074 | 0.99493 | -0.035557 | 0.99518 | -0.033777 | 4.4718
23 | 0.013636 | 0.0034171 | -0.01363 | -0.0034152 | 5.5451e-06 | 1.8546e-06 | 0.02038 | 0.02038 | 0.02038 | 0.9956 | -0.030837 | 0.99518 | -0.033777 | 7.5482
24 | -0.018456 | -0.0046251 | 0.018467 | 0.0046289 | 1.0784e-05 | 3.8521e-06 | 0.027584 | 0.027584 | 0.027584 | 0.9956 | -0.030837 | 0.9962 | -0.026618 | 10.2162
25 | 0.0038105 | 0.00095453 | -0.0038101 | -0.00095464 | 4.3681e-07 | -1.1216e-07 | 0.0056974 | 0.0056975 | 0.0056975 | 0.99518 | -0.033777 | 0.99506 | -0.034605 | 2.1102
26 | -0.025032 | -0.0062743 | 0.025035 | 0.0062753 | 2.9264e-06 | 1.0818e-06 | 0.03739 | 0.03739 | 0.03739 | 0.9962 | -0.026618 | 0.99632 | -0.025774 | 13.8481
27 | 0.0019113 | 0.00047875 | -0.0019112 | -0.00047898 | 1.0451e-07 | -2.2614e-07 | 0.002858 | 0.0028581 | 0.0028581 | 0.99506 | -0.034605 | 0.99501 | -0.035001 | 1.0586
28 | 0.012809 | 0.0032103 | -0.012809 | -0.0032102 | 1.9507e-07 | 6.3888e-08 | 0.019124 | 0.019124 | 0.019124 | 0.99668 | -0.023248 | 0.99666 | -0.023358 | 7.0828
29 | 0.0037422 | 0.00093783 | -0.0037421 | -0.00093786 | 9.2837e-08 | -2.6758e-08 | 0.0055791 | 0.0055791 | 0.0055791 | 0.99808 | -0.013451 | 0.99805 | -0.01363 | 2.0664

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.13157 | 0.032814

## res_load
| p_mw | q_mvar
0 | 0.0032449 | 0.00081324
1 | 0.0033852 | 0.00084842
2 | 0.0031856 | 0.00079839
3 | 0.010635 | 0.0026655
4 | 0.0053313 | 0.0013361
5 | 0.0042577 | 0.0010671
6 | 0.0032982 | 0.0008266
7 | 0.0057791 | 0.0014484
8 | 0.0061737 | 0.0015473
9 | 0.0018395 | 0.00046103
10 | 0.0024024 | 0.00060209
11 | 0.011226 | 0.0028136
12 | 0.0038307 | 0.00096005
13 | 0.0048199 | 0.001208
14 | 0.0017449 | 0.0004373
15 | 0.0065651 | 0.0016454
16 | 0.0088854 | 0.0022269
17 | 0.0018988 | 0.00047589
18 | 0.0090371 | 0.0022649
19 | 0.0035251 | 0.00088348
20 | 0.0019112 | 0.00047898
21 | 0.0021544 | 0.00053995
22 | 0.0087305 | 0.0021881
23 | 0.0037421 | 0.00093786
24 | 0.012809 | 0.0032102

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1