## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1402-58_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1402-58_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1402-58_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1402-58_0_3_node_33 | 0.4 | n |  | TRUE
4 | bus_LV_1402-58_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1402-58_0_3_node_50 | 0.4 | n |  | TRUE
6 | bus_LV_1402-58_0_3_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_1402-58_0_3_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1402-58_0_3_node_49 | 0.4 | n |  | TRUE
9 | bus_LV_1402-58_0_3_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_1402-58_0_3_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_1402-58_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1402-58_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1402-58_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1402-58_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1402-58_0_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1402-58_0_3_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1402-58_0_3_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1402-58_0_3_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1402-58_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1402-58_0_3_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1402-58_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1402-58_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1402-58_0_3_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_1402-58_0_3_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1402-58_0_3_node_46 | 0.4 | n |  | TRUE
26 | bus_LV_1402-58_0_3_node_52 | 0.4 | n |  | TRUE
27 | bus_LV_1402-58_0_3_node_53 | 0.4 | n |  | TRUE
28 | bus_LV_1402-58_0_3_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1402-58_0_3_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1402-58_0_3_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1402-58_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1402-58_0_3_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1402-58_0_3_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1402-58_0_3_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_1402-58_0_3_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1402-58_0_3_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1402-58_0_3_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1402-58_0_3_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1402-58_0_3_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_1402-58_0_3_node_47 | 0.4 | n |  | TRUE
41 | bus_LV_1402-58_0_3_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_1402-58_0_3_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_1402-58_0_3_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_1402-58_0_3_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_1402-58_0_3_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_1402-58_0_3_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_1402-58_0_3_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_1402-58_0_3_node_48 | 0.4 | n |  | TRUE
49 | bus_LV_1402-58_0_3_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_1402-58_0_3_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_1402-58_0_3_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_1402-58_0_3_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_1402-58_0_3_node_44 | 0.4 | n |  | TRUE
54 | bus_MV_137_0_node_107 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1402-58_0_3_load_0 | 0 | 0.009087 | 0.0022774 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1402-58_0_3_load_1 | 1 | 0.0043831 | 0.0010985 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1402-58_0_3_load_33 | 3 | 0.0034374 | 0.0008615 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1402-58_0_3_load_26 | 6 | 0.0064597 | 0.001619 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1402-58_0_3_load_49 | 8 | 0.0036843 | 0.00092338 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1402-58_0_3_load_24 | 9 | 0.014807 | 0.0037109 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1402-58_0_3_load_4 | 10 | 0.0018886 | 0.00047332 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1402-58_0_3_load_5 | 11 | 0.0047301 | 0.0011855 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1402-58_0_3_load_6 | 12 | 0.0010681 | 0.00026768 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1402-58_0_3_load_7 | 13 | 0.0039541 | 0.00099098 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1402-58_0_3_load_8 | 14 | 0.0029861 | 0.00074838 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1402-58_0_3_load_28 | 15 | 0.0057533 | 0.0014419 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1402-58_0_3_load_18 | 16 | 0.0011693 | 0.00029306 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1402-58_0_3_load_9 | 18 | 0.0044599 | 0.0011177 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1402-58_0_3_load_10 | 19 | 0.0052258 | 0.0013097 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1402-58_0_3_load_12 | 21 | 0.0062579 | 0.0015684 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1402-58_0_3_load_13 | 22 | 0.0068584 | 0.0017189 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1402-58_0_3_load_45 | 23 | 0.0067536 | 0.0016926 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1402-58_0_3_load_40 | 24 | 0.014949 | 0.0037465 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1402-58_0_3_load_52 | 26 | 0.0057052 | 0.0014299 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1402-58_0_3_load_53 | 27 | 0.0046271 | 0.0011597 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1402-58_0_3_load_14 | 28 | 0.0026467 | 0.00066332 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1402-58_0_3_load_27 | 30 | 0.0089939 | 0.0022541 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1402-58_0_3_load_32 | 31 | 0.001826 | 0.00045765 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1402-58_0_3_load_19 | 33 | 0.007744 | 0.0019408 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1402-58_0_3_load_20 | 34 | 0.0066691 | 0.0016714 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1402-58_0_3_load_22 | 36 | 0.0038255 | 0.00095877 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1402-58_0_3_load_25 | 38 | 0.0062013 | 0.0015542 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1402-58_0_3_load_51 | 39 | 0.0048092 | 0.0012053 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1402-58_0_3_load_47 | 40 | 0.0047384 | 0.0011876 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1402-58_0_3_load_29 | 41 | 0.0021951 | 0.00055014 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1402-58_0_3_load_30 | 42 | 0.0021848 | 0.00054755 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1402-58_0_3_load_34 | 43 | 0.0024416 | 0.00061192 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1402-58_0_3_load_35 | 44 | 0.0051313 | 0.001286 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1402-58_0_3_load_39 | 47 | 0.003751 | 0.00094008 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1402-58_0_3_load_48 | 48 | 0.0044072 | 0.0011045 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1402-58_0_3_load_38 | 49 | 0.012694 | 0.0031814 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1402-58_0_3_load_41 | 50 | 0.0067093 | 0.0016815 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1402-58_0_3_load_42 | 51 | 0.0068786 | 0.0017239 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1402-58_0_3_load_43 | 52 | 0.008412 | 0.0021083 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1402-58_0_3_load_44 | 53 | 0.006844 | 0.0017153 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1402-58_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1402-58_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.038398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1402-58_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.059842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1402-58_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.026425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1402-58_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.016123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1402-58_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.011366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1402-58_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.02292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1402-58_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.019132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1402-58_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.015855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1402-58_0_3_line_9 | NAYY 4x150 SE | 7 | 31 | 0.012509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1402-58_0_3_line_10 | NAYY 4x150 SE | 7 | 29 | 0.004173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1402-58_0_3_line_11 | NAYY 4x150 SE | 8 | 48 | 0.022692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1402-58_0_3_line_12 | NAYY 4x150 SE | 9 | 38 | 0.0014174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1402-58_0_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.025933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1402-58_0_3_line_14 | NAYY 4x150 SE | 10 | 12 | 0.004547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1402-58_0_3_line_15 | NAYY 4x150 SE | 11 | 13 | 0.0213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1402-58_0_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.027516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1402-58_0_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.02283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1402-58_0_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.0076113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1402-58_0_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.016046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1402-58_0_3_line_20 | NAYY 4x150 SE | 17 | 30 | 0.04312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1402-58_0_3_line_21 | NAYY 4x150 SE | 17 | 29 | 0.017576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1402-58_0_3_line_22 | NAYY 4x150 SE | 18 | 19 | 0.022002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1402-58_0_3_line_23 | NAYY 4x150 SE | 18 | 20 | 0.0036815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1402-58_0_3_line_24 | NAYY 4x150 SE | 19 | 21 | 0.015991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1402-58_0_3_line_25 | NAYY 4x150 SE | 20 | 22 | 0.01759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1402-58_0_3_line_26 | NAYY 4x150 SE | 21 | 23 | 0.0065522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1402-58_0_3_line_27 | NAYY 4x150 SE | 22 | 24 | 0.02263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1402-58_0_3_line_28 | NAYY 4x150 SE | 23 | 25 | 0.0089317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1402-58_0_3_line_29 | NAYY 4x150 SE | 25 | 40 | 0.010753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1402-58_0_3_line_30 | NAYY 4x150 SE | 25 | 27 | 0.060536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1402-58_0_3_line_31 | NAYY 4x150 SE | 25 | 53 | 0.016765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1402-58_0_3_line_32 | NAYY 4x150 SE | 26 | 27 | 0.018781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1402-58_0_3_line_33 | NAYY 4x150 SE | 28 | 29 | 0.022376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1402-58_0_3_line_34 | NAYY 4x150 SE | 31 | 32 | 0.031137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1402-58_0_3_line_35 | NAYY 4x150 SE | 32 | 41 | 0.032588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1402-58_0_3_line_36 | NAYY 4x150 SE | 33 | 34 | 0.017008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_1402-58_0_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.016569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1402-58_0_3_line_38 | NAYY 4x150 SE | 34 | 36 | 0.015991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1402-58_0_3_line_39 | NAYY 4x150 SE | 35 | 37 | 0.014064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1402-58_0_3_line_40 | NAYY 4x150 SE | 36 | 38 | 0.0076058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1402-58_0_3_line_41 | NAYY 4x150 SE | 37 | 39 | 0.033713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1402-58_0_3_line_42 | NAYY 4x150 SE | 39 | 40 | 0.025811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_1402-58_0_3_line_43 | NAYY 4x150 SE | 41 | 42 | 0.0030107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1402-58_0_3_line_44 | NAYY 4x150 SE | 43 | 44 | 0.026341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1402-58_0_3_line_45 | NAYY 4x150 SE | 44 | 45 | 0.03386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1402-58_0_3_line_46 | NAYY 4x150 SE | 45 | 46 | 0.032617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1402-58_0_3_line_47 | NAYY 4x150 SE | 46 | 47 | 0.037329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1402-58_0_3_line_48 | NAYY 4x150 SE | 46 | 48 | 0.021944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1402-58_0_3_line_49 | NAYY 4x150 SE | 47 | 49 | 0.035956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1402-58_0_3_line_50 | NAYY 4x150 SE | 50 | 51 | 0.00058733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1402-58_0_3_line_51 | NAYY 4x150 SE | 50 | 52 | 0.015383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1402-58_0_3_line_52 | NAYY 4x150 SE | 51 | 53 | 0.019688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1402-58_0_3_trafo_43 | 0.25 MVA 20/0.4 kV | 54 | 52 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2674825.316 | 1185820.4529 | 2674824.9354 | 1185818.8025 | 2674819.6088 | 1185800.4362 | 2674819.3316 | 1185799.0183
1 | 2674816.4805 | 1185854.7405 | 2674824.7132 | 1185845.7491 | 2674827.1049 | 1185841.2318 | 2674827.8555 | 1185834.9152 | 2674827.6792 | 1185830.6994 | 2674825.316 | 1185820.4529
2 | 2674819.3316 | 1185799.0183 | 2674760.5592 | 1185787.7532
3 | 2674816.4805 | 1185854.7405 | 2674825.5116 | 1185879.5791
4 | 2674825.5116 | 1185879.5791 | 2674811.2371 | 1185887.1498
5 | 2674825.5116 | 1185879.5791 | 2674835.9704 | 1185875.1303
6 | 2674789.2569 | 1185892.701 | 2674792.6001 | 1185892.0534 | 2674800.5455 | 1185888.9396 | 2674805.3586 | 1185887.3099 | 2674807.7992 | 1185886.8289 | 2674809.6309 | 1185886.8185 | 2674811.2371 | 1185887.1498
7 | 2674811.2371 | 1185887.1498 | 2674813.7917 | 1185888.5381 | 2674815.8473 | 1185890.7651 | 2674820.562 | 1185896.4051 | 2674823.6788 | 1185901.3477
8 | 2674835.9704 | 1185875.1303 | 2674850.5599 | 1185868.9246
9 | 2674789.2569 | 1185892.701 | 2674792.0498 | 1185899.4509 | 2674793.5803 | 1185903.3946 | 2674794.0395 | 1185904.2535
10 | 2674789.2569 | 1185892.701 | 2674785.1618 | 1185891.8382
11 | 2674835.9288 | 1185920.4466 | 2674832.7376 | 1185915.713 | 2674823.6788 | 1185901.3477
12 | 2674851.8642 | 1185868.3697 | 2674850.5599 | 1185868.9246
13 | 2674695.1503 | 1185925.4775 | 2674695.9561 | 1185924.0891 | 2674701.7004 | 1185917.5569 | 2674710.1943 | 1185913.2936 | 2674716.3195 | 1185913.2629
14 | 2674695.1503 | 1185925.4775 | 2674692.8678 | 1185929.4101
15 | 2674737.6186 | 1185913.4245 | 2674722.2761 | 1185913.2331 | 2674716.3195 | 1185913.2629
16 | 2674692.8678 | 1185929.4101 | 2674686.1992 | 1185940.8997 | 2674676.259 | 1185941.8097 | 2674672.0155 | 1185941.5748
17 | 2674737.6186 | 1185913.4245 | 2674749.3035 | 1185913.5704 | 2674760.3358 | 1185911.9959
18 | 2674672.0155 | 1185941.5748 | 2674664.4158 | 1185941.1541
19 | 2674774.6742 | 1185904.7928 | 2674760.3358 | 1185911.9959 | 2674760.3358 | 1185911.9959
20 | 2674774.6742 | 1185904.7928 | 2674758.1345 | 1185899.4277 | 2674752.727 | 1185906.4866 | 2674736.229 | 1185903.113
21 | 2674774.6742 | 1185904.7928 | 2674778.9457 | 1185902.5337 | 2674782.431 | 1185899.064 | 2674784.4344 | 1185895.6981 | 2674785.1618 | 1185891.8382
22 | 2674970.6117 | 1185941.2875 | 2674960.4477 | 1185921.7741
23 | 2674972.3124 | 1185944.5527 | 2674970.6117 | 1185941.2875
24 | 2674953.0606 | 1185907.5916 | 2674960.4477 | 1185921.7741
25 | 2674972.3124 | 1185944.5527 | 2674956.2871 | 1185951.8061
26 | 2674953.0606 | 1185907.5916 | 2674950.0337 | 1185901.7805
27 | 2674935.671 | 1185961.1375 | 2674956.2871 | 1185951.8061
28 | 2674945.9076 | 1185893.8589 | 2674950.0337 | 1185901.7805
29 | 2674945.9076 | 1185893.8589 | 2674941.0838 | 1185884.2484
30 | 2674945.9076 | 1185893.8589 | 2674999.6159 | 1185865.9305
31 | 2674945.9076 | 1185893.8589 | 2674930.728 | 1185900.9755
32 | 2675008.9905 | 1185882.204 | 2674999.6159 | 1185865.9305
33 | 2674785.1618 | 1185891.8382 | 2674774.3147 | 1185888.3563 | 2674765.8539 | 1185883.2366 | 2674764.9716 | 1185882.5887
34 | 2674802.66 | 1185932.8921 | 2674803.7055 | 1185929.2252 | 2674804.236 | 1185926.4747 | 2674803.582 | 1185923.8427 | 2674800.0013 | 1185915.4041 | 2674794.0395 | 1185904.2535
35 | 2674802.66 | 1185932.8921 | 2674786.4763 | 1185961.1781
36 | 2674873.5783 | 1185859.1334 | 2674880.8387 | 1185856.0452 | 2674886.1152 | 1185852.7647 | 2674888.4225 | 1185850.9989
37 | 2674901.5803 | 1185840.9288 | 2674888.4225 | 1185850.9989
38 | 2674873.5783 | 1185859.1334 | 2674858.8632 | 1185865.3927
39 | 2674912.5885 | 1185832.1389 | 2674901.5803 | 1185840.9288
40 | 2674851.8642 | 1185868.3697 | 2674858.8632 | 1185865.3927
41 | 2674912.5885 | 1185832.1389 | 2674917.1623 | 1185838.0552 | 2674920.9406 | 1185844.1171 | 2674929.5053 | 1185861.1806
42 | 2674941.0838 | 1185884.2484 | 2674929.5053 | 1185861.1806
43 | 2674786.4763 | 1185961.1781 | 2674784.9812 | 1185963.7913
44 | 2674827.3775 | 1186022.4469 | 2674832.8706 | 1186021.1106 | 2674836.7542 | 1186018.7355 | 2674839.1316 | 1186015.3632 | 2674839.5518 | 1186009.8318 | 2674839.2071 | 1186003.3793
45 | 2674838.2312 | 1185969.5581 | 2674837.9252 | 1185979.3823 | 2674839.2071 | 1186003.3793
46 | 2674848.1953 | 1185938.6419 | 2674841.76 | 1185955.2714 | 2674838.8805 | 1185964.0073 | 2674838.2312 | 1185969.5581
47 | 2674848.1953 | 1185938.6419 | 2674856.9776 | 1185947.9461 | 2674864.6965 | 1185955.6248 | 2674870.4768 | 1185960.2554 | 2674875.6189 | 1185963.7919
48 | 2674848.1953 | 1185938.6419 | 2674835.9288 | 1185920.4466
49 | 2674906.4553 | 1185982.2693 | 2674893.8076 | 1185974.8445 | 2674878.5277 | 1185965.7926 | 2674875.6189 | 1185963.7919
50 | 2674912.3703 | 1185909.582 | 2674912.9021 | 1185909.3327
51 | 2674898.442 | 1185916.112 | 2674912.3703 | 1185909.582
52 | 2674930.728 | 1185900.9755 | 2674912.9021 | 1185909.3327

## bus_geodata
| x | y | coords
0 | 2674825.316 | 1185820.4529
1 | 2674819.3316 | 1185799.0183
2 | 2674816.4805 | 1185854.7405
3 | 2674760.5592 | 1185787.7532
4 | 2674825.5116 | 1185879.5791
5 | 2674811.2371 | 1185887.1498
6 | 2674835.9704 | 1185875.1303
7 | 2674789.2569 | 1185892.701
8 | 2674823.6788 | 1185901.3477
9 | 2674850.5599 | 1185868.9246
10 | 2674695.1503 | 1185925.4775
11 | 2674716.3195 | 1185913.2629
12 | 2674692.8678 | 1185929.4101
13 | 2674737.6186 | 1185913.4245
14 | 2674672.0155 | 1185941.5748
15 | 2674760.3358 | 1185911.9959
16 | 2674664.4158 | 1185941.1541
17 | 2674774.6742 | 1185904.7928
18 | 2674970.6117 | 1185941.2875
19 | 2674960.4477 | 1185921.7741
20 | 2674972.3124 | 1185944.5527
21 | 2674953.0606 | 1185907.5916
22 | 2674956.2871 | 1185951.8061
23 | 2674950.0337 | 1185901.7805
24 | 2674935.671 | 1185961.1375
25 | 2674945.9076 | 1185893.8589
26 | 2675008.9905 | 1185882.204
27 | 2674999.6159 | 1185865.9305
28 | 2674764.9716 | 1185882.5887
29 | 2674785.1618 | 1185891.8382
30 | 2674736.229 | 1185903.113
31 | 2674794.0395 | 1185904.2535
32 | 2674802.66 | 1185932.8921
33 | 2674888.4225 | 1185850.9989
34 | 2674873.5783 | 1185859.1334
35 | 2674901.5803 | 1185840.9288
36 | 2674858.8632 | 1185865.3927
37 | 2674912.5885 | 1185832.1389
38 | 2674851.8642 | 1185868.3697
39 | 2674929.5053 | 1185861.1806
40 | 2674941.0838 | 1185884.2484
41 | 2674786.4763 | 1185961.1781
42 | 2674784.9812 | 1185963.7913
43 | 2674827.3775 | 1186022.4469
44 | 2674839.2071 | 1186003.3793
45 | 2674838.2312 | 1185969.5581
46 | 2674848.1953 | 1185938.6419
47 | 2674875.6189 | 1185963.7919
48 | 2674835.9288 | 1185920.4466
49 | 2674906.4553 | 1185982.2693
50 | 2674912.3703 | 1185909.582
51 | 2674912.9021 | 1185909.3327
52 | 2674898.442 | 1185916.112
53 | 2674930.728 | 1185900.9755
54 | 2674945.9076 | 1185893.8589

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98033 | -0.13793 | 0.009087 | 0.0022774
1 | 0.98008 | -0.13974 | 0.0043831 | 0.0010985
2 | 0.98127 | -0.13119 | 0 | 0
3 | 0.97978 | -0.14188 | 0.0034374 | 0.0008615
4 | 0.98192 | -0.12656 | 0 | 0
5 | 0.98024 | -0.13852 | 0 | 0
6 | 0.98339 | -0.11616 | 0.0064597 | 0.001619
7 | 0.97893 | -0.14792 | 0 | 0
8 | 0.97935 | -0.14491 | 0.0036843 | 0.00092338
9 | 0.98558 | -0.10066 | 0.014807 | 0.0037109
10 | 0.97627 | -0.16692 | 0.0018886 | 0.00047332
11 | 0.97654 | -0.16498 | 0.0047301 | 0.0011855
12 | 0.97624 | -0.16717 | 0.0010681 | 0.00026768
13 | 0.97691 | -0.16234 | 0.0039541 | 0.00099098
14 | 0.97607 | -0.16836 | 0.0029861 | 0.00074838
15 | 0.97744 | -0.15857 | 0.0057533 | 0.0014419
16 | 0.97606 | -0.16846 | 0.0011693 | 0.00029306
17 | 0.97794 | -0.15496 | 0 | 0
18 | 0.99228 | -0.053812 | 0.0044599 | 0.0011177
19 | 0.99311 | -0.047958 | 0.0052258 | 0.0013097
20 | 0.99216 | -0.054626 | 0 | 0
21 | 0.99383 | -0.042865 | 0.0062579 | 0.0015684
22 | 0.99161 | -0.058518 | 0.0068584 | 0.0017189
23 | 0.99419 | -0.040366 | 0.0067536 | 0.0016926
24 | 0.99112 | -0.061954 | 0.014949 | 0.0037465
25 | 0.99476 | -0.036354 | 0 | 0
26 | 0.99371 | -0.043753 | 0.0057052 | 0.0014299
27 | 0.99386 | -0.042671 | 0.0046271 | 0.0011597
28 | 0.97864 | -0.14998 | 0.0026467 | 0.00066332
29 | 0.97872 | -0.14936 | 0 | 0
30 | 0.97737 | -0.15901 | 0.0089939 | 0.0022541
31 | 0.97881 | -0.14873 | 0.001826 | 0.00045765
32 | 0.97861 | -0.15015 | 0 | 0
33 | 0.98809 | -0.082961 | 0.007744 | 0.0019408
34 | 0.98705 | -0.090297 | 0.0066691 | 0.0016714
35 | 0.98917 | -0.075392 | 0 | 0
36 | 0.98612 | -0.096844 | 0.0038255 | 0.00095877
37 | 0.99008 | -0.068981 | 0 | 0
38 | 0.98569 | -0.099862 | 0.0062013 | 0.0015542
39 | 0.99227 | -0.053659 | 0.0048092 | 0.0012053
40 | 0.99401 | -0.041555 | 0.0047384 | 0.0011876
41 | 0.97841 | -0.15164 | 0.0021951 | 0.00055014
42 | 0.9784 | -0.15171 | 0.0021848 | 0.00054755
43 | 0.97681 | -0.16307 | 0.0024416 | 0.00061192
44 | 0.9769 | -0.1624 | 0.0051313 | 0.001286
45 | 0.97728 | -0.15972 | 0 | 0
46 | 0.97764 | -0.15713 | 0 | 0
47 | 0.97674 | -0.16355 | 0.003751 | 0.00094008
48 | 0.9784 | -0.15163 | 0.0044072 | 0.0011045
49 | 0.97607 | -0.16833 | 0.012694 | 0.0031814
50 | 0.99838 | -0.01123 | 0.0067093 | 0.0016815
51 | 0.99832 | -0.011646 | 0.0068786 | 0.0017239
52 | 1 | 0 | -0.22282 | -0.056038
53 | 0.99637 | -0.025176 | 0.006844 | 0.0017153
54 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0078235 | 0.0019601 | -0.0078215 | -0.0019596 | 1.9588e-06 | 4.7279e-07 | 0.011875 | 0.011875 | 0.011875 | 0.98033 | -0.13793 | 0.98008 | -0.13974 | 4.3981
1 | -0.01691 | -0.0042375 | 0.016926 | 0.0042431 | 1.5786e-05 | 5.5869e-06 | 0.025668 | 0.025668 | 0.025668 | 0.98033 | -0.13793 | 0.98127 | -0.13119 | 9.5066
2 | 0.0034384 | 0.00086114 | -0.0034374 | -0.0008615 | 1.0176e-06 | -3.6248e-07 | 0.0052202 | 0.0052205 | 0.0052205 | 0.98008 | -0.13974 | 0.97978 | -0.14188 | 1.9335
3 | -0.016926 | -0.0042431 | 0.016937 | 0.004247 | 1.0863e-05 | 3.8442e-06 | 0.025668 | 0.025667 | 0.025668 | 0.98127 | -0.13119 | 0.98192 | -0.12656 | 9.5065
4 | 0.071843 | 0.018044 | -0.071723 | -0.017998 | 0.00011928 | 4.5673e-05 | 0.10888 | 0.10888 | 0.10888 | 0.98192 | -0.12656 | 0.98024 | -0.13852 | 40.3277
5 | -0.08878 | -0.022291 | 0.088908 | 0.02234 | 0.0001284 | 4.924e-05 | 0.13455 | 0.13455 | 0.13455 | 0.98192 | -0.12656 | 0.98339 | -0.11616 | 49.8341
6 | 0.039512 | 0.0099141 | -0.03946 | -0.0098946 | 5.1459e-05 | 1.9503e-05 | 0.059983 | 0.059983 | 0.059983 | 0.98024 | -0.13852 | 0.97893 | -0.14792 | 22.2161
7 | 0.032212 | 0.0080838 | -0.032183 | -0.0080731 | 2.855e-05 | 1.074e-05 | 0.048901 | 0.048902 | 0.048902 | 0.98024 | -0.13852 | 0.97935 | -0.14491 | 18.1117
8 | -0.095368 | -0.023959 | 0.095574 | 0.024038 | 0.00020608 | 7.9059e-05 | 0.14433 | 0.14433 | 0.14433 | 0.98339 | -0.11616 | 0.98558 | -0.10066 | 53.4543
9 | 0.0062083 | 0.0015553 | -0.0062077 | -0.0015552 | 6.9512e-07 | 1.1011e-07 | 0.0094368 | 0.0094368 | 0.0094368 | 0.97893 | -0.14792 | 0.97881 | -0.14873 | 3.4951
10 | 0.033252 | 0.0083393 | -0.033245 | -0.0083368 | 6.653e-06 | 2.5064e-06 | 0.050547 | 0.050547 | 0.050547 | 0.97893 | -0.14792 | 0.97872 | -0.14936 | 18.721
11 | 0.028499 | 0.0071497 | -0.028472 | -0.0071398 | 2.6552e-05 | 9.9272e-06 | 0.043304 | 0.043304 | 0.043304 | 0.97935 | -0.14491 | 0.9784 | -0.15163 | 16.0384
12 | -0.11038 | -0.027749 | 0.11039 | 0.027753 | 1.2287e-05 | 4.6895e-06 | 0.16668 | 0.16668 | 0.16668 | 0.98558 | -0.10066 | 0.98569 | -0.099862 | 30.8669
13 | -0.0071129 | -0.0017823 | 0.0071148 | 0.0017827 | 1.9019e-06 | 4.0715e-07 | 0.010841 | 0.010841 | 0.010841 | 0.97627 | -0.16692 | 0.97654 | -0.16498 | 4.0153
14 | 0.0052243 | 0.001309 | -0.0052242 | -0.001309 | 1.799e-07 | 1.2339e-08 | 0.0079627 | 0.0079627 | 0.0079627 | 0.97627 | -0.16692 | 0.97624 | -0.16717 | 2.9492
15 | -0.011845 | -0.0029682 | 0.011849 | 0.0029696 | 4.3297e-06 | 1.3987e-06 | 0.018049 | 0.018049 | 0.018049 | 0.97654 | -0.16498 | 0.97691 | -0.16234 | 6.6847
16 | 0.0041561 | 0.0010413 | -0.0041554 | -0.0010414 | 6.8904e-07 | -7.8969e-08 | 0.0063348 | 0.0063349 | 0.0063349 | 0.97624 | -0.16717 | 0.97607 | -0.16836 | 2.3462
17 | -0.015803 | -0.0039605 | 0.015812 | 0.0039634 | 8.2545e-06 | 2.8888e-06 | 0.024071 | 0.024071 | 0.024071 | 0.97691 | -0.16234 | 0.97744 | -0.15857 | 8.9153
18 | 0.0011693 | 0.00029297 | -0.0011693 | -0.00029306 | 1.5093e-08 | -8.9327e-08 | 0.0017826 | 0.0017827 | 0.0017827 | 0.97607 | -0.16836 | 0.97606 | -0.16846 | 0.66024
19 | -0.021565 | -0.0054053 | 0.021576 | 0.0054093 | 1.0792e-05 | 3.9494e-06 | 0.03283 | 0.03283 | 0.03283 | 0.97744 | -0.15857 | 0.97794 | -0.15496 | 12.1592
20 | 0.008999 | 0.0022555 | -0.0089939 | -0.0022541 | 5.0448e-06 | 1.3996e-06 | 0.013693 | 0.013693 | 0.013693 | 0.97794 | -0.15496 | 0.97737 | -0.15901 | 5.0715
21 | -0.030575 | -0.0076648 | 0.030598 | 0.0076737 | 2.3737e-05 | 8.909e-06 | 0.046523 | 0.046522 | 0.046523 | 0.97794 | -0.15496 | 0.97872 | -0.14936 | 17.2306
22 | -0.026288 | -0.0065907 | 0.026309 | 0.0065986 | 2.1337e-05 | 7.922e-06 | 0.039422 | 0.039422 | 0.039422 | 0.99228 | -0.053812 | 0.99311 | -0.047958 | 14.6009
23 | 0.021828 | 0.005473 | -0.021826 | -0.0054721 | 2.4616e-06 | 8.9923e-07 | 0.032734 | 0.032734 | 0.032734 | 0.99228 | -0.053812 | 0.99216 | -0.054626 | 12.1239
24 | -0.031535 | -0.0079084 | 0.031558 | 0.0079167 | 2.228e-05 | 8.362e-06 | 0.047252 | 0.047252 | 0.047252 | 0.99311 | -0.047958 | 0.99383 | -0.042865 | 17.5009
25 | 0.021826 | 0.0054721 | -0.021814 | -0.0054678 | 1.1762e-05 | 4.2967e-06 | 0.032734 | 0.032735 | 0.032735 | 0.99216 | -0.054626 | 0.99161 | -0.058518 | 12.1239
26 | -0.037815 | -0.0094851 | 0.037829 | 0.00949 | 1.3108e-05 | 4.9566e-06 | 0.056622 | 0.056622 | 0.056622 | 0.99383 | -0.042865 | 0.99419 | -0.040366 | 20.9711
27 | 0.014956 | 0.0037489 | -0.014949 | -0.0037465 | 7.1124e-06 | 2.4438e-06 | 0.022443 | 0.022443 | 0.022443 | 0.99161 | -0.058518 | 0.99112 | -0.061954 | 8.3122
28 | -0.044582 | -0.011183 | 0.044607 | 0.011192 | 2.4818e-05 | 9.4294e-06 | 0.06673 | 0.06673 | 0.06673 | 0.99419 | -0.040366 | 0.99476 | -0.036354 | 24.7148
29 | 0.14557 | 0.036723 | -0.14546 | -0.036683 | 0.00010613 | 4.0402e-05 | 0.21783 | 0.21783 | 0.21783 | 0.99476 | -0.036354 | 0.99401 | -0.041555 | 26.8932
30 | 0.010342 | 0.0025923 | -0.010333 | -0.0025896 | 9.041e-06 | 2.6921e-06 | 0.015471 | 0.015471 | 0.015471 | 0.99476 | -0.036354 | 0.99386 | -0.042671 | 5.7299
31 | -0.20052 | -0.050507 | 0.20083 | 0.050628 | 0.00031392 | 0.00012008 | 0.30004 | 0.30003 | 0.30004 | 0.99476 | -0.036354 | 0.99637 | -0.025176 | 37.0414
32 | -0.0057052 | -0.0014299 | 0.0057061 | 0.00143 | 8.5533e-07 | 8.5639e-08 | 0.0085432 | 0.0085432 | 0.0085432 | 0.99371 | -0.043753 | 0.99386 | -0.042671 | 3.1642
33 | -0.0026467 | -0.00066332 | 0.0026469 | 0.00066313 | 2.2612e-07 | -1.9421e-07 | 0.0040243 | 0.0040242 | 0.0040243 | 0.97864 | -0.14998 | 0.97872 | -0.14936 | 1.4905
34 | 0.0043816 | 0.0010975 | -0.0043808 | -0.0010976 | 8.6205e-07 | -5.9736e-08 | 0.0066608 | 0.006661 | 0.006661 | 0.97881 | -0.14873 | 0.97861 | -0.15015 | 2.467
35 | 0.0043808 | 0.0010976 | -0.0043799 | -0.0010977 | 9.0226e-07 | -6.2334e-08 | 0.006661 | 0.0066611 | 0.0066611 | 0.97861 | -0.15015 | 0.97841 | -0.15164 | 2.4671
36 | 0.12738 | 0.032047 | -0.12725 | -0.031998 | 0.00013024 | 4.9439e-05 | 0.19187 | 0.19187 | 0.19187 | 0.98809 | -0.082961 | 0.98705 | -0.090297 | 23.6875
37 | -0.13512 | -0.033988 | 0.13526 | 0.034043 | 0.00014277 | 5.4272e-05 | 0.20353 | 0.20353 | 0.20353 | 0.98809 | -0.082961 | 0.98917 | -0.075392 | 25.1273
38 | 0.12058 | 0.030327 | -0.12047 | -0.030285 | 0.00010995 | 4.1676e-05 | 0.18182 | 0.18182 | 0.18182 | 0.98705 | -0.090297 | 0.98612 | -0.096844 | 22.4463
39 | -0.13526 | -0.034043 | 0.13539 | 0.034089 | 0.00012118 | 4.6066e-05 | 0.20353 | 0.20353 | 0.20353 | 0.98917 | -0.075392 | 0.99008 | -0.068981 | 25.1272
40 | 0.11664 | 0.029326 | -0.11659 | -0.029308 | 4.9028e-05 | 1.8566e-05 | 0.17604 | 0.17604 | 0.17604 | 0.98612 | -0.096844 | 0.98569 | -0.099862 | 21.7337
41 | -0.13539 | -0.034089 | 0.13568 | 0.034199 | 0.00029048 | 0.00011042 | 0.20353 | 0.20353 | 0.20353 | 0.99008 | -0.068981 | 0.99227 | -0.053659 | 25.1272
42 | -0.14049 | -0.035404 | 0.14072 | 0.035495 | 0.00023843 | 9.0702e-05 | 0.21074 | 0.21074 | 0.21074 | 0.99227 | -0.053659 | 0.99401 | -0.041555 | 26.0175
43 | 0.0021848 | 0.00054752 | -0.0021848 | -0.00054755 | 2.0742e-08 | -2.9833e-08 | 0.0033227 | 0.0033228 | 0.0033228 | 0.97841 | -0.15164 | 0.9784 | -0.15171 | 1.2306
44 | -0.0024416 | -0.00061192 | 0.0024418 | 0.00061168 | 2.2737e-07 | -2.4231e-07 | 0.0037194 | 0.0037193 | 0.0037194 | 0.97681 | -0.16307 | 0.9769 | -0.1624 | 1.3776
45 | -0.0075731 | -0.0018977 | 0.0075759 | 0.0018984 | 2.8114e-06 | 6.572e-07 | 0.011535 | 0.011535 | 0.011535 | 0.9769 | -0.1624 | 0.97728 | -0.15972 | 4.2723
46 | -0.0075759 | -0.0018984 | 0.0075786 | 0.001899 | 2.7081e-06 | 6.3274e-07 | 0.011535 | 0.011535 | 0.011535 | 0.97728 | -0.15972 | 0.97764 | -0.15713 | 4.2723
47 | 0.016468 | 0.0041295 | -0.016453 | -0.0041243 | 1.4636e-05 | 5.1614e-06 | 0.025066 | 0.025066 | 0.025066 | 0.97764 | -0.15713 | 0.97674 | -0.16355 | 9.2838
48 | -0.024047 | -0.0060284 | 0.024065 | 0.0060352 | 1.8344e-05 | 6.7799e-06 | 0.036601 | 0.036601 | 0.036601 | 0.97764 | -0.15713 | 0.9784 | -0.15163 | 13.5559
49 | 0.012702 | 0.0031842 | -0.012694 | -0.0031814 | 8.4025e-06 | 2.782e-06 | 0.019352 | 0.019352 | 0.019352 | 0.97674 | -0.16355 | 0.97607 | -0.16833 | 7.1674
50 | 0.21496 | 0.054222 | -0.21495 | -0.054218 | 1.2549e-05 | 4.8037e-06 | 0.32051 | 0.32051 | 0.32051 | 0.99838 | -0.01123 | 0.99832 | -0.011646 | 39.569
51 | -0.22167 | -0.055904 | 0.22202 | 0.056038 | 0.00034952 | 0.00013383 | 0.33051 | 0.33051 | 0.33051 | 0.99838 | -0.01123 | 1 | 0 | 40.8035
52 | 0.20807 | 0.052494 | -0.20768 | -0.052343 | 0.00039418 | 0.00015084 | 0.31026 | 0.31026 | 0.31026 | 0.99832 | -0.011646 | 0.99637 | -0.025176 | 38.3032

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23123 | 0.058146

## res_load
| p_mw | q_mvar
0 | 0.009087 | 0.0022774
1 | 0.0043831 | 0.0010985
2 | 0.0034374 | 0.0008615
3 | 0.0064597 | 0.001619
4 | 0.0036843 | 0.00092338
5 | 0.014807 | 0.0037109
6 | 0.0018886 | 0.00047332
7 | 0.0047301 | 0.0011855
8 | 0.0010681 | 0.00026768
9 | 0.0039541 | 0.00099098
10 | 0.0029861 | 0.00074838
11 | 0.0057533 | 0.0014419
12 | 0.0011693 | 0.00029306
13 | 0.0044599 | 0.0011177
14 | 0.0052258 | 0.0013097
15 | 0.0062579 | 0.0015684
16 | 0.0068584 | 0.0017189
17 | 0.0067536 | 0.0016926
18 | 0.014949 | 0.0037465
19 | 0.0057052 | 0.0014299
20 | 0.0046271 | 0.0011597
21 | 0.0026467 | 0.00066332
22 | 0.0089939 | 0.0022541
23 | 0.001826 | 0.00045765
24 | 0.007744 | 0.0019408
25 | 0.0066691 | 0.0016714
26 | 0.0038255 | 0.00095877
27 | 0.0062013 | 0.0015542
28 | 0.0048092 | 0.0012053
29 | 0.0047384 | 0.0011876
30 | 0.0021951 | 0.00055014
31 | 0.0021848 | 0.00054755
32 | 0.0024416 | 0.00061192
33 | 0.0051313 | 0.001286
34 | 0.003751 | 0.00094008
35 | 0.0044072 | 0.0011045
36 | 0.012694 | 0.0031814
37 | 0.0067093 | 0.0016815
38 | 0.0068786 | 0.0017239
39 | 0.008412 | 0.0021083
40 | 0.006844 | 0.0017153

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1