## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1403-12_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1403-12_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1403-12_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1403-12_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1403-12_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1403-12_0_4_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_1403-12_0_4_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_1403-12_0_4_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1403-12_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1403-12_0_4_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1403-12_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1403-12_0_4_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_1403-12_0_4_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_1403-12_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1403-12_0_4_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1403-12_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1403-12_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1403-12_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1403-12_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1403-12_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1403-12_0_4_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_1403-12_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1403-12_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1403-12_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1403-12_0_4_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1403-12_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1403-12_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1403-12_0_4_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1403-12_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1403-12_0_4_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1403-12_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1403-12_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_MV_138_0_node_272 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1403-12_0_4_load_0 | 0 | 0.0062827 | 0.0015746 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1403-12_0_4_load_1 | 1 | 0.006118 | 0.0015333 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1403-12_0_4_load_3 | 3 | 0.010278 | 0.0025759 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1403-12_0_4_load_29 | 5 | 0.019877 | 0.0049817 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1403-12_0_4_load_5 | 8 | 0.0053272 | 0.0013351 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1403-12_0_4_load_6 | 10 | 0.0026639 | 0.00066762 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1403-12_0_4_load_20 | 11 | 0.0050536 | 0.0012665 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1403-12_0_4_load_7 | 13 | 0.0038684 | 0.00096951 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1403-12_0_4_load_18 | 14 | 0.0013832 | 0.00034667 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1403-12_0_4_load_24 | 15 | 0.0022932 | 0.00057473 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1403-12_0_4_load_8 | 16 | 0.016705 | 0.0041868 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1403-12_0_4_load_10 | 18 | 0.029622 | 0.007424 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1403-12_0_4_load_11 | 19 | 0.0031955 | 0.00080088 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1403-12_0_4_load_31 | 20 | 0.0030552 | 0.00076572 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1403-12_0_4_load_12 | 23 | 0.0076899 | 0.0019273 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1403-12_0_4_load_13 | 24 | 0.0046614 | 0.0011682 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1403-12_0_4_load_15 | 25 | 0.0043067 | 0.0010794 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1403-12_0_4_load_17 | 26 | 0.004766 | 0.0011945 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1403-12_0_4_load_25 | 27 | 0.0042018 | 0.0010531 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1403-12_0_4_load_22 | 28 | 0.0026933 | 0.000675 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1403-12_0_4_load_30 | 29 | 0.020213 | 0.0050658 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1403-12_0_4_load_23 | 30 | 0.0047937 | 0.0012014 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1403-12_0_4_load_27 | 31 | 0.0084358 | 0.0021142 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1403-12_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.034021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1403-12_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.061592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1403-12_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0034054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1403-12_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.10599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1403-12_0_4_line_4 | NAYY 4x150 SE | 3 | 7 | 0.05164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1403-12_0_4_line_5 | NAYY 4x150 SE | 4 | 8 | 0.068092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1403-12_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.023475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1403-12_0_4_line_7 | NAYY 4x150 SE | 6 | 29 | 0.022128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1403-12_0_4_line_8 | NAYY 4x150 SE | 6 | 21 | 0.042712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1403-12_0_4_line_9 | NAYY 4x150 SE | 7 | 9 | 0.008649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1403-12_0_4_line_10 | NAYY 4x150 SE | 8 | 10 | 0.0064201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1403-12_0_4_line_11 | NAYY 4x150 SE | 9 | 20 | 0.044368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1403-12_0_4_line_12 | NAYY 4x150 SE | 10 | 13 | 0.071354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1403-12_0_4_line_13 | NAYY 4x150 SE | 11 | 12 | 0.017287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1403-12_0_4_line_14 | NAYY 4x150 SE | 12 | 28 | 0.0030701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1403-12_0_4_line_15 | NAYY 4x150 SE | 12 | 30 | 0.025366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1403-12_0_4_line_16 | NAYY 4x150 SE | 13 | 14 | 0.041156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1403-12_0_4_line_17 | NAYY 4x150 SE | 13 | 15 | 0.029112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1403-12_0_4_line_18 | NAYY 4x150 SE | 16 | 17 | 0.023278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1403-12_0_4_line_19 | NAYY 4x150 SE | 16 | 18 | 0.052911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1403-12_0_4_line_20 | NAYY 4x150 SE | 17 | 19 | 0.023127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1403-12_0_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.031462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1403-12_0_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.018964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1403-12_0_4_line_23 | NAYY 4x150 SE | 21 | 22 | 0.007101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1403-12_0_4_line_24 | NAYY 4x150 SE | 22 | 26 | 0.032067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1403-12_0_4_line_25 | NAYY 4x150 SE | 22 | 23 | 0.0067262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1403-12_0_4_line_26 | NAYY 4x150 SE | 23 | 24 | 0.0088278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1403-12_0_4_line_27 | NAYY 4x150 SE | 24 | 25 | 0.022661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1403-12_0_4_line_28 | NAYY 4x150 SE | 25 | 27 | 0.0015484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1403-12_0_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.0080525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1403-12_0_4_line_30 | NAYY 4x150 SE | 30 | 31 | 0.013666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1403-12_0_4_trafo_28 | 0.25 MVA 20/0.4 kV | 32 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2655944.9113 | 1187745.0532 | 2655970.4685 | 1187722.5969
1 | 2655960.2185 | 1187794.1294 | 2655935.5622 | 1187760.6359 | 2655934.763 | 1187754.7251 | 2655938.4699 | 1187750.713 | 2655944.9113 | 1187745.0532
2 | 2655970.4685 | 1187722.5969 | 2655973.0267 | 1187720.3491
3 | 2655858.0375 | 1187821.169 | 2655886.6033 | 1187810.1514 | 2655911.3199 | 1187803.7005 | 2655945.2702 | 1187796.947 | 2655960.2185 | 1187794.1294
4 | 2656021.2867 | 1187703.6714 | 2655985.4772 | 1187712.564 | 2655975.6149 | 1187718.0749 | 2655973.0267 | 1187720.3491
5 | 2655858.0375 | 1187821.169 | 2655853.4838 | 1187819.4589 | 2655829.7658 | 1187801.4611 | 2655819.5693 | 1187796.2076 | 2655805.4288 | 1187788.4826 | 2655800.9648 | 1187784.6697
6 | 2655929.8784 | 1187661.0046 | 2655920.9403 | 1187669.6705 | 2655920.9875 | 1187672.7838 | 2655926.2878 | 1187678.6922
7 | 2655929.8784 | 1187661.0046 | 2655945.8596 | 1187645.6563
8 | 2655909.8998 | 1187623.2303 | 2655929.8784 | 1187661.0046
9 | 2656021.2867 | 1187703.6714 | 2656029.6836 | 1187701.5043
10 | 2655800.9648 | 1187784.6697 | 2655796.0831 | 1187780.4999
11 | 2656029.6836 | 1187701.5043 | 2656013.0558 | 1187660.359
12 | 2655738.4218 | 1187738.8123 | 2655739.7455 | 1187739.1991 | 2655749.5576 | 1187744.7935 | 2655783.4268 | 1187769.6894 | 2655796.0831 | 1187780.4999
13 | 2655860.4735 | 1187653.2529 | 2655852.6396 | 1187660.495 | 2655847.689 | 1187664.8882
14 | 2655860.4735 | 1187653.2529 | 2655862.9307 | 1187651.4123
15 | 2655860.4735 | 1187653.2529 | 2655842.0046 | 1187635.8656
16 | 2655700.0917 | 1187750.559 | 2655724.2335 | 1187739.4661 | 2655733.8111 | 1187737.4651 | 2655738.4218 | 1187738.8123
17 | 2655738.4218 | 1187738.8123 | 2655728.086 | 1187711.5974
18 | 2655945.1323 | 1187600.2018 | 2655961.7033 | 1187616.5502
19 | 2655982.1525 | 1187654.4558 | 2655990.0559 | 1187646.3251 | 2655989.8988 | 1187644.3669 | 2655961.7033 | 1187616.5502
20 | 2655945.1323 | 1187600.2018 | 2655925.774 | 1187612.8546
21 | 2655982.1525 | 1187654.4558 | 2656013.0558 | 1187660.359
22 | 2655909.8998 | 1187623.2303 | 2655925.774 | 1187612.8546
23 | 2655903.9434 | 1187627.1214 | 2655909.8998 | 1187623.2303
24 | 2655903.9434 | 1187627.1214 | 2655880.7363 | 1187604.9915
25 | 2655903.9434 | 1187627.1214 | 2655897.9677 | 1187630.2088
26 | 2655890.1248 | 1187634.261 | 2655897.9677 | 1187630.2088
27 | 2655890.1248 | 1187634.261 | 2655876.2768 | 1187641.4158 | 2655870.615 | 1187645.6566
28 | 2655869.3757 | 1187646.5849 | 2655870.615 | 1187645.6566
29 | 2655862.9307 | 1187651.4123 | 2655869.3757 | 1187646.5849
30 | 2655842.0046 | 1187635.8656 | 2655832.0539 | 1187626.4978

## bus_geodata
| x | y | coords
0 | 2655944.9113 | 1187745.0532
1 | 2655970.4685 | 1187722.5969
2 | 2655960.2185 | 1187794.1294
3 | 2655973.0267 | 1187720.3491
4 | 2655858.0375 | 1187821.169
5 | 2655926.2878 | 1187678.6922
6 | 2655929.8784 | 1187661.0046
7 | 2656021.2867 | 1187703.6714
8 | 2655800.9648 | 1187784.6697
9 | 2656029.6836 | 1187701.5043
10 | 2655796.0831 | 1187780.4999
11 | 2655847.689 | 1187664.8882
12 | 2655860.4735 | 1187653.2529
13 | 2655738.4218 | 1187738.8123
14 | 2655700.0917 | 1187750.559
15 | 2655728.086 | 1187711.5974
16 | 2655961.7033 | 1187616.5502
17 | 2655945.1323 | 1187600.2018
18 | 2655982.1525 | 1187654.4558
19 | 2655925.774 | 1187612.8546
20 | 2656013.0558 | 1187660.359
21 | 2655909.8998 | 1187623.2303
22 | 2655903.9434 | 1187627.1214
23 | 2655897.9677 | 1187630.2088
24 | 2655890.1248 | 1187634.261
25 | 2655870.615 | 1187645.6566
26 | 2655880.7363 | 1187604.9915
27 | 2655869.3757 | 1187646.5849
28 | 2655862.9307 | 1187651.4123
29 | 2655945.8596 | 1187645.6563
30 | 2655842.0046 | 1187635.8656
31 | 2655832.0539 | 1187626.4978
32 | 2655945.8596 | 1187645.6563

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97714 | -0.16064 | 0.0062827 | 0.0015746
1 | 0.97823 | -0.15287 | 0.006118 | 0.0015333
2 | 0.97573 | -0.17067 | 0 | 0
3 | 0.97836 | -0.15188 | 0.010278 | 0.0025759
4 | 0.97332 | -0.18801 | 0 | 0
5 | 0.99933 | -0.0046604 | 0.019877 | 0.0049817
6 | 1 | 0 | -0.18015 | -0.045185
7 | 0.98125 | -0.13134 | 0 | 0
8 | 0.97177 | -0.19918 | 0.0053272 | 0.0013351
9 | 0.98173 | -0.12791 | 0 | 0
10 | 0.97167 | -0.19987 | 0.0026639 | 0.00066762
11 | 0.99298 | -0.048947 | 0.0050536 | 0.0012665
12 | 0.99311 | -0.048063 | 0 | 0
13 | 0.97088 | -0.20558 | 0.0038684 | 0.00096951
14 | 0.9708 | -0.20618 | 0.0013832 | 0.00034667
15 | 0.97078 | -0.20628 | 0.0022932 | 0.00057473
16 | 0.99156 | -0.058695 | 0.016705 | 0.0041868
17 | 0.99304 | -0.048354 | 0 | 0
18 | 0.98611 | -0.097011 | 0.029622 | 0.007424
19 | 0.99451 | -0.038111 | 0.0031955 | 0.00080088
20 | 0.98421 | -0.11038 | 0.0030552 | 0.00076572
21 | 0.99576 | -0.029428 | 0 | 0
22 | 0.99528 | -0.032761 | 0 | 0
23 | 0.99488 | -0.035598 | 0.0076899 | 0.0019273
24 | 0.99445 | -0.03864 | 0.0046614 | 0.0011682
25 | 0.99349 | -0.045391 | 0.0043067 | 0.0010794
26 | 0.99507 | -0.034302 | 0.004766 | 0.0011945
27 | 0.99343 | -0.045786 | 0.0042018 | 0.0010531
28 | 0.99319 | -0.047495 | 0.0026933 | 0.000675
29 | 0.99936 | -0.0044669 | 0.020213 | 0.0050658
30 | 0.99263 | -0.051461 | 0.0047937 | 0.0012014
31 | 0.99246 | -0.052629 | 0.0084358 | 0.0021142
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.021909 | -0.0054983 | 0.021933 | 0.005507 | 2.3635e-05 | 8.6637e-06 | 0.033366 | 0.033366 | 0.033366 | 0.97714 | -0.16064 | 0.97823 | -0.15287 | 12.3579
1 | 0.015626 | 0.0039237 | -0.015605 | -0.0039161 | 2.1769e-05 | 7.6021e-06 | 0.023799 | 0.023799 | 0.023799 | 0.97714 | -0.16064 | 0.97573 | -0.17067 | 8.8145
2 | -0.028051 | -0.0070403 | 0.028055 | 0.0070417 | 3.8694e-06 | 1.4455e-06 | 0.042673 | 0.042673 | 0.042673 | 0.97823 | -0.15287 | 0.97836 | -0.15188 | 15.8047
3 | 0.015605 | 0.0039161 | -0.015567 | -0.003903 | 3.7461e-05 | 1.3088e-05 | 0.023799 | 0.0238 | 0.0238 | 0.97573 | -0.17067 | 0.97332 | -0.18801 | 8.8147
4 | -0.038333 | -0.0096176 | 0.038442 | 0.0096591 | 0.00010954 | 4.1481e-05 | 0.058305 | 0.058304 | 0.058305 | 0.97836 | -0.15188 | 0.98125 | -0.13134 | 21.5943
5 | 0.015567 | 0.003903 | -0.015543 | -0.0038946 | 2.4067e-05 | 8.4118e-06 | 0.0238 | 0.0238 | 0.0238 | 0.97332 | -0.18801 | 0.97177 | -0.19918 | 8.8148
6 | -0.019877 | -0.0049817 | 0.01989 | 0.0049863 | 1.2832e-05 | 4.6276e-06 | 0.029597 | 0.029597 | 0.029597 | 0.99933 | -0.0046604 | 1 | 0 | 10.962
7 | 0.020225 | 0.0050703 | -0.020213 | -0.0050658 | 1.2507e-05 | 4.5201e-06 | 0.030096 | 0.030096 | 0.030096 | 1 | 0 | 0.99936 | -0.0044669 | 11.1466
8 | 0.13923 | 0.035128 | -0.13866 | -0.034909 | 0.00057245 | 0.00021906 | 0.20726 | 0.20726 | 0.20726 | 1 | 0 | 0.99576 | -0.029428 | 38.3817
9 | -0.038442 | -0.0096591 | 0.03846 | 0.0096661 | 1.8346e-05 | 6.947e-06 | 0.058304 | 0.058304 | 0.058304 | 0.98125 | -0.13134 | 0.98173 | -0.12791 | 21.5942
10 | 0.010216 | 0.0025595 | -0.010215 | -0.0025592 | 9.8029e-07 | 2.9751e-07 | 0.015643 | 0.015643 | 0.015643 | 0.97177 | -0.19918 | 0.97167 | -0.19987 | 5.7936
11 | -0.03846 | -0.0096661 | 0.038555 | 0.0097017 | 9.4114e-05 | 3.5635e-05 | 0.058304 | 0.058304 | 0.058304 | 0.98173 | -0.12791 | 0.98421 | -0.11038 | 21.5942
12 | 0.0075511 | 0.0018916 | -0.0075451 | -0.0018902 | 5.9537e-06 | 1.4068e-06 | 0.011563 | 0.011564 | 0.011564 | 0.97167 | -0.19987 | 0.97088 | -0.20558 | 4.2829
13 | -0.0050536 | -0.0012665 | 0.0050542 | 0.0012666 | 6.1863e-07 | 1.428e-08 | 0.0075729 | 0.0075728 | 0.0075729 | 0.99298 | -0.048947 | 0.99311 | -0.048063 | 2.8048
14 | -0.018291 | -0.0045846 | 0.018293 | 0.0045851 | 1.439e-06 | 5.1372e-07 | 0.027407 | 0.027407 | 0.027407 | 0.99311 | -0.048063 | 0.99319 | -0.047495 | 10.1506
15 | 0.013237 | 0.0033181 | -0.013231 | -0.003316 | 6.2266e-06 | 2.0668e-06 | 0.019834 | 0.019834 | 0.019834 | 0.99311 | -0.048063 | 0.99263 | -0.051461 | 7.3459
16 | 0.0013833 | 0.0003462 | -0.0013832 | -0.00034667 | 1.1543e-07 | -4.6451e-07 | 0.00212 | 0.0021202 | 0.0021202 | 0.97088 | -0.20558 | 0.9708 | -0.20618 | 0.78525
17 | 0.0022934 | 0.00057445 | -0.0022932 | -0.00057473 | 2.2443e-07 | -2.7365e-07 | 0.0035149 | 0.003515 | 0.003515 | 0.97088 | -0.20558 | 0.97078 | -0.20628 | 1.3019
18 | -0.088398 | -0.022254 | 0.088525 | 0.022303 | 0.00012788 | 4.8582e-05 | 0.13269 | 0.13269 | 0.13269 | 0.99156 | -0.058695 | 0.99304 | -0.048354 | 24.5725
19 | 0.071692 | 0.018067 | -0.07131 | -0.017921 | 0.00038242 | 0.0001464 | 0.10762 | 0.10762 | 0.10762 | 0.99156 | -0.058695 | 0.98611 | -0.097011 | 39.8602
20 | -0.088525 | -0.022303 | 0.088652 | 0.022351 | 0.00012704 | 4.8263e-05 | 0.13269 | 0.13269 | 0.13269 | 0.99304 | -0.048354 | 0.99451 | -0.038111 | 24.5725
21 | 0.041688 | 0.010497 | -0.04161 | -0.010467 | 7.7731e-05 | 2.9496e-05 | 0.062923 | 0.062923 | 0.062923 | 0.98611 | -0.097011 | 0.98421 | -0.11038 | 23.3049
22 | -0.091848 | -0.023152 | 0.09196 | 0.023194 | 0.00011182 | 4.2515e-05 | 0.13747 | 0.13747 | 0.13747 | 0.99451 | -0.038111 | 0.99576 | -0.029428 | 25.4579
23 | 0.046699 | 0.011715 | -0.046678 | -0.011707 | 2.1581e-05 | 8.2082e-06 | 0.069789 | 0.069789 | 0.069789 | 0.99576 | -0.029428 | 0.99528 | -0.032761 | 25.8478
24 | 0.004767 | 0.0011944 | -0.004766 | -0.0011945 | 1.0164e-06 | -2.5737e-08 | 0.0071269 | 0.007127 | 0.007127 | 0.99528 | -0.032761 | 0.99507 | -0.034302 | 2.6396
25 | 0.041911 | 0.010512 | -0.041894 | -0.010506 | 1.648e-05 | 6.2512e-06 | 0.062662 | 0.062662 | 0.062662 | 0.99528 | -0.032761 | 0.99488 | -0.035598 | 23.2082
26 | 0.034204 | 0.0085789 | -0.03419 | -0.0085735 | 1.4418e-05 | 5.4309e-06 | 0.051161 | 0.051161 | 0.051161 | 0.99488 | -0.035598 | 0.99445 | -0.03864 | 18.9484
27 | 0.029529 | 0.0074052 | -0.029501 | -0.0073949 | 2.7608e-05 | 1.0325e-05 | 0.044186 | 0.044186 | 0.044186 | 0.99445 | -0.03864 | 0.99349 | -0.045391 | 16.3652
28 | 0.025194 | 0.0063155 | -0.025193 | -0.006315 | 1.3758e-06 | 5.0911e-07 | 0.037736 | 0.037736 | 0.037736 | 0.99349 | -0.045391 | 0.99343 | -0.045786 | 13.9761
29 | 0.020991 | 0.0052619 | -0.020986 | -0.0052601 | 4.9674e-06 | 1.8063e-06 | 0.031442 | 0.031442 | 0.031442 | 0.99343 | -0.045786 | 0.99319 | -0.047495 | 11.6451
30 | 0.0084372 | 0.0021146 | -0.0084358 | -0.0021142 | 1.3642e-06 | 3.4807e-07 | 0.012648 | 0.012648 | 0.012648 | 0.99263 | -0.051461 | 0.99246 | -0.052629 | 4.6844

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18015 | 0.045185

## res_load
| p_mw | q_mvar
0 | 0.0062827 | 0.0015746
1 | 0.006118 | 0.0015333
2 | 0.010278 | 0.0025759
3 | 0.019877 | 0.0049817
4 | 0.0053272 | 0.0013351
5 | 0.0026639 | 0.00066762
6 | 0.0050536 | 0.0012665
7 | 0.0038684 | 0.00096951
8 | 0.0013832 | 0.00034667
9 | 0.0022932 | 0.00057473
10 | 0.016705 | 0.0041868
11 | 0.029622 | 0.007424
12 | 0.0031955 | 0.00080088
13 | 0.0030552 | 0.00076572
14 | 0.0076899 | 0.0019273
15 | 0.0046614 | 0.0011682
16 | 0.0043067 | 0.0010794
17 | 0.004766 | 0.0011945
18 | 0.0042018 | 0.0010531
19 | 0.0026933 | 0.000675
20 | 0.020213 | 0.0050658
21 | 0.0047937 | 0.0012014
22 | 0.0084358 | 0.0021142

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1