## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1403-14_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1403-14_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1403-14_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1403-14_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1403-14_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1403-14_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1403-14_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1403-14_0_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1403-14_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1403-14_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1403-14_0_3_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_1403-14_0_3_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_1403-14_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1403-14_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1403-14_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1403-14_0_3_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1403-14_0_3_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_1403-14_0_3_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_1403-14_0_3_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1403-14_0_3_node_33 | 0.4 | n |  | TRUE
20 | bus_LV_1403-14_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1403-14_0_3_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_1403-14_0_3_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_1403-14_0_3_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_1403-14_0_3_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_1403-14_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1403-14_0_3_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_1403-14_0_3_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_1403-14_0_3_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1403-14_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1403-14_0_3_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_1403-14_0_3_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_1403-14_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1403-14_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1403-14_0_3_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_1403-14_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1403-14_0_3_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1403-14_0_3_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_1403-14_0_3_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1403-14_0_3_node_32 | 0.4 | n |  | TRUE
40 | bus_MV_138_0_node_257 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1403-14_0_3_load_0 | 0 | 0.0068629 | 0.00172 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1403-14_0_3_load_16 | 7 | 0.0053869 | 0.0013501 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1403-14_0_3_load_12 | 8 | 0.00082775 | 0.00020745 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1403-14_0_3_load_11 | 9 | 0.0034683 | 0.00086924 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1403-14_0_3_load_17 | 11 | 0.0066878 | 0.0016761 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1403-14_0_3_load_24 | 15 | 0.008297 | 0.0020794 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1403-14_0_3_load_22 | 16 | 0.033162 | 0.0083113 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1403-14_0_3_load_21 | 17 | 0.025383 | 0.0063615 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1403-14_0_3_load_9 | 18 | 0.0098004 | 0.0024562 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1403-14_0_3_load_13 | 20 | 0.0045374 | 0.0011372 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1403-14_0_3_load_40 | 21 | 0.0048986 | 0.0012277 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1403-14_0_3_load_25 | 23 | 0.048902 | 0.012256 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1403-14_0_3_load_23 | 24 | 0.0027003 | 0.00067677 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1403-14_0_3_load_19 | 25 | 0.0075211 | 0.001885 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1403-14_0_3_load_36 | 27 | 0.0068826 | 0.0017249 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1403-14_0_3_load_15 | 28 | 0.0098028 | 0.0024568 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1403-14_0_3_load_20 | 29 | 0.0095464 | 0.0023926 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1403-14_0_3_load_38 | 30 | 0.0026729 | 0.0006699 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1403-14_0_3_load_39 | 31 | 0.0027664 | 0.00069333 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1403-14_0_3_load_26 | 32 | 0.001435 | 0.00035964 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1403-14_0_3_load_27 | 33 | 0.0020783 | 0.00052088 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1403-14_0_3_load_28 | 34 | 0.0020347 | 0.00050995 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1403-14_0_3_load_31 | 36 | 0.0014195 | 0.00035576 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1403-14_0_3_load_34 | 37 | 0.0069133 | 0.0017326 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1403-14_0_3_load_30 | 38 | 0.0013065 | 0.00032743 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1403-14_0_3_load_32 | 39 | 0.0037477 | 0.00093926 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1403-14_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0082668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1403-14_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.028311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1403-14_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.00558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1403-14_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.04383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1403-14_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.017854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1403-14_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.034023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1403-14_0_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.0064326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1403-14_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.019478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1403-14_0_3_line_8 | NAYY 4x150 SE | 4 | 9 | 0.021362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1403-14_0_3_line_9 | NAYY 4x150 SE | 5 | 19 | 0.012856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1403-14_0_3_line_10 | NAYY 4x150 SE | 5 | 18 | 0.013424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1403-14_0_3_line_11 | NAYY 4x150 SE | 6 | 10 | 0.025119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1403-14_0_3_line_12 | NAYY 4x150 SE | 6 | 11 | 0.020344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1403-14_0_3_line_13 | NAYY 4x150 SE | 8 | 20 | 0.055547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1403-14_0_3_line_14 | NAYY 4x150 SE | 10 | 21 | 0.022855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1403-14_0_3_line_15 | NAYY 4x150 SE | 10 | 22 | 0.004572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1403-14_0_3_line_16 | NAYY 4x150 SE | 11 | 12 | 0.01569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1403-14_0_3_line_17 | NAYY 4x150 SE | 12 | 13 | 0.010232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1403-14_0_3_line_18 | NAYY 4x150 SE | 12 | 14 | 0.08854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1403-14_0_3_line_19 | NAYY 4x150 SE | 13 | 17 | 0.026752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1403-14_0_3_line_20 | NAYY 4x150 SE | 14 | 15 | 0.043031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1403-14_0_3_line_21 | NAYY 4x150 SE | 14 | 16 | 0.038948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1403-14_0_3_line_22 | NAYY 4x150 SE | 15 | 23 | 0.030843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1403-14_0_3_line_23 | NAYY 4x150 SE | 16 | 24 | 0.015766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1403-14_0_3_line_24 | NAYY 4x150 SE | 17 | 25 | 0.0084018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1403-14_0_3_line_25 | NAYY 4x150 SE | 19 | 26 | 0.014061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1403-14_0_3_line_26 | NAYY 4x150 SE | 19 | 27 | 0.013434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1403-14_0_3_line_27 | NAYY 4x150 SE | 22 | 30 | 0.027151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1403-14_0_3_line_28 | NAYY 4x150 SE | 22 | 31 | 0.032456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1403-14_0_3_line_29 | NAYY 4x150 SE | 25 | 29 | 0.029605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1403-14_0_3_line_30 | NAYY 4x150 SE | 26 | 37 | 0.013231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1403-14_0_3_line_31 | NAYY 4x150 SE | 28 | 29 | 0.017059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1403-14_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.0018748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1403-14_0_3_line_33 | NAYY 4x150 SE | 32 | 34 | 0.045813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1403-14_0_3_line_34 | NAYY 4x150 SE | 33 | 35 | 0.015201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1403-14_0_3_line_35 | NAYY 4x150 SE | 34 | 36 | 0.15738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1403-14_0_3_line_36 | NAYY 4x150 SE | 35 | 37 | 0.15414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1403-14_0_3_line_37 | NAYY 4x150 SE | 36 | 38 | 2.7236e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1403-14_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.027356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1403-14_0_3_trafo_8 | 0.25 MVA 20/0.4 kV | 40 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2657020.9992 | 1187546.0017 | 2657026.8147 | 1187543.3778 | 2657027.656 | 1187545.0665
1 | 2657045.6012 | 1187555.8303 | 2657035.2515 | 1187560.3121 | 2657027.656 | 1187545.0665
2 | 2657020.9992 | 1187546.0017 | 2657015.9786 | 1187548.4664
3 | 2657002.1885 | 1187506.4226 | 2657009.2333 | 1187522.9323 | 2657020.9992 | 1187546.0017
4 | 2657054.6106 | 1187568.7011 | 2657047.7242 | 1187554.8055 | 2657045.6012 | 1187555.8303
5 | 2657015.9786 | 1187548.4664 | 2657031.0531 | 1187578.9826
6 | 2657015.9786 | 1187548.4664 | 2657013.167 | 1187542.6809
7 | 2657002.1885 | 1187506.4226 | 2656984.6367 | 1187514.8686
8 | 2657002.1885 | 1187506.4226 | 2656997.8671 | 1187494.7416 | 2656994.9118 | 1187486.3394
9 | 2657066.1472 | 1187562.9633 | 2657054.6106 | 1187568.7011
10 | 2657054.6106 | 1187568.7011 | 2657059.4906 | 1187578.5976 | 2657057.2474 | 1187579.4211
11 | 2657008.5691 | 1187590.3084 | 2657031.0531 | 1187578.9826
12 | 2657031.0531 | 1187578.9826 | 2657038.957 | 1187594.9891 | 2657040.0717 | 1187597.2189
13 | 2656984.6367 | 1187514.8686 | 2656979.0346 | 1187517.5642 | 2656964.7755 | 1187523.1985 | 2656951.3001 | 1187527.4395 | 2656940.352 | 1187530.6706 | 2656932.4778 | 1187533.175 | 2656932.3003 | 1187533.2522
14 | 2657008.5691 | 1187590.3084 | 2656998.9171 | 1187569.5827
15 | 2657004.5355 | 1187592.4823 | 2657008.5691 | 1187590.3084
16 | 2657047.0873 | 1187611.2535 | 2657040.0717 | 1187597.2189
17 | 2657047.0873 | 1187611.2535 | 2657037.8742 | 1187615.7572
18 | 2657047.0873 | 1187611.2535 | 2657050.3513 | 1187617.7882 | 2657062.2092 | 1187641.5701 | 2657066.1991 | 1187649.5793 | 2657072.465 | 1187662.1349 | 2657081.2758 | 1187679.8177 | 2657069.4091 | 1187680.9942
19 | 2657037.8742 | 1187615.7572 | 2657013.8406 | 1187627.5058
20 | 2657069.4091 | 1187680.9942 | 2657067.7279 | 1187686.0922 | 2657034.4094 | 1187703.6527
21 | 2657069.4091 | 1187680.9942 | 2657030.5168 | 1187683.0797
22 | 2657007.1243 | 1187718.0333 | 2657034.4094 | 1187703.6527
23 | 2657030.5168 | 1187683.0797 | 2657014.7732 | 1187683.9239
24 | 2657013.8406 | 1187627.5058 | 2657006.2925 | 1187631.1956
25 | 2657078.7945 | 1187556.7469 | 2657066.1472 | 1187562.9633
26 | 2657066.1472 | 1187562.9633 | 2657060.1594 | 1187550.9376
27 | 2657004.5355 | 1187592.4823 | 2656999.272 | 1187597.2238 | 2656992.2731 | 1187601.5486 | 2656986.417 | 1187603.6385 | 2656980.8814 | 1187604.9088
28 | 2657004.5355 | 1187592.4823 | 2656997.8679 | 1187594.0531 | 2656995.4106 | 1187594.1298 | 2656992.654 | 1187593.5922 | 2656990.8223 | 1187592.8632 | 2656989.6116 | 1187591.0173 | 2656982.4795 | 1187576.4635
29 | 2657006.2925 | 1187631.1956 | 2656979.6953 | 1187644.1974
30 | 2657078.7945 | 1187556.7469 | 2657072.8547 | 1187544.924
31 | 2656964.3695 | 1187651.6893 | 2656979.6953 | 1187644.1974
32 | 2657186.5819 | 1187431.3907 | 2657184.8159 | 1187430.7613
33 | 2657186.5819 | 1187431.3907 | 2657191.7489 | 1187433.2321 | 2657228.1568 | 1187450.5761
34 | 2657170.4973 | 1187425.6584 | 2657184.8159 | 1187430.7613
35 | 2657228.1568 | 1187450.5761 | 2657359.9884 | 1187364.6168
36 | 2657072.8547 | 1187544.924 | 2657170.4973 | 1187425.6584
37 | 2657360.0147 | 1187364.624 | 2657360.0147 | 1187364.624 | 2657359.9884 | 1187364.6168
38 | 2657360.0147 | 1187364.624 | 2657368.1411 | 1187350.1715 | 2657374.0665 | 1187341.1721

## bus_geodata
| x | y | coords
0 | 2657027.656 | 1187545.0665
1 | 2657020.9992 | 1187546.0017
2 | 2657045.6012 | 1187555.8303
3 | 2657015.9786 | 1187548.4664
4 | 2657002.1885 | 1187506.4226
5 | 2657054.6106 | 1187568.7011
6 | 2657031.0531 | 1187578.9826
7 | 2657013.167 | 1187542.6809
8 | 2656984.6367 | 1187514.8686
9 | 2656994.9118 | 1187486.3394
10 | 2657008.5691 | 1187590.3084
11 | 2657040.0717 | 1187597.2189
12 | 2657047.0873 | 1187611.2535
13 | 2657037.8742 | 1187615.7572
14 | 2657069.4091 | 1187680.9942
15 | 2657034.4094 | 1187703.6527
16 | 2657030.5168 | 1187683.0797
17 | 2657013.8406 | 1187627.5058
18 | 2657057.2474 | 1187579.4211
19 | 2657066.1472 | 1187562.9633
20 | 2656932.3003 | 1187533.2522
21 | 2656998.9171 | 1187569.5827
22 | 2657004.5355 | 1187592.4823
23 | 2657007.1243 | 1187718.0333
24 | 2657014.7732 | 1187683.9239
25 | 2657006.2925 | 1187631.1956
26 | 2657078.7945 | 1187556.7469
27 | 2657060.1594 | 1187550.9376
28 | 2656964.3695 | 1187651.6893
29 | 2656979.6953 | 1187644.1974
30 | 2656980.8814 | 1187604.9088
31 | 2656982.4795 | 1187576.4635
32 | 2657186.5819 | 1187431.3907
33 | 2657184.8159 | 1187430.7613
34 | 2657228.1568 | 1187450.5761
35 | 2657170.4973 | 1187425.6584
36 | 2657359.9884 | 1187364.6168
37 | 2657072.8547 | 1187544.924
38 | 2657360.0147 | 1187364.624
39 | 2657374.0665 | 1187341.1721
40 | 2657047.0873 | 1187611.2535

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99143 | -0.059866 | 0.0068629 | 0.00172
1 | 0.99194 | -0.056298 | 0 | 0
2 | 0.98998 | -0.070134 | 0 | 0
3 | 0.99235 | -0.053392 | 0 | 0
4 | 0.99138 | -0.060233 | 0 | 0
5 | 0.98906 | -0.076624 | 0 | 0
6 | 0.99514 | -0.033872 | 0 | 0
7 | 0.9923 | -0.053743 | 0.0053869 | 0.0013501
8 | 0.99123 | -0.061295 | 0.00082775 | 0.00020745
9 | 0.99128 | -0.060985 | 0.0034683 | 0.00086924
10 | 0.99476 | -0.036493 | 0 | 0
11 | 0.9971 | -0.020138 | 0.0066878 | 0.0016761
12 | 0.99877 | -0.008532 | 0 | 0
13 | 1 | 0 | -0.22227 | -0.055816
14 | 0.98681 | -0.091984 | 0 | 0
15 | 0.98324 | -0.1173 | 0.008297 | 0.0020794
16 | 0.98479 | -0.10633 | 0.033162 | 0.0083113
17 | 0.998 | -0.013981 | 0.025383 | 0.0063615
18 | 0.98887 | -0.077967 | 0.0098004 | 0.0024562
19 | 0.98858 | -0.080018 | 0 | 0
20 | 0.99087 | -0.063858 | 0.0045374 | 0.0011372
21 | 0.9946 | -0.037622 | 0.0048986 | 0.0012277
22 | 0.99473 | -0.036744 | 0 | 0
23 | 0.98105 | -0.13291 | 0.048902 | 0.012256
24 | 0.98473 | -0.10677 | 0.0027003 | 0.00067677
25 | 0.99768 | -0.016244 | 0.0075211 | 0.001885
26 | 0.98819 | -0.082743 | 0 | 0
27 | 0.98845 | -0.080962 | 0.0068826 | 0.0017249
28 | 0.99662 | -0.023673 | 0.0098028 | 0.0024568
29 | 0.99686 | -0.021993 | 0.0095464 | 0.0023926
30 | 0.99462 | -0.037476 | 0.0026729 | 0.0006699
31 | 0.9946 | -0.03765 | 0.0027664 | 0.00069333
32 | 0.98486 | -0.10644 | 0.001435 | 0.00035964
33 | 0.98488 | -0.10625 | 0.0020783 | 0.00052088
34 | 0.98429 | -0.11046 | 0.0020347 | 0.00050995
35 | 0.98515 | -0.10436 | 0 | 0
36 | 0.98281 | -0.12099 | 0.0014195 | 0.00035576
37 | 0.98783 | -0.08531 | 0.0069133 | 0.0017326
38 | 0.98281 | -0.12099 | 0.0013065 | 0.00032743
39 | 0.98266 | -0.12205 | 0.0037477 | 0.00093926
40 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.042643 | -0.010702 | 0.042664 | 0.01071 | 2.1134e-05 | 8.0216e-06 | 0.064007 | 0.064007 | 0.064007 | 0.99143 | -0.059866 | 0.99194 | -0.056298 | 23.7061
1 | 0.03578 | 0.0089824 | -0.035729 | -0.0089632 | 5.0956e-05 | 1.9234e-05 | 0.053706 | 0.053706 | 0.053706 | 0.99143 | -0.059866 | 0.98998 | -0.070134 | 19.8913
2 | -0.051505 | -0.012925 | 0.051526 | 0.012933 | 2.0789e-05 | 7.9236e-06 | 0.077269 | 0.077269 | 0.077269 | 0.99194 | -0.056298 | 0.99235 | -0.053392 | 28.6181
3 | 0.0088411 | 0.002215 | -0.0088363 | -0.0022137 | 4.8106e-06 | 1.2847e-06 | 0.013262 | 0.013262 | 0.013262 | 0.99194 | -0.056298 | 0.99138 | -0.060233 | 4.912
4 | 0.035729 | 0.0089632 | -0.035697 | -0.008951 | 3.2135e-05 | 1.213e-05 | 0.053706 | 0.053706 | 0.053706 | 0.98998 | -0.070134 | 0.98906 | -0.076624 | 19.8913
5 | -0.056913 | -0.014283 | 0.057067 | 0.014342 | 0.00015464 | 5.9037e-05 | 0.085347 | 0.085346 | 0.085347 | 0.99235 | -0.053392 | 0.99514 | -0.033872 | 31.6099
6 | 0.0053871 | 0.0013501 | -0.0053869 | -0.0013501 | 2.6192e-07 | 1.7637e-08 | 0.0080779 | 0.0080779 | 0.0080779 | 0.99235 | -0.053392 | 0.9923 | -0.053743 | 2.9918
7 | 0.0053676 | 0.0013446 | -0.0053668 | -0.0013445 | 7.8886e-07 | 5.2289e-08 | 0.0080562 | 0.0080563 | 0.0080563 | 0.99138 | -0.060233 | 0.99123 | -0.061295 | 2.9838
8 | 0.0034687 | 0.00086911 | -0.0034683 | -0.00086924 | 3.613e-07 | -1.3645e-07 | 0.0052062 | 0.0052063 | 0.0052063 | 0.99138 | -0.060233 | 0.99128 | -0.060985 | 1.9283
9 | 0.025895 | 0.0064943 | -0.025882 | -0.0064898 | 1.2176e-05 | 4.5183e-06 | 0.038959 | 0.038959 | 0.038959 | 0.98906 | -0.076624 | 0.98858 | -0.080018 | 14.4294
10 | 0.0098022 | 0.0024567 | -0.0098004 | -0.0024562 | 1.8217e-06 | 5.2841e-07 | 0.014747 | 0.014747 | 0.014747 | 0.98906 | -0.076624 | 0.98887 | -0.077967 | 5.4619
11 | 0.010343 | 0.0025915 | -0.010339 | -0.0025904 | 3.7492e-06 | 1.1158e-06 | 0.015466 | 0.015466 | 0.015466 | 0.99514 | -0.033872 | 0.99476 | -0.036493 | 5.7281
12 | -0.067411 | -0.016934 | 0.06754 | 0.016983 | 0.00012902 | 4.9358e-05 | 0.10081 | 0.10081 | 0.10081 | 0.99514 | -0.033872 | 0.9971 | -0.020138 | 37.3379
13 | 0.004539 | 0.0011371 | -0.0045374 | -0.0011372 | 1.6093e-06 | -9.6809e-08 | 0.0068137 | 0.006814 | 0.006814 | 0.99123 | -0.061295 | 0.99087 | -0.063858 | 2.5237
14 | 0.0048993 | 0.0012277 | -0.0048986 | -0.0012277 | 7.6597e-07 | -2.0586e-09 | 0.0073286 | 0.0073287 | 0.0073287 | 0.99476 | -0.036493 | 0.9946 | -0.037622 | 2.7143
15 | 0.0054402 | 0.0013627 | -0.00544 | -0.0013627 | 1.8891e-07 | 1.3306e-08 | 0.0081374 | 0.0081374 | 0.0081374 | 0.99476 | -0.036493 | 0.99473 | -0.036744 | 3.0139
16 | -0.074228 | -0.018659 | 0.074348 | 0.018705 | 0.00012018 | 4.6019e-05 | 0.11079 | 0.11079 | 0.11079 | 0.9971 | -0.020138 | 0.99877 | -0.008532 | 41.0344
17 | -0.16889 | -0.042594 | 0.16909 | 0.042672 | 0.00020226 | 7.7526e-05 | 0.25171 | 0.25171 | 0.25171 | 0.99877 | -0.008532 | 1 | 0 | 46.6131
18 | 0.094539 | 0.023889 | -0.093442 | -0.023468 | 0.0010971 | 0.00042083 | 0.14092 | 0.14092 | 0.14092 | 0.99877 | -0.008532 | 0.98681 | -0.091984 | 52.1919
19 | 0.052381 | 0.013144 | -0.052279 | -0.013105 | 0.00010143 | 3.866e-05 | 0.077949 | 0.077949 | 0.077949 | 1 | 0 | 0.998 | -0.013981 | 28.8699
20 | 0.057507 | 0.014453 | -0.057305 | -0.014376 | 0.00020198 | 7.7136e-05 | 0.08673 | 0.08673 | 0.08673 | 0.98681 | -0.091984 | 0.98324 | -0.1173 | 32.1222
21 | 0.035934 | 0.0090149 | -0.035863 | -0.0089879 | 7.1366e-05 | 2.6952e-05 | 0.054189 | 0.054189 | 0.054189 | 0.98681 | -0.091984 | 0.98479 | -0.10633 | 20.0699
22 | 0.049008 | 0.012296 | -0.048902 | -0.012256 | 0.00010589 | 4.0335e-05 | 0.074173 | 0.074173 | 0.074173 | 0.98324 | -0.1173 | 0.98105 | -0.13291 | 27.4717
23 | 0.0027005 | 0.00067663 | -0.0027003 | -0.00067677 | 1.638e-07 | -1.3758e-07 | 0.0040804 | 0.0040804 | 0.0040804 | 0.98479 | -0.10633 | 0.98473 | -0.10677 | 1.5113
24 | 0.026896 | 0.0067436 | -0.026888 | -0.0067405 | 8.4317e-06 | 3.1332e-06 | 0.040103 | 0.040103 | 0.040103 | 0.998 | -0.013981 | 0.99768 | -0.016244 | 14.8531
25 | 0.018999 | 0.0047647 | -0.018992 | -0.0047621 | 7.176e-06 | 2.5798e-06 | 0.028598 | 0.028598 | 0.028598 | 0.98858 | -0.080018 | 0.98819 | -0.082743 | 10.592
26 | 0.0068835 | 0.0017251 | -0.0068826 | -0.0017249 | 8.9991e-07 | 1.739e-07 | 0.010361 | 0.010361 | 0.010361 | 0.98858 | -0.080018 | 0.98845 | -0.080962 | 3.8375
27 | 0.0026732 | 0.00066965 | -0.0026729 | -0.0006699 | 2.7091e-07 | -2.4822e-07 | 0.0039987 | 0.0039989 | 0.0039989 | 0.99473 | -0.036744 | 0.99462 | -0.037476 | 1.4811
28 | 0.0027668 | 0.00069304 | -0.0027664 | -0.00069333 | 3.4691e-07 | -2.8784e-07 | 0.0041387 | 0.0041388 | 0.0041388 | 0.99473 | -0.036744 | 0.9946 | -0.03765 | 1.5329
29 | 0.019367 | 0.0048556 | -0.019351 | -0.00485 | 1.5414e-05 | 5.5423e-06 | 0.028886 | 0.028886 | 0.028886 | 0.99768 | -0.016244 | 0.99686 | -0.021993 | 10.6985
30 | 0.018992 | 0.0047621 | -0.018985 | -0.0047597 | 6.7525e-06 | 2.4277e-06 | 0.028598 | 0.028598 | 0.028598 | 0.98819 | -0.082743 | 0.98783 | -0.08531 | 10.592
31 | -0.0098028 | -0.0024568 | 0.0098051 | 0.0024575 | 2.2803e-06 | 6.5468e-07 | 0.014636 | 0.014636 | 0.014636 | 0.99662 | -0.023673 | 0.99686 | -0.021993 | 5.4208
32 | -0.0099581 | -0.0024948 | 0.0099584 | 0.0024949 | 2.6481e-07 | 7.7994e-08 | 0.015045 | 0.015045 | 0.015045 | 0.98486 | -0.10644 | 0.98488 | -0.10625 | 5.5723
33 | 0.0085231 | 0.0021351 | -0.0085184 | -0.0021339 | 4.7405e-06 | 1.2406e-06 | 0.012877 | 0.012877 | 0.012877 | 0.98486 | -0.10644 | 0.98429 | -0.11046 | 4.7694
34 | -0.012037 | -0.0030157 | 0.01204 | 0.0030167 | 3.1368e-06 | 1.013e-06 | 0.018185 | 0.018185 | 0.018185 | 0.98488 | -0.10625 | 0.98515 | -0.10436 | 6.7353
35 | 0.0064836 | 0.0016239 | -0.0064742 | -0.0016223 | 9.435e-06 | 1.6315e-06 | 0.0098014 | 0.0098021 | 0.0098021 | 0.98429 | -0.11046 | 0.98281 | -0.12099 | 3.6304
36 | -0.01204 | -0.0030167 | 0.012072 | 0.003027 | 3.1806e-05 | 1.0265e-05 | 0.018185 | 0.018185 | 0.018185 | 0.98515 | -0.10436 | 0.98783 | -0.08531 | 6.7353
37 | 0.0050547 | 0.0012666 | -0.0050547 | -0.0012666 | 9.9464e-10 | 3.9589e-11 | 0.0076529 | 0.0076529 | 0.0076529 | 0.98281 | -0.12099 | 0.98281 | -0.12099 | 2.8344
38 | 0.0037482 | 0.00093912 | -0.0037477 | -0.00093926 | 5.4973e-07 | -1.3517e-07 | 0.0056749 | 0.005675 | 0.005675 | 0.98281 | -0.12099 | 0.98266 | -0.12205 | 2.1019

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22227 | 0.055816

## res_load
| p_mw | q_mvar
0 | 0.0068629 | 0.00172
1 | 0.0053869 | 0.0013501
2 | 0.00082775 | 0.00020745
3 | 0.0034683 | 0.00086924
4 | 0.0066878 | 0.0016761
5 | 0.008297 | 0.0020794
6 | 0.033162 | 0.0083113
7 | 0.025383 | 0.0063615
8 | 0.0098004 | 0.0024562
9 | 0.0045374 | 0.0011372
10 | 0.0048986 | 0.0012277
11 | 0.048902 | 0.012256
12 | 0.0027003 | 0.00067677
13 | 0.0075211 | 0.001885
14 | 0.0068826 | 0.0017249
15 | 0.0098028 | 0.0024568
16 | 0.0095464 | 0.0023926
17 | 0.0026729 | 0.0006699
18 | 0.0027664 | 0.00069333
19 | 0.001435 | 0.00035964
20 | 0.0020783 | 0.00052088
21 | 0.0020347 | 0.00050995
22 | 0.0014195 | 0.00035576
23 | 0.0069133 | 0.0017326
24 | 0.0013065 | 0.00032743
25 | 0.0037477 | 0.00093926

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1