## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1403-21_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1403-21_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1403-21_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1403-21_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1403-21_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1403-21_0_4_node_47 | 0.4 | n |  | TRUE
6 | bus_LV_1403-21_0_4_node_122 | 0.4 | n |  | TRUE
7 | bus_LV_1403-21_0_4_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1403-21_0_4_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_1403-21_0_4_node_123 | 0.4 | n |  | TRUE
10 | bus_LV_1403-21_0_4_node_28 | 0.4 | n |  | TRUE
11 | bus_LV_1403-21_0_4_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_1403-21_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1403-21_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1403-21_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1403-21_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1403-21_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1403-21_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1403-21_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1403-21_0_4_node_124 | 0.4 | n |  | TRUE
20 | bus_LV_1403-21_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1403-21_0_4_node_100 | 0.4 | n |  | TRUE
22 | bus_LV_1403-21_0_4_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_1403-21_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1403-21_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1403-21_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1403-21_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1403-21_0_4_node_101 | 0.4 | n |  | TRUE
28 | bus_LV_1403-21_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1403-21_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1403-21_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1403-21_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1403-21_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1403-21_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1403-21_0_4_node_125 | 0.4 | n |  | TRUE
35 | bus_LV_1403-21_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1403-21_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1403-21_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_1403-21_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1403-21_0_4_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_1403-21_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1403-21_0_4_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_1403-21_0_4_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_1403-21_0_4_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_1403-21_0_4_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_1403-21_0_4_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1403-21_0_4_node_126 | 0.4 | n |  | TRUE
47 | bus_LV_1403-21_0_4_node_127 | 0.4 | n |  | TRUE
48 | bus_LV_1403-21_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_1403-21_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_1403-21_0_4_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_1403-21_0_4_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_1403-21_0_4_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_1403-21_0_4_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_1403-21_0_4_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_1403-21_0_4_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_1403-21_0_4_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_1403-21_0_4_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_1403-21_0_4_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_1403-21_0_4_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_1403-21_0_4_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_1403-21_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_1403-21_0_4_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_1403-21_0_4_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_1403-21_0_4_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_1403-21_0_4_node_90 | 0.4 | n |  | TRUE
66 | bus_LV_1403-21_0_4_node_91 | 0.4 | n |  | TRUE
67 | bus_LV_1403-21_0_4_node_92 | 0.4 | n |  | TRUE
68 | bus_LV_1403-21_0_4_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_1403-21_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_1403-21_0_4_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_1403-21_0_4_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_1403-21_0_4_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_1403-21_0_4_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_1403-21_0_4_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_1403-21_0_4_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_1403-21_0_4_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_1403-21_0_4_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_1403-21_0_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_1403-21_0_4_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_1403-21_0_4_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_1403-21_0_4_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_1403-21_0_4_node_84 | 0.4 | n |  | TRUE
83 | bus_LV_1403-21_0_4_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_1403-21_0_4_node_83 | 0.4 | n |  | TRUE
85 | bus_LV_1403-21_0_4_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_1403-21_0_4_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_1403-21_0_4_node_76 | 0.4 | n |  | TRUE
88 | bus_LV_1403-21_0_4_node_77 | 0.4 | n |  | TRUE
89 | bus_LV_1403-21_0_4_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_1403-21_0_4_node_79 | 0.4 | n |  | TRUE
91 | bus_LV_1403-21_0_4_node_80 | 0.4 | n |  | TRUE
92 | bus_LV_1403-21_0_4_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_1403-21_0_4_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_1403-21_0_4_node_89 | 0.4 | n |  | TRUE
95 | bus_LV_1403-21_0_4_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_1403-21_0_4_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_1403-21_0_4_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_1403-21_0_4_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_1403-21_0_4_node_96 | 0.4 | n |  | TRUE
100 | bus_LV_1403-21_0_4_node_95 | 0.4 | n |  | TRUE
101 | bus_LV_1403-21_0_4_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_1403-21_0_4_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_1403-21_0_4_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_1403-21_0_4_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_1403-21_0_4_node_82 | 0.4 | n |  | TRUE
106 | bus_LV_1403-21_0_4_node_120 | 0.4 | n |  | TRUE
107 | bus_LV_1403-21_0_4_node_121 | 0.4 | n |  | TRUE
108 | bus_LV_1403-21_0_4_node_102 | 0.4 | n |  | TRUE
109 | bus_LV_1403-21_0_4_node_103 | 0.4 | n |  | TRUE
110 | bus_LV_1403-21_0_4_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_1403-21_0_4_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_1403-21_0_4_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_1403-21_0_4_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_1403-21_0_4_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_1403-21_0_4_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_1403-21_0_4_node_114 | 0.4 | n |  | TRUE
117 | bus_LV_1403-21_0_4_node_113 | 0.4 | n |  | TRUE
118 | bus_LV_1403-21_0_4_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_1403-21_0_4_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_1403-21_0_4_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_1403-21_0_4_node_116 | 0.4 | n |  | TRUE
122 | bus_LV_1403-21_0_4_node_117 | 0.4 | n |  | TRUE
123 | bus_LV_1403-21_0_4_node_118 | 0.4 | n |  | TRUE
124 | bus_LV_1403-21_0_4_node_119 | 0.4 | n |  | TRUE
125 | bus_MV_138_0_node_254 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1403-21_0_4_load_0 | 0 | 0.0078923 | 0.001978 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1403-21_0_4_load_1 | 1 | 0.00052147 | 0.00013069 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1403-21_0_4_load_4 | 4 | 0.0032511 | 0.00081481 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1403-21_0_4_load_122 | 6 | 0.028327 | 0.0070995 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1403-21_0_4_load_33 | 8 | 0.0037634 | 0.00094319 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1403-21_0_4_load_123 | 9 | 0.00078212 | 0.00019602 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1403-21_0_4_load_28 | 10 | 0.0049784 | 0.0012477 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1403-21_0_4_load_25 | 11 | 0.0006843 | 0.0001715 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1403-21_0_4_load_5 | 12 | 0.0031328 | 0.00078515 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1403-21_0_4_load_12 | 16 | 0.01108 | 0.002777 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1403-21_0_4_load_13 | 17 | 0.001484 | 0.00037194 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1403-21_0_4_load_9 | 18 | 0.01051 | 0.002634 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1403-21_0_4_load_124 | 19 | 0.0044408 | 0.001113 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1403-21_0_4_load_14 | 20 | 0.0014398 | 0.00036085 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1403-21_0_4_load_100 | 21 | 0.0026468 | 0.00066335 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1403-21_0_4_load_10 | 22 | 0.00052676 | 0.00013202 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1403-21_0_4_load_11 | 23 | 0.0033076 | 0.00082897 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1403-21_0_4_load_19 | 24 | 0.0010647 | 0.00026685 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1403-21_0_4_load_20 | 25 | 0.0018278 | 0.0004581 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1403-21_0_4_load_15 | 26 | 0.0038146 | 0.00095603 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1403-21_0_4_load_101 | 27 | 0.0034687 | 0.00086933 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1403-21_0_4_load_16 | 28 | 0.0012536 | 0.00031418 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1403-21_0_4_load_17 | 29 | 0.0016468 | 0.00041272 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1403-21_0_4_load_18 | 30 | 0.0011421 | 0.00028623 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1403-21_0_4_load_26 | 31 | 0.0014067 | 0.00035254 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1403-21_0_4_load_24 | 32 | 0.0013403 | 0.0003359 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1403-21_0_4_load_21 | 33 | 0.0012063 | 0.00030233 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1403-21_0_4_load_125 | 34 | 0.0027161 | 0.00068072 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1403-21_0_4_load_22 | 35 | 0.0019644 | 0.00049233 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1403-21_0_4_load_23 | 36 | 0.00074037 | 0.00018556 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1403-21_0_4_load_29 | 37 | 0.0018931 | 0.00047445 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1403-21_0_4_load_30 | 38 | 0.0029072 | 0.0007286 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1403-21_0_4_load_31 | 39 | 0.0032973 | 0.00082638 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1403-21_0_4_load_34 | 41 | 0.00087792 | 0.00022003 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1403-21_0_4_load_35 | 42 | 0.0015854 | 0.00039733 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1403-21_0_4_load_36 | 43 | 0.00092351 | 0.00023145 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1403-21_0_4_load_46 | 44 | 0.0041925 | 0.0010507 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1403-21_0_4_load_37 | 45 | 0.00073918 | 0.00018526 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1403-21_0_4_load_126 | 46 | 0.00092312 | 0.00023136 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1403-21_0_4_load_127 | 47 | 0.00092383 | 0.00023153 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1403-21_0_4_load_38 | 48 | 0.00063028 | 0.00015796 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1403-21_0_4_load_39 | 49 | 0.0023526 | 0.00058962 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1403-21_0_4_load_41 | 51 | 0.0036571 | 0.00091655 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1403-21_0_4_load_42 | 52 | 0.0017973 | 0.00045045 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1403-21_0_4_load_43 | 53 | 0.00091646 | 0.00022969 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1403-21_0_4_load_51 | 54 | 0.0046946 | 0.0011766 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1403-21_0_4_load_45 | 57 | 0.002189 | 0.00054861 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1403-21_0_4_load_55 | 58 | 0.0011067 | 0.00027737 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1403-21_0_4_load_56 | 59 | 0.0035481 | 0.00088925 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1403-21_0_4_load_48 | 60 | 0.0013755 | 0.00034474 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1403-21_0_4_load_49 | 61 | 0.0041116 | 0.0010305 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1403-21_0_4_load_50 | 62 | 0.003738 | 0.00093684 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1403-21_0_4_load_54 | 63 | 0.0032322 | 0.00081007 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1403-21_0_4_load_53 | 64 | 0.0010136 | 0.00025403 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1403-21_0_4_load_90 | 65 | 0.00124 | 0.00031078 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1403-21_0_4_load_92 | 67 | 0.00024702 | 6.1908e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1403-21_0_4_load_57 | 68 | 0.0004561 | 0.00011431 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1403-21_0_4_load_58 | 69 | 0.00045829 | 0.00011486 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1403-21_0_4_load_59 | 70 | 0.0007253 | 0.00018178 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1403-21_0_4_load_60 | 71 | 0.00050824 | 0.00012738 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1403-21_0_4_load_61 | 72 | 0.00093704 | 0.00023485 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1403-21_0_4_load_62 | 73 | 0.00029706 | 7.4449e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1403-21_0_4_load_63 | 74 | 0.0021148 | 0.00053003 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1403-21_0_4_load_64 | 75 | 0.00082263 | 0.00020617 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1403-21_0_4_load_66 | 76 | 0.00093791 | 0.00023506 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1403-21_0_4_load_65 | 77 | 0.00082259 | 0.00020616 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1403-21_0_4_load_69 | 78 | 0.00030325 | 7.6002e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1403-21_0_4_load_71 | 80 | 0.00067891 | 0.00017015 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1403-21_0_4_load_72 | 81 | 0.0029697 | 0.00074427 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1403-21_0_4_load_83 | 84 | 0.00018975 | 4.7557e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1403-21_0_4_load_73 | 85 | 0.0031476 | 0.00078886 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1403-21_0_4_load_74 | 86 | 0.000228 | 5.7141e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1403-21_0_4_load_76 | 87 | 0.00032492 | 8.1433e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1403-21_0_4_load_77 | 88 | 0.00017804 | 4.4622e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1403-21_0_4_load_79 | 90 | 0.00010025 | 2.5125e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1403-21_0_4_load_85 | 92 | 0.00030899 | 7.7441e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1403-21_0_4_load_81 | 93 | 0.0007826 | 0.00019614 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1403-21_0_4_load_86 | 95 | 0.00047947 | 0.00012017 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1403-21_0_4_load_87 | 96 | 0.00077725 | 0.0001948 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1403-21_0_4_load_88 | 97 | 0.00063725 | 0.00015971 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1403-21_0_4_load_93 | 98 | 8.9837e-05 | 2.2515e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1403-21_0_4_load_95 | 100 | 0.0003079 | 7.7168e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1403-21_0_4_load_94 | 101 | 0.0025312 | 0.00063438 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1403-21_0_4_load_97 | 102 | 0.00013568 | 3.4005e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1403-21_0_4_load_98 | 103 | 0.00017371 | 4.3537e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1403-21_0_4_load_99 | 104 | 0.00029835 | 7.4773e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1403-21_0_4_load_82 | 105 | 0.00063605 | 0.00015941 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1403-21_0_4_load_120 | 106 | 0.0017248 | 0.00043228 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1403-21_0_4_load_121 | 107 | 0.0029543 | 0.00074042 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1403-21_0_4_load_102 | 108 | 0.00072755 | 0.00018234 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1403-21_0_4_load_103 | 109 | 0.00049322 | 0.00012361 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1403-21_0_4_load_104 | 110 | 0.00049337 | 0.00012365 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1403-21_0_4_load_105 | 111 | 0.00049337 | 0.00012365 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1403-21_0_4_load_107 | 112 | 0.00083253 | 0.00020865 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1403-21_0_4_load_106 | 113 | 0.0013425 | 0.00033647 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1403-21_0_4_load_110 | 115 | 0.0014177 | 0.00035531 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1403-21_0_4_load_114 | 116 | 0.0028872 | 0.0007236 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1403-21_0_4_load_113 | 117 | 0.0018212 | 0.00045645 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1403-21_0_4_load_111 | 118 | 0.0027612 | 0.00069203 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1403-21_0_4_load_112 | 119 | 0.0043737 | 0.0010962 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1403-21_0_4_load_115 | 120 | 0.00073837 | 0.00018505 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1403-21_0_4_load_116 | 121 | 0.0020406 | 0.00051142 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1403-21_0_4_load_117 | 122 | 0.0010425 | 0.00026127 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1403-21_0_4_load_118 | 123 | 0.00058159 | 0.00014576 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1403-21_0_4_load_119 | 124 | 0.0015175 | 0.00038031 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1403-21_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.023635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1403-21_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.045812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1403-21_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.021586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1403-21_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.02722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1403-21_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.005787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1403-21_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.058072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1403-21_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0077814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1403-21_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.052086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1403-21_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.014704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1403-21_0_4_line_9 | NAYY 4x150 SE | 7 | 10 | 0.064351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1403-21_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.020516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1403-21_0_4_line_11 | NAYY 4x150 SE | 8 | 39 | 0.023321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1403-21_0_4_line_12 | NAYY 4x150 SE | 9 | 123 | 0.00214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1403-21_0_4_line_13 | NAYY 4x150 SE | 10 | 37 | 0.024024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1403-21_0_4_line_14 | NAYY 4x150 SE | 11 | 36 | 0.014254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1403-21_0_4_line_15 | NAYY 4x150 SE | 12 | 13 | 0.018923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1403-21_0_4_line_16 | NAYY 4x150 SE | 13 | 14 | 0.02712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1403-21_0_4_line_17 | NAYY 4x150 SE | 13 | 15 | 0.027615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1403-21_0_4_line_18 | NAYY 4x150 SE | 14 | 16 | 0.02648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1403-21_0_4_line_19 | NAYY 4x150 SE | 14 | 17 | 0.046613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1403-21_0_4_line_20 | NAYY 4x150 SE | 14 | 18 | 0.044849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1403-21_0_4_line_21 | NAYY 4x150 SE | 15 | 19 | 0.032001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1403-21_0_4_line_22 | NAYY 4x150 SE | 16 | 20 | 0.010277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1403-21_0_4_line_23 | NAYY 4x150 SE | 17 | 21 | 0.0012509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1403-21_0_4_line_24 | NAYY 4x150 SE | 18 | 22 | 0.042071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1403-21_0_4_line_25 | NAYY 4x150 SE | 20 | 26 | 0.017976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1403-21_0_4_line_26 | NAYY 4x150 SE | 21 | 27 | 0.0036503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1403-21_0_4_line_27 | NAYY 4x150 SE | 22 | 23 | 0.0002062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1403-21_0_4_line_28 | NAYY 4x150 SE | 23 | 24 | 0.033298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1403-21_0_4_line_29 | NAYY 4x150 SE | 24 | 25 | 0.008952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1403-21_0_4_line_30 | NAYY 4x150 SE | 25 | 33 | 0.013604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1403-21_0_4_line_31 | NAYY 4x150 SE | 26 | 28 | 0.012335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1403-21_0_4_line_32 | NAYY 4x150 SE | 27 | 108 | 0.012113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1403-21_0_4_line_33 | NAYY 4x150 SE | 28 | 29 | 4.7863e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1403-21_0_4_line_34 | NAYY 4x150 SE | 29 | 30 | 0.010002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1403-21_0_4_line_35 | NAYY 4x150 SE | 30 | 31 | 0.005969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1403-21_0_4_line_36 | NAYY 4x150 SE | 31 | 32 | 0.0091236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1403-21_0_4_line_37 | NAYY 4x150 SE | 32 | 35 | 0.022045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1403-21_0_4_line_38 | NAYY 4x150 SE | 33 | 34 | 0.050522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1403-21_0_4_line_39 | NAYY 4x150 SE | 35 | 36 | 0.004623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1403-21_0_4_line_40 | NAYY 4x150 SE | 38 | 39 | 0.00053663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_1403-21_0_4_line_41 | NAYY 4x150 SE | 38 | 40 | 0.016362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1403-21_0_4_line_42 | NAYY 4x150 SE | 40 | 41 | 0.00022947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_1403-21_0_4_line_43 | NAYY 4x150 SE | 40 | 42 | 0.013461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1403-21_0_4_line_44 | NAYY 4x150 SE | 41 | 43 | 0.019124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_1403-21_0_4_line_45 | NAYY 4x150 SE | 42 | 44 | 0.025392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1403-21_0_4_line_46 | NAYY 4x150 SE | 43 | 45 | 0.0034011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_1403-21_0_4_line_47 | NAYY 4x150 SE | 45 | 46 | 0.002533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_1403-21_0_4_line_48 | NAYY 4x150 SE | 46 | 47 | 0.0059365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1403-21_0_4_line_49 | NAYY 4x150 SE | 47 | 53 | 0.0059147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_1403-21_0_4_line_50 | NAYY 4x150 SE | 48 | 49 | 0.037354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_1403-21_0_4_line_51 | NAYY 4x150 SE | 48 | 50 | 0.023508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
52 | LV_1403-21_0_4_line_52 | NAYY 4x150 SE | 49 | 51 | 0.0037535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1403-21_0_4_line_53 | NAYY 4x150 SE | 50 | 52 | 0.01663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1403-21_0_4_line_54 | NAYY 4x150 SE | 50 | 53 | 0.012863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_1403-21_0_4_line_55 | NAYY 4x150 SE | 51 | 54 | 0.054581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_1403-21_0_4_line_56 | NAYY 4x150 SE | 52 | 55 | 0.032291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1403-21_0_4_line_57 | NAYY 4x150 SE | 54 | 56 | 0.041258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_1403-21_0_4_line_58 | NAYY 4x150 SE | 55 | 57 | 0.016816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1403-21_0_4_line_59 | NAYY 4x150 SE | 56 | 64 | 0.03537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1403-21_0_4_line_60 | NAYY 4x150 SE | 56 | 65 | 0.2198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_1403-21_0_4_line_61 | NAYY 4x150 SE | 57 | 58 | 0.012118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1403-21_0_4_line_62 | NAYY 4x150 SE | 58 | 59 | 0.0027879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1403-21_0_4_line_63 | NAYY 4x150 SE | 59 | 68 | 0.015886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1403-21_0_4_line_64 | NAYY 4x150 SE | 60 | 61 | 0.024789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1403-21_0_4_line_65 | NAYY 4x150 SE | 61 | 62 | 0.012569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1403-21_0_4_line_66 | NAYY 4x150 SE | 62 | 63 | 0.01074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1403-21_0_4_line_67 | NAYY 4x150 SE | 63 | 64 | 0.012918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1403-21_0_4_line_68 | NAYY 4x150 SE | 65 | 66 | 0.089937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1403-21_0_4_line_69 | NAYY 4x150 SE | 65 | 67 | 0.018116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1403-21_0_4_line_70 | NAYY 4x150 SE | 66 | 98 | 0.021545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1403-21_0_4_line_71 | NAYY 4x150 SE | 66 | 96 | 0.11588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1403-21_0_4_line_72 | NAYY 4x150 SE | 68 | 69 | 0.0029624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1403-21_0_4_line_73 | NAYY 4x150 SE | 69 | 70 | 0.011536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1403-21_0_4_line_74 | NAYY 4x150 SE | 70 | 71 | 0.030975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1403-21_0_4_line_75 | NAYY 4x150 SE | 71 | 72 | 0.021504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1403-21_0_4_line_76 | NAYY 4x150 SE | 72 | 73 | 0.01575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1403-21_0_4_line_77 | NAYY 4x150 SE | 73 | 74 | 0.040747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1403-21_0_4_line_78 | NAYY 4x150 SE | 74 | 75 | 0.047041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1403-21_0_4_line_79 | NAYY 4x150 SE | 74 | 76 | 0.054476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1403-21_0_4_line_80 | NAYY 4x150 SE | 75 | 77 | 0.043847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1403-21_0_4_line_81 | NAYY 4x150 SE | 78 | 79 | 0.11938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1403-21_0_4_line_82 | NAYY 4x150 SE | 79 | 80 | 0.076159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1403-21_0_4_line_83 | NAYY 4x150 SE | 79 | 81 | 0.041122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1403-21_0_4_line_84 | NAYY 4x150 SE | 80 | 85 | 0.13699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1403-21_0_4_line_85 | NAYY 4x150 SE | 82 | 83 | 0.26111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1403-21_0_4_line_86 | NAYY 4x150 SE | 82 | 84 | 0.082481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1403-21_0_4_line_87 | NAYY 4x150 SE | 83 | 86 | 0.042437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1403-21_0_4_line_88 | NAYY 4x150 SE | 84 | 105 | 0.023457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1403-21_0_4_line_89 | NAYY 4x150 SE | 85 | 86 | 0.029904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1403-21_0_4_line_90 | NAYY 4x150 SE | 87 | 88 | 0.0044907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1403-21_0_4_line_91 | NAYY 4x150 SE | 87 | 89 | 0.010142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1403-21_0_4_line_92 | NAYY 4x150 SE | 88 | 90 | 0.0093539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1403-21_0_4_line_93 | NAYY 4x150 SE | 89 | 91 | 0.01141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1403-21_0_4_line_94 | NAYY 4x150 SE | 90 | 92 | 0.044111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1403-21_0_4_line_95 | NAYY 4x150 SE | 91 | 93 | 0.017578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1403-21_0_4_line_96 | NAYY 4x150 SE | 91 | 94 | 0.1262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1403-21_0_4_line_97 | NAYY 4x150 SE | 93 | 105 | 0.022189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1403-21_0_4_line_98 | NAYY 4x150 SE | 94 | 96 | 0.023008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1403-21_0_4_line_99 | NAYY 4x150 SE | 95 | 96 | 0.020398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1403-21_0_4_line_100 | NAYY 4x150 SE | 95 | 97 | 0.015019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1403-21_0_4_line_101 | NAYY 4x150 SE | 98 | 99 | 0.0084781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1403-21_0_4_line_102 | NAYY 4x150 SE | 99 | 102 | 0.017525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1403-21_0_4_line_103 | NAYY 4x150 SE | 99 | 100 | 0.035284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1403-21_0_4_line_104 | NAYY 4x150 SE | 100 | 101 | 0.027862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1403-21_0_4_line_105 | NAYY 4x150 SE | 102 | 103 | 0.0097826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1403-21_0_4_line_106 | NAYY 4x150 SE | 103 | 104 | 0.024222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1403-21_0_4_line_107 | NAYY 4x150 SE | 106 | 107 | 0.0078779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1403-21_0_4_line_108 | NAYY 4x150 SE | 107 | 124 | 0.016846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1403-21_0_4_line_109 | NAYY 4x150 SE | 108 | 109 | 0.0045744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1403-21_0_4_line_110 | NAYY 4x150 SE | 109 | 110 | 0.0033783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1403-21_0_4_line_111 | NAYY 4x150 SE | 110 | 111 | 0.0033735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1403-21_0_4_line_112 | NAYY 4x150 SE | 111 | 112 | 0.016578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1403-21_0_4_line_113 | NAYY 4x150 SE | 112 | 113 | 0.028184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1403-21_0_4_line_114 | NAYY 4x150 SE | 113 | 114 | 0.022225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1403-21_0_4_line_115 | NAYY 4x150 SE | 114 | 115 | 0.0088052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1403-21_0_4_line_116 | NAYY 4x150 SE | 115 | 116 | 0.0082388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1403-21_0_4_line_117 | NAYY 4x150 SE | 116 | 117 | 0.0028734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1403-21_0_4_line_118 | NAYY 4x150 SE | 117 | 118 | 0.041756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1403-21_0_4_line_119 | NAYY 4x150 SE | 118 | 119 | 0.0087476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1403-21_0_4_line_120 | NAYY 4x150 SE | 120 | 121 | 0.018507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1403-21_0_4_line_121 | NAYY 4x150 SE | 120 | 122 | 0.006323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1403-21_0_4_line_122 | NAYY 4x150 SE | 121 | 123 | 0.014963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1403-21_0_4_line_123 | NAYY 4x150 SE | 122 | 124 | 0.011308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1403-21_0_4_trafo_2 | 0.25 MVA 20/0.4 kV | 125 | 2 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2656703.7231 | 1188294.6349 | 2656695.4225 | 1188272.5058
1 | 2656679.3333 | 1188229.6119 | 2656695.4225 | 1188272.5058
2 | 2656679.3333 | 1188229.6119 | 2656666.5588 | 1188247.0343
3 | 2656679.3333 | 1188229.6119 | 2656695.3162 | 1188207.5781
4 | 2656663.1959 | 1188251.7496 | 2656666.5588 | 1188247.0343
5 | 2656666.5588 | 1188247.0343 | 2656619.7319 | 1188212.6886
6 | 2656699.8852 | 1188201.2793 | 2656695.3162 | 1188207.5781
7 | 2656663.1959 | 1188251.7496 | 2656671.9463 | 1188274.2339 | 2656674.1789 | 1188278.5241 | 2656677.8532 | 1188283.6284 | 2656679.5327 | 1188286.7127 | 2656684.4756 | 1188299.0834
8 | 2656619.7319 | 1188212.6886 | 2656612.9529 | 1188207.7164 | 2656610.5079 | 1188204.9029 | 2656609.3856 | 1188202.5909
9 | 2656699.8852 | 1188201.2793 | 2656707.5259 | 1188206.4101 | 2656711.5435 | 1188212.3181 | 2656729.1633 | 1188256.97
10 | 2656699.8852 | 1188201.2793 | 2656711.9345 | 1188184.6748
11 | 2656684.4756 | 1188299.0834 | 2656686.1498 | 1188303.2735 | 2656688.2259 | 1188306.3616 | 2656692.9993 | 1188311.3985 | 2656694.8527 | 1188314.6401 | 2656696.4649 | 1188318.7493
12 | 2656609.1387 | 1188200.4652 | 2656609.3856 | 1188202.5909 | 2656609.3856 | 1188202.5909
13 | 2656737.9816 | 1188279.3173 | 2656729.1633 | 1188256.97
14 | 2656720.3062 | 1188173.1383 | 2656711.9345 | 1188184.6748
15 | 2656810.9974 | 1188060.786 | 2656809.3474 | 1188041.9353
16 | 2656788.381 | 1188075.8467 | 2656810.9974 | 1188060.786
17 | 2656838.0202 | 1188054.8834 | 2656814.1663 | 1188059.6598 | 2656810.9974 | 1188060.786
18 | 2656788.381 | 1188075.8467 | 2656778.7874 | 1188093.2211 | 2656774.811 | 1188098.5303
19 | 2656788.381 | 1188075.8467 | 2656783.7541 | 1188029.464
20 | 2656788.381 | 1188075.8467 | 2656801.4659 | 1188070.0008 | 2656809.3045 | 1188071.9762 | 2656813.158 | 1188075.0701 | 2656816.3362 | 1188092.2707
21 | 2656838.0202 | 1188054.8834 | 2656835.9831 | 1188022.9468
22 | 2656768.6504 | 1188106.7557 | 2656774.811 | 1188098.5303
23 | 2656783.63 | 1188028.2193 | 2656783.63 | 1188028.2193 | 2656783.7541 | 1188029.464
24 | 2656816.3362 | 1188092.2707 | 2656821.9159 | 1188122.4687 | 2656824.2759 | 1188133.5832
25 | 2656768.6504 | 1188106.7557 | 2656763.1031 | 1188114.1621 | 2656757.9801 | 1188121.2218
26 | 2656783.63 | 1188028.2193 | 2656783.3324 | 1188024.5811
27 | 2656824.3187 | 1188133.7849 | 2656824.2759 | 1188133.5832
28 | 2656831.2349 | 1188166.3563 | 2656824.3187 | 1188133.7849
29 | 2656831.2349 | 1188166.3563 | 2656833.0943 | 1188175.1131
30 | 2656835.92 | 1188188.4207 | 2656833.0943 | 1188175.1131
31 | 2656750.7355 | 1188131.2053 | 2656757.9801 | 1188121.2218
32 | 2656783.3324 | 1188024.5811 | 2656782.3449 | 1188012.5084
33 | 2656750.7074 | 1188131.244 | 2656750.7355 | 1188131.2053
34 | 2656750.7074 | 1188131.244 | 2656744.8331 | 1188139.339
35 | 2656741.3274 | 1188144.1701 | 2656744.8331 | 1188139.339
36 | 2656741.3274 | 1188144.1701 | 2656735.9689 | 1188151.5543
37 | 2656735.9689 | 1188151.5543 | 2656723.0214 | 1188169.3966
38 | 2656835.92 | 1188188.4207 | 2656871.3191 | 1188224.468
39 | 2656720.3062 | 1188173.1383 | 2656723.0214 | 1188169.3966
40 | 2656696.4649 | 1188318.7493 | 2656696.6608 | 1188319.2489
41 | 2656702.6363 | 1188334.4805 | 2656696.6608 | 1188319.2489
42 | 2656702.7202 | 1188334.6941 | 2656702.6363 | 1188334.4805
43 | 2656702.6363 | 1188334.4805 | 2656715.302 | 1188329.9211
44 | 2656709.7083 | 1188352.4957 | 2656702.7202 | 1188334.6941
45 | 2656735.6911 | 1188332.3141 | 2656734.3984 | 1188329.0114 | 2656733.448 | 1188327.068 | 2656732.3014 | 1188325.7119 | 2656730.1334 | 1188325.0799 | 2656728.0638 | 1188325.3271 | 2656715.302 | 1188329.9211
46 | 2656709.7083 | 1188352.4957 | 2656710.9511 | 1188355.6615
47 | 2656711.8766 | 1188358.0193 | 2656710.9511 | 1188355.6615
48 | 2656714.0459 | 1188363.5453 | 2656711.8766 | 1188358.0193
49 | 2656714.0459 | 1188363.5453 | 2656716.2071 | 1188369.0509
50 | 2656697.4773 | 1188379.1158 | 2656663.451 | 1188376.3445 | 2656660.239 | 1188376.2148
51 | 2656720.9073 | 1188381.0241 | 2656697.4773 | 1188379.1158
52 | 2656656.5273 | 1188376.7241 | 2656656.6128 | 1188376.7022 | 2656659.8519 | 1188376.1992 | 2656660.239 | 1188376.2148
53 | 2656720.9073 | 1188381.0241 | 2656737.4819 | 1188382.3754
54 | 2656720.9073 | 1188381.0241 | 2656716.2071 | 1188369.0509
55 | 2656605.9983 | 1188389.5068 | 2656622.4682 | 1188391.3543 | 2656627.228 | 1188391.366 | 2656630.4907 | 1188390.7854 | 2656634.9507 | 1188389.4268 | 2656638.7766 | 1188387.3618 | 2656645.209 | 1188382.3198 | 2656649.8465 | 1188379.1396 | 2656653.6383 | 1188377.4634 | 2656656.5273 | 1188376.7241
56 | 2656769.6666 | 1188384.9993 | 2656737.4819 | 1188382.3754
57 | 2656565.5933 | 1188383.2681 | 2656567.4488 | 1188384.6864 | 2656568.5573 | 1188385.2305 | 2656569.5472 | 1188385.4177 | 2656605.9983 | 1188389.5068
58 | 2656769.6666 | 1188384.9993 | 2656786.427 | 1188386.3664
59 | 2656565.5933 | 1188383.2681 | 2656586.6716 | 1188354.8653
60 | 2656565.5933 | 1188383.2681 | 2656355.3799 | 1188319.0731
61 | 2656786.427 | 1188386.3664 | 2656798.5048 | 1188387.3515
62 | 2656801.2835 | 1188387.5782 | 2656798.5048 | 1188387.3515
63 | 2656816.8506 | 1188390.743 | 2656801.2835 | 1188387.5782 | 2656801.2835 | 1188387.5782
64 | 2656623.0332 | 1188305.8684 | 2656608.2605 | 1188325.7744
65 | 2656600.7703 | 1188335.8674 | 2656608.2605 | 1188325.7744
66 | 2656600.7703 | 1188335.8674 | 2656594.3701 | 1188344.4916
67 | 2656586.6716 | 1188354.8653 | 2656594.3701 | 1188344.4916
68 | 2656266.859 | 1188325.1445 | 2656328.8768 | 1188325.0495 | 2656345.5414 | 1188323.7388 | 2656352.6621 | 1188321.7379 | 2656355.3799 | 1188319.0731
69 | 2656351.8638 | 1188302.8087 | 2656355.9664 | 1188309.4399 | 2656357.5093 | 1188314.0903 | 2656355.3799 | 1188319.0731
70 | 2656266.859 | 1188325.1445 | 2656264.3506 | 1188312.0136 | 2656263.2658 | 1188303.9089
71 | 2656266.859 | 1188325.1445 | 2656263.2342 | 1188440.9684
72 | 2656819.7536 | 1188391.3332 | 2656816.8506 | 1188390.743
73 | 2656819.7536 | 1188391.3332 | 2656819.7536 | 1188391.3332 | 2656829.9002 | 1188396.8215
74 | 2656829.9002 | 1188396.8215 | 2656829.9002 | 1188396.8215 | 2656839.8948 | 1188406.2772 | 2656850.5671 | 1188419.7871
75 | 2656850.5671 | 1188419.7871 | 2656863.8969 | 1188436.6613
76 | 2656863.8969 | 1188436.6613 | 2656873.6603 | 1188449.0206
77 | 2656873.6603 | 1188449.0206 | 2656898.9187 | 1188480.995
78 | 2656898.9187 | 1188480.995 | 2656928.0783 | 1188517.9079
79 | 2656898.9187 | 1188480.995 | 2656945.5698 | 1188452.8644
80 | 2656928.0783 | 1188517.9079 | 2656971.5126 | 1188511.9081
81 | 2656697.4524 | 1188777.1924 | 2656690.1675 | 1188896.3468
82 | 2656697.4524 | 1188777.1924 | 2656677.2812 | 1188775.1781 | 2656626.4383 | 1188751.5173
83 | 2656697.4524 | 1188777.1924 | 2656698.4482 | 1188736.0827
84 | 2656626.4383 | 1188751.5173 | 2656518.9502 | 1188836.4448
85 | 2656424.5946 | 1188581.6948 | 2656447.7035 | 1188841.7815
86 | 2656424.5946 | 1188581.6948 | 2656342.4792 | 1188573.9427
87 | 2656447.7035 | 1188841.7815 | 2656466.9369 | 1188842.9189 | 2656484.1919 | 1188844.3713 | 2656489.8486 | 1188842.8655
88 | 2656319.1262 | 1188571.7381 | 2656342.4792 | 1188573.9427
89 | 2656518.9502 | 1188836.4448 | 2656507.289 | 1188837.7965 | 2656496.0902 | 1188841.2039 | 2656489.8486 | 1188842.8655
90 | 2656264.6363 | 1188577.2153 | 2656263.1042 | 1188581.4366
91 | 2656268.0963 | 1188567.6817 | 2656264.6363 | 1188577.2153
92 | 2656263.1042 | 1188581.4366 | 2656259.9131 | 1188590.2293
93 | 2656279.5351 | 1188568.0005 | 2656268.0963 | 1188567.6817
94 | 2656245.9373 | 1188632.0594 | 2656254.4164 | 1188605.3745 | 2656259.9131 | 1188590.2293
95 | 2656279.5351 | 1188568.0005 | 2656297.0356 | 1188569.6526
96 | 2656279.5351 | 1188568.0005 | 2656286.2194 | 1188441.9811
97 | 2656297.0356 | 1188569.6526 | 2656319.1262 | 1188571.7381
98 | 2656286.2194 | 1188441.9811 | 2656263.2342 | 1188440.9684
99 | 2656242.856 | 1188440.0705 | 2656263.2342 | 1188440.9684
100 | 2656227.8511 | 1188439.4094 | 2656242.856 | 1188440.0705
101 | 2656262.141 | 1188295.5058 | 2656263.2658 | 1188303.9089
102 | 2656262.141 | 1188295.5058 | 2656244.9158 | 1188298.7347
103 | 2656262.141 | 1188295.5058 | 2656267.4277 | 1188267.0505 | 2656268.364 | 1188260.7781
104 | 2656271.1721 | 1188233.0776 | 2656269.9351 | 1188250.2535 | 2656268.364 | 1188260.7781
105 | 2656244.9158 | 1188298.7347 | 2656237.8558 | 1188300.0581 | 2656235.5569 | 1188301.2717
106 | 2656230.8161 | 1188321.871 | 2656228.4001 | 1188312.7098 | 2656228.3712 | 1188308.4738 | 2656231.6692 | 1188303.3241 | 2656235.5569 | 1188301.2717
107 | 2656588.3869 | 1188148.0964 | 2656594.8236 | 1188152.6385
108 | 2656594.8236 | 1188152.6385 | 2656597.9822 | 1188154.8674 | 2656601.3742 | 1188156.7561 | 2656606.7263 | 1188158.6966 | 2656609.7398 | 1188160.2815 | 2656609.7398 | 1188160.2815
109 | 2656781.972 | 1188007.9493 | 2656782.3449 | 1188012.5084
110 | 2656781.6966 | 1188004.5822 | 2656781.972 | 1188007.9493
111 | 2656781.4216 | 1188001.2199 | 2656781.6966 | 1188004.5822
112 | 2656781.4216 | 1188001.2199 | 2656780.7588 | 1187993.1167 | 2656778.9362 | 1187984.8681
113 | 2656769.8351 | 1187958.5308 | 2656775.1119 | 1187967.5599 | 2656778.9362 | 1187984.8681
114 | 2656755.608 | 1187941.5382 | 2656767.9578 | 1187955.3186 | 2656769.8351 | 1187958.5308
115 | 2656755.608 | 1187941.5382 | 2656747.9984 | 1187937.1081
116 | 2656747.9984 | 1187937.1081 | 2656747.9984 | 1187937.1081 | 2656741.0553 | 1187932.6728
117 | 2656738.6338 | 1187931.126 | 2656741.0553 | 1187932.6728
118 | 2656702.5254 | 1187910.1939 | 2656726.9941 | 1187923.6905 | 2656738.6338 | 1187931.126
119 | 2656702.5254 | 1187910.1939 | 2656694.8658 | 1187905.969
120 | 2656623.3732 | 1188171.4167 | 2656624.0628 | 1188173.5132 | 2656623.7804 | 1188175.9453 | 2656622.8029 | 1188178.4819 | 2656616.393 | 1188187.5846
121 | 2656623.3732 | 1188171.4167 | 2656623.3732 | 1188171.4167 | 2656621.7271 | 1188169.6334 | 2656618.6551 | 1188167.2369
122 | 2656616.393 | 1188187.5846 | 2656610.6866 | 1188195.6882 | 2656609.5638 | 1188198.2569 | 2656609.1387 | 1188200.4652 | 2656609.1387 | 1188200.4652
123 | 2656609.7398 | 1188160.2815 | 2656618.6551 | 1188167.2369

## bus_geodata
| x | y | coords
0 | 2656695.4225 | 1188272.5058
1 | 2656703.7231 | 1188294.6349
2 | 2656679.3333 | 1188229.6119
3 | 2656666.5588 | 1188247.0343
4 | 2656695.3162 | 1188207.5781
5 | 2656663.1959 | 1188251.7496
6 | 2656619.7319 | 1188212.6886
7 | 2656699.8852 | 1188201.2793
8 | 2656684.4756 | 1188299.0834
9 | 2656609.3856 | 1188202.5909
10 | 2656729.1633 | 1188256.97
11 | 2656711.9345 | 1188184.6748
12 | 2656809.3474 | 1188041.9353
13 | 2656810.9974 | 1188060.786
14 | 2656788.381 | 1188075.8467
15 | 2656838.0202 | 1188054.8834
16 | 2656774.811 | 1188098.5303
17 | 2656783.7541 | 1188029.464
18 | 2656816.3362 | 1188092.2707
19 | 2656835.9831 | 1188022.9468
20 | 2656768.6504 | 1188106.7557
21 | 2656783.63 | 1188028.2193
22 | 2656824.2759 | 1188133.5832
23 | 2656824.3187 | 1188133.7849
24 | 2656831.2349 | 1188166.3563
25 | 2656833.0943 | 1188175.1131
26 | 2656757.9801 | 1188121.2218
27 | 2656783.3324 | 1188024.5811
28 | 2656750.7355 | 1188131.2053
29 | 2656750.7074 | 1188131.244
30 | 2656744.8331 | 1188139.339
31 | 2656741.3274 | 1188144.1701
32 | 2656735.9689 | 1188151.5543
33 | 2656835.92 | 1188188.4207
34 | 2656871.3191 | 1188224.468
35 | 2656723.0214 | 1188169.3966
36 | 2656720.3062 | 1188173.1383
37 | 2656737.9816 | 1188279.3173
38 | 2656696.6608 | 1188319.2489
39 | 2656696.4649 | 1188318.7493
40 | 2656702.6363 | 1188334.4805
41 | 2656702.7202 | 1188334.6941
42 | 2656715.302 | 1188329.9211
43 | 2656709.7083 | 1188352.4957
44 | 2656735.6911 | 1188332.3141
45 | 2656710.9511 | 1188355.6615
46 | 2656711.8766 | 1188358.0193
47 | 2656714.0459 | 1188363.5453
48 | 2656697.4773 | 1188379.1158
49 | 2656660.239 | 1188376.2148
50 | 2656720.9073 | 1188381.0241
51 | 2656656.5273 | 1188376.7241
52 | 2656737.4819 | 1188382.3754
53 | 2656716.2071 | 1188369.0509
54 | 2656605.9983 | 1188389.5068
55 | 2656769.6666 | 1188384.9993
56 | 2656565.5933 | 1188383.2681
57 | 2656786.427 | 1188386.3664
58 | 2656798.5048 | 1188387.3515
59 | 2656801.2835 | 1188387.5782
60 | 2656623.0332 | 1188305.8684
61 | 2656608.2605 | 1188325.7744
62 | 2656600.7703 | 1188335.8674
63 | 2656594.3701 | 1188344.4916
64 | 2656586.6716 | 1188354.8653
65 | 2656355.3799 | 1188319.0731
66 | 2656266.859 | 1188325.1445
67 | 2656351.8638 | 1188302.8086
68 | 2656816.8506 | 1188390.743
69 | 2656819.7536 | 1188391.3332
70 | 2656829.9002 | 1188396.8215
71 | 2656850.5671 | 1188419.7871
72 | 2656863.8969 | 1188436.6613
73 | 2656873.6603 | 1188449.0206
74 | 2656898.9187 | 1188480.995
75 | 2656928.0783 | 1188517.9079
76 | 2656945.5698 | 1188452.8644
77 | 2656971.5126 | 1188511.9081
78 | 2656690.1675 | 1188896.3468
79 | 2656697.4524 | 1188777.1924
80 | 2656626.4383 | 1188751.5173
81 | 2656698.4482 | 1188736.0827
82 | 2656424.5946 | 1188581.6948
83 | 2656447.7035 | 1188841.7815
84 | 2656342.4792 | 1188573.9427
85 | 2656518.9502 | 1188836.4448
86 | 2656489.8486 | 1188842.8655
87 | 2656264.6363 | 1188577.2153
88 | 2656263.1042 | 1188581.4366
89 | 2656268.0963 | 1188567.6817
90 | 2656259.9131 | 1188590.2293
91 | 2656279.5351 | 1188568.0005
92 | 2656245.9373 | 1188632.0594
93 | 2656297.0356 | 1188569.6526
94 | 2656286.2194 | 1188441.9811
95 | 2656242.856 | 1188440.0705
96 | 2656263.2342 | 1188440.9684
97 | 2656227.8511 | 1188439.4094
98 | 2656263.2658 | 1188303.9089
99 | 2656262.141 | 1188295.5058
100 | 2656268.364 | 1188260.7781
101 | 2656271.1721 | 1188233.0776
102 | 2656244.9159 | 1188298.7347
103 | 2656235.5569 | 1188301.2717
104 | 2656230.8161 | 1188321.871
105 | 2656319.1262 | 1188571.7381
106 | 2656588.3869 | 1188148.0964
107 | 2656594.8236 | 1188152.6385
108 | 2656782.3449 | 1188012.5084
109 | 2656781.972 | 1188007.9493
110 | 2656781.6966 | 1188004.5822
111 | 2656781.4216 | 1188001.2199
112 | 2656778.9362 | 1187984.8681
113 | 2656769.8351 | 1187958.5308
114 | 2656755.608 | 1187941.5382
115 | 2656747.9984 | 1187937.1081
116 | 2656741.0553 | 1187932.6728
117 | 2656738.6338 | 1187931.126
118 | 2656702.5254 | 1187910.1939
119 | 2656694.8658 | 1187905.969
120 | 2656623.3732 | 1188171.4167
121 | 2656616.393 | 1188187.5846
122 | 2656618.6551 | 1188167.2369
123 | 2656609.1387 | 1188200.4652
124 | 2656609.7398 | 1188160.2815
125 | 2656666.5588 | 1188247.0343

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99945 | -0.0038511 | 0.0078923 | 0.001978
1 | 0.99943 | -0.0039746 | 0.00052147 | 0.00013069
2 | 1 | 0 | -0.22181 | -0.055731
3 | 0.99815 | -0.012881 | 0 | 0
4 | 0.99642 | -0.024725 | 0.0032511 | 0.00081481
5 | 0.99782 | -0.015189 | 0 | 0
6 | 0.99484 | -0.036064 | 0.028327 | 0.0070995
7 | 0.99543 | -0.03157 | 0 | 0
8 | 0.99483 | -0.036038 | 0.0037634 | 0.00094319
9 | 0.9946 | -0.037754 | 0.00078212 | 0.00019602
10 | 0.9948 | -0.036031 | 0.0049784 | 0.0012477
11 | 0.99303 | -0.048256 | 0.0006843 | 0.0001715
12 | 0.97919 | -0.14583 | 0.0031328 | 0.00078515
13 | 0.97928 | -0.14521 | 0 | 0
14 | 0.97957 | -0.14307 | 0 | 0
15 | 0.9791 | -0.14649 | 0 | 0
16 | 0.98166 | -0.12822 | 0.01108 | 0.002777
17 | 0.97786 | -0.15534 | 0.001484 | 0.00037194
18 | 0.97819 | -0.15296 | 0.01051 | 0.002634
19 | 0.97889 | -0.14797 | 0.0044408 | 0.001113
20 | 0.98263 | -0.1213 | 0.0014398 | 0.00036085
21 | 0.97781 | -0.15565 | 0.0026468 | 0.00066335
22 | 0.97754 | -0.15764 | 0.00052676 | 0.00013202
23 | 0.97753 | -0.15766 | 0.0033076 | 0.00082897
24 | 0.9772 | -0.16004 | 0.0010647 | 0.00026685
25 | 0.97713 | -0.16058 | 0.0018278 | 0.0004581
26 | 0.98438 | -0.10896 | 0.0038146 | 0.00095603
27 | 0.9777 | -0.15645 | 0.0034687 | 0.00086933
28 | 0.98564 | -0.10003 | 0.0012536 | 0.00031418
29 | 0.98564 | -0.099992 | 0.0016468 | 0.00041272
30 | 0.98671 | -0.092472 | 0.0011421 | 0.00028623
31 | 0.98736 | -0.087922 | 0.0014067 | 0.00035254
32 | 0.98836 | -0.080848 | 0.0013403 | 0.0003359
33 | 0.97705 | -0.16113 | 0.0012063 | 0.00030233
34 | 0.97685 | -0.16257 | 0.0027161 | 0.00068072
35 | 0.99084 | -0.063513 | 0.0019644 | 0.00049233
36 | 0.99137 | -0.059796 | 0.00074037 | 0.00018556
37 | 0.99473 | -0.03649 | 0.0018931 | 0.00047445
38 | 0.99353 | -0.045166 | 0.0029072 | 0.0007286
39 | 0.99356 | -0.044969 | 0.0032973 | 0.00082638
40 | 0.99271 | -0.050931 | 0 | 0
41 | 0.9927 | -0.051005 | 0.00087792 | 0.00022003
42 | 0.9926 | -0.051719 | 0.0015854 | 0.00039733
43 | 0.99183 | -0.05711 | 0.00092351 | 0.00023145
44 | 0.99244 | -0.052798 | 0.0041925 | 0.0010507
45 | 0.99168 | -0.05818 | 0.00073918 | 0.00018526
46 | 0.99157 | -0.058969 | 0.00092312 | 0.00023136
47 | 0.99131 | -0.060789 | 0.00092383 | 0.00023153
48 | 0.9898 | -0.071404 | 0.00063028 | 0.00015796
49 | 0.98869 | -0.079242 | 0.0023526 | 0.00058962
50 | 0.99051 | -0.066404 | 0 | 0
51 | 0.98859 | -0.079986 | 0.0036571 | 0.00091655
52 | 0.99011 | -0.069239 | 0.0017973 | 0.00045045
53 | 0.99105 | -0.062575 | 0.00091646 | 0.00022969
54 | 0.9872 | -0.089791 | 0.0046946 | 0.0011766
55 | 0.98942 | -0.074159 | 0 | 0
56 | 0.9863 | -0.096225 | 0 | 0
57 | 0.98905 | -0.076724 | 0.002189 | 0.00054861
58 | 0.98883 | -0.078302 | 0.0011067 | 0.00027737
59 | 0.98878 | -0.078634 | 0.0035481 | 0.00088925
60 | 0.98508 | -0.10485 | 0.0013755 | 0.00034474
61 | 0.98513 | -0.1045 | 0.0041116 | 0.0010305
62 | 0.98523 | -0.10379 | 0.003738 | 0.00093684
63 | 0.98537 | -0.10277 | 0.0032322 | 0.00081007
64 | 0.98561 | -0.10112 | 0.0010136 | 0.00025403
65 | 0.98361 | -0.11536 | 0.00124 | 0.00031078
66 | 0.9816 | -0.12969 | 0 | 0
67 | 0.9836 | -0.11541 | 0.00024702 | 6.1908e-05
68 | 0.9886 | -0.079948 | 0.0004561 | 0.00011431
69 | 0.98857 | -0.08018 | 0.00045829 | 0.00011486
70 | 0.98845 | -0.081027 | 0.0007253 | 0.00018178
71 | 0.98816 | -0.083073 | 0.00050824 | 0.00012738
72 | 0.98798 | -0.084381 | 0.00093704 | 0.00023485
73 | 0.98786 | -0.085189 | 0.00029706 | 7.4449e-05
74 | 0.98759 | -0.087154 | 0.0021148 | 0.00053003
75 | 0.98747 | -0.087949 | 0.00082263 | 0.00020617
76 | 0.98751 | -0.087678 | 0.00093791 | 0.00023506
77 | 0.98742 | -0.088319 | 0.00082259 | 0.00020616
78 | 0.97103 | -0.20583 | 0.00030325 | 7.6002e-05
79 | 0.97109 | -0.20544 | 0 | 0
80 | 0.97145 | -0.20279 | 0.00067891 | 0.00017015
81 | 0.97091 | -0.20673 | 0.0029697 | 0.00074427
82 | 0.97582 | -0.17122 | 0 | 0
83 | 0.97301 | -0.19148 | 0 | 0
84 | 0.97671 | -0.16483 | 0.00018975 | 4.7557e-05
85 | 0.97225 | -0.19702 | 0.0031476 | 0.00078886
86 | 0.97256 | -0.19477 | 0.000228 | 5.7141e-05
87 | 0.97743 | -0.15961 | 0.00032492 | 8.1433e-05
88 | 0.97743 | -0.15964 | 0.00017804 | 4.4622e-05
89 | 0.97744 | -0.15951 | 0 | 0
90 | 0.97742 | -0.15968 | 0.00010025 | 2.5125e-05
91 | 0.97746 | -0.1594 | 0 | 0
92 | 0.9774 | -0.15982 | 0.00030899 | 7.7441e-05
93 | 0.97723 | -0.16106 | 0.0007826 | 0.00019614
94 | 0.97928 | -0.14632 | 0 | 0
95 | 0.97958 | -0.14418 | 0.00047947 | 0.00012017
96 | 0.97961 | -0.14394 | 0.00077725 | 0.0001948
97 | 0.97956 | -0.14428 | 0.00063725 | 0.00015971
98 | 0.98149 | -0.13048 | 8.9837e-05 | 2.2515e-05
99 | 0.98145 | -0.13078 | 0 | 0
100 | 0.9813 | -0.13182 | 0.0003079 | 7.7168e-05
101 | 0.9812 | -0.13256 | 0.0025312 | 0.00063438
102 | 0.98143 | -0.1309 | 0.00013568 | 3.4005e-05
103 | 0.98143 | -0.13094 | 0.00017371 | 4.3537e-05
104 | 0.98142 | -0.13102 | 0.00029835 | 7.4773e-05
105 | 0.97696 | -0.16297 | 0.00063605 | 0.00015941
106 | 0.99385 | -0.043092 | 0.0017248 | 0.00043228
107 | 0.99387 | -0.042955 | 0.0029543 | 0.00074042
108 | 0.97739 | -0.15869 | 0.00072755 | 0.00018234
109 | 0.97728 | -0.1595 | 0.00049322 | 0.00012361
110 | 0.97719 | -0.16008 | 0.00049337 | 0.00012365
111 | 0.97712 | -0.16064 | 0.00049337 | 0.00012365
112 | 0.97674 | -0.16332 | 0.00083253 | 0.00020865
113 | 0.97614 | -0.16763 | 0.0013425 | 0.00033647
114 | 0.97571 | -0.17072 | 0 | 0
115 | 0.97554 | -0.17194 | 0.0014177 | 0.00035531
116 | 0.9754 | -0.17297 | 0.0028872 | 0.0007236
117 | 0.97536 | -0.17324 | 0.0018212 | 0.00045645
118 | 0.97492 | -0.17636 | 0.0027612 | 0.00069203
119 | 0.97487 | -0.17677 | 0.0043737 | 0.0010962
120 | 0.99414 | -0.040988 | 0.00073837 | 0.00018505
121 | 0.99436 | -0.039496 | 0.0020406 | 0.00051142
122 | 0.99408 | -0.04145 | 0.0010425 | 0.00026127
123 | 0.99457 | -0.037983 | 0.00058159 | 0.00014576
124 | 0.99398 | -0.042158 | 0.0015175 | 0.00038031
125 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00052148 | 0.00013039 | -0.00052147 | -0.00013069 | 8.8887e-09 | -3.063e-07 | 0.00077629 | 0.00077639 | 0.00077639 | 0.99945 | -0.0038511 | 0.99943 | -0.0039746 | 0.28755
1 | -0.0084138 | -0.0021084 | 0.0084183 | 0.0021095 | 4.4857e-06 | 1.1246e-06 | 0.012527 | 0.012526 | 0.012527 | 0.99945 | -0.0038511 | 1 | 0 | 4.6395
2 | 0.12031 | 0.030281 | -0.1201 | -0.030198 | 0.00021596 | 8.2496e-05 | 0.17907 | 0.17907 | 0.17907 | 1 | 0 | 0.99815 | -0.012881 | 33.1612
3 | 0.09228 | 0.023341 | -0.09196 | -0.023218 | 0.00032062 | 0.00012296 | 0.13739 | 0.13739 | 0.13739 | 1 | 0 | 0.99642 | -0.024725 | 50.8852
4 | 0.08025 | 0.020196 | -0.080224 | -0.020186 | 2.5854e-05 | 9.7928e-06 | 0.11966 | 0.11966 | 0.11966 | 0.99815 | -0.012881 | 0.99782 | -0.015189 | 22.16
5 | 0.039845 | 0.010003 | -0.039718 | -0.0099541 | 0.00012789 | 4.843e-05 | 0.059406 | 0.059407 | 0.059407 | 0.99815 | -0.012881 | 0.99484 | -0.036064 | 22.0025
6 | 0.088709 | 0.022403 | -0.088623 | -0.022371 | 8.5292e-05 | 3.2703e-05 | 0.13254 | 0.13254 | 0.13254 | 0.99642 | -0.024725 | 0.99543 | -0.03157 | 49.0871
7 | 0.080224 | 0.020186 | -0.079991 | -0.020098 | 0.00023271 | 8.8145e-05 | 0.11966 | 0.11966 | 0.11966 | 0.99782 | -0.015189 | 0.99483 | -0.036038 | 22.1601
8 | 0.01139 | 0.0028545 | -0.011387 | -0.0028537 | 2.6631e-06 | 8.334e-07 | 0.017036 | 0.017036 | 0.017036 | 0.99484 | -0.036064 | 0.9946 | -0.037754 | 6.3098
9 | 0.0068758 | 0.0017227 | -0.0068716 | -0.0017219 | 4.2421e-06 | 7.9558e-07 | 0.010278 | 0.010278 | 0.010278 | 0.99543 | -0.03157 | 0.9948 | -0.036031 | 3.8068
10 | 0.081748 | 0.020648 | -0.081556 | -0.020575 | 0.00019135 | 7.3329e-05 | 0.12226 | 0.12226 | 0.12226 | 0.99543 | -0.03157 | 0.99303 | -0.048256 | 45.2804
11 | 0.076228 | 0.019155 | -0.076133 | -0.019119 | 9.462e-05 | 3.5787e-05 | 0.11404 | 0.11404 | 0.11404 | 0.99483 | -0.036038 | 0.99356 | -0.044969 | 21.1177
12 | 0.010605 | 0.0026577 | -0.010605 | -0.0026576 | 3.3617e-07 | 1.0152e-07 | 0.015866 | 0.015866 | 0.015866 | 0.9946 | -0.037754 | 0.99457 | -0.037983 | 5.8764
13 | 0.0018932 | 0.00047418 | -0.0018931 | -0.00047445 | 1.2021e-07 | -2.6565e-07 | 0.0028317 | 0.0028318 | 0.0028318 | 0.9948 | -0.036031 | 0.99473 | -0.03649 | 1.0488
14 | 0.080872 | 0.020403 | -0.080741 | -0.020353 | 0.00013072 | 5.0094e-05 | 0.12123 | 0.12123 | 0.12123 | 0.99303 | -0.048256 | 0.99137 | -0.059796 | 44.9006
15 | -0.0031328 | -0.00078515 | 0.0031331 | 0.00078502 | 2.6761e-07 | -1.3512e-07 | 0.0047607 | 0.0047606 | 0.0047607 | 0.97919 | -0.14583 | 0.97928 | -0.14521 | 1.7632
16 | -0.0075756 | -0.0018979 | 0.0075779 | 0.0018984 | 2.2423e-06 | 5.2111e-07 | 0.011511 | 0.011511 | 0.011511 | 0.97928 | -0.14521 | 0.97957 | -0.14307 | 4.2633
17 | 0.0044425 | 0.0011129 | -0.0044418 | -0.0011129 | 7.852e-07 | -4.5364e-08 | 0.0067503 | 0.0067504 | 0.0067504 | 0.97928 | -0.14521 | 0.9791 | -0.14649 | 2.5002
18 | -0.054104 | -0.01357 | 0.054215 | 0.013613 | 0.00011162 | 4.2597e-05 | 0.08219 | 0.082189 | 0.08219 | 0.97957 | -0.14307 | 0.98166 | -0.12822 | 30.4406
19 | 0.025327 | 0.0063562 | -0.025284 | -0.0063403 | 4.3061e-05 | 1.5976e-05 | 0.038476 | 0.038477 | 0.038477 | 0.97957 | -0.14307 | 0.97786 | -0.15534 | 14.2506
20 | 0.021198 | 0.0053157 | -0.021169 | -0.0053051 | 2.9021e-05 | 1.0598e-05 | 0.032202 | 0.032203 | 0.032203 | 0.97957 | -0.14307 | 0.97819 | -0.15296 | 11.9269
21 | 0.0044418 | 0.0011129 | -0.0044408 | -0.001113 | 9.0996e-07 | -5.2397e-08 | 0.0067504 | 0.0067506 | 0.0067506 | 0.9791 | -0.14649 | 0.97889 | -0.14797 | 2.5002
22 | -0.065296 | -0.01639 | 0.065359 | 0.016414 | 6.2832e-05 | 2.4036e-05 | 0.098985 | 0.098985 | 0.098985 | 0.98166 | -0.12822 | 0.98263 | -0.1213 | 36.6613
23 | 0.0238 | 0.0059683 | -0.023799 | -0.005968 | 1.0239e-06 | 3.7812e-07 | 0.036218 | 0.036218 | 0.036218 | 0.97786 | -0.15534 | 0.97781 | -0.15565 | 13.4142
24 | 0.01066 | 0.0026711 | -0.010653 | -0.002669 | 6.9029e-06 | 2.1272e-06 | 0.016215 | 0.016216 | 0.016216 | 0.97819 | -0.15296 | 0.97754 | -0.15764 | 6.0058
25 | -0.066798 | -0.016775 | 0.066913 | 0.016819 | 0.0001148 | 4.3926e-05 | 0.10117 | 0.10117 | 0.10117 | 0.98263 | -0.1213 | 0.98438 | -0.10896 | 37.4688
26 | 0.021152 | 0.0053046 | -0.02115 | -0.0053037 | 2.3603e-06 | 8.6203e-07 | 0.03219 | 0.03219 | 0.03219 | 0.97781 | -0.15565 | 0.9777 | -0.15645 | 11.9224
27 | 0.010126 | 0.002537 | -0.010126 | -0.002537 | 3.0569e-08 | 9.1725e-09 | 0.015414 | 0.015414 | 0.015414 | 0.97754 | -0.15764 | 0.97753 | -0.15766 | 5.7088
28 | 0.0068185 | 0.001708 | -0.0068162 | -0.0017076 | 2.2382e-06 | 4.4356e-07 | 0.010379 | 0.010379 | 0.010379 | 0.97753 | -0.15766 | 0.9772 | -0.16004 | 3.8441
29 | 0.0057515 | 0.0014407 | -0.0057511 | -0.0014407 | 4.2844e-07 | 5.2642e-08 | 0.0087577 | 0.0087577 | 0.0087577 | 0.9772 | -0.16004 | 0.97713 | -0.16058 | 3.2436
30 | 0.0039232 | 0.00098257 | -0.0039229 | -0.00098262 | 3.0299e-07 | -5.386e-08 | 0.0059742 | 0.0059743 | 0.0059743 | 0.97713 | -0.16058 | 0.97705 | -0.16113 | 2.2127
31 | -0.070728 | -0.017775 | 0.070816 | 0.017809 | 8.8012e-05 | 3.3694e-05 | 0.10693 | 0.10693 | 0.10693 | 0.98438 | -0.10896 | 0.98564 | -0.10003 | 39.6044
32 | 0.017681 | 0.0044344 | -0.017676 | -0.0044324 | 5.474e-06 | 1.9535e-06 | 0.026911 | 0.026911 | 0.026911 | 0.9777 | -0.15645 | 0.97739 | -0.15869 | 9.9672
33 | -0.072069 | -0.018123 | 0.07207 | 0.018123 | 3.537e-07 | 1.3543e-07 | 0.10882 | 0.10882 | 0.10882 | 0.98564 | -0.10003 | 0.98564 | -0.099992 | 40.3053
34 | -0.073716 | -0.018536 | 0.073794 | 0.018565 | 7.7328e-05 | 2.9614e-05 | 0.11131 | 0.11131 | 0.11131 | 0.98564 | -0.099992 | 0.98671 | -0.092472 | 41.2261
35 | -0.074936 | -0.018851 | 0.074983 | 0.01887 | 4.7588e-05 | 1.8227e-05 | 0.11303 | 0.11303 | 0.11303 | 0.98671 | -0.092472 | 0.98736 | -0.087922 | 41.864
36 | -0.07639 | -0.019222 | 0.076466 | 0.019251 | 7.5491e-05 | 2.8918e-05 | 0.11515 | 0.11515 | 0.11515 | 0.98736 | -0.087922 | 0.98836 | -0.080848 | 42.6491
37 | -0.077806 | -0.019587 | 0.077995 | 0.019659 | 0.00018886 | 7.2354e-05 | 0.11717 | 0.11717 | 0.11717 | 0.98836 | -0.080848 | 0.99084 | -0.063513 | 43.3964
38 | 0.0027166 | 0.00068029 | -0.0027161 | -0.00068072 | 5.3963e-07 | -4.2507e-07 | 0.0041372 | 0.0041374 | 0.0041374 | 0.97705 | -0.16113 | 0.97685 | -0.16257 | 1.5324
39 | -0.079959 | -0.020152 | 0.080001 | 0.020168 | 4.1624e-05 | 1.595e-05 | 0.12012 | 0.12012 | 0.12012 | 0.99084 | -0.063513 | 0.99137 | -0.059796 | 44.489
40 | -0.072834 | -0.018292 | 0.072836 | 0.018292 | 1.9928e-06 | 7.5255e-07 | 0.1091 | 0.1091 | 0.1091 | 0.99353 | -0.045166 | 0.99356 | -0.044969 | 20.2032
41 | 0.069927 | 0.017563 | -0.069871 | -0.017542 | 5.6006e-05 | 2.1118e-05 | 0.10474 | 0.10474 | 0.10474 | 0.99353 | -0.045166 | 0.99271 | -0.050931 | 19.3969
42 | 0.064092 | 0.016094 | -0.064091 | -0.016094 | 6.6094e-07 | 2.4827e-07 | 0.096081 | 0.096081 | 0.096081 | 0.99271 | -0.050931 | 0.9927 | -0.051005 | 17.7928
43 | 0.0057791 | 0.001448 | -0.0057784 | -0.001448 | 6.303e-07 | 6.8407e-08 | 0.0086624 | 0.0086624 | 0.0086624 | 0.99271 | -0.050931 | 0.9926 | -0.051719 | 3.2083
44 | 0.063213 | 0.015874 | -0.06316 | -0.015853 | 5.3584e-05 | 2.0115e-05 | 0.094765 | 0.094765 | 0.094765 | 0.9927 | -0.051005 | 0.99183 | -0.05711 | 17.5491
45 | 0.0041931 | 0.0010506 | -0.0041925 | -0.0010507 | 6.2606e-07 | -8.737e-08 | 0.0062858 | 0.0062859 | 0.0062859 | 0.9926 | -0.051719 | 0.99244 | -0.052798 | 2.3281
46 | 0.062236 | 0.015622 | -0.062227 | -0.015619 | 9.2528e-06 | 3.471e-06 | 0.09338 | 0.09338 | 0.09338 | 0.99183 | -0.05711 | 0.99168 | -0.05818 | 17.2926
47 | 0.061488 | 0.015433 | -0.061481 | -0.015431 | 6.7284e-06 | 2.5225e-06 | 0.092271 | 0.092271 | 0.092271 | 0.99168 | -0.05818 | 0.99157 | -0.058969 | 17.0872
48 | 0.060558 | 0.015199 | -0.060543 | -0.015194 | 1.5299e-05 | 5.7312e-06 | 0.090885 | 0.090885 | 0.090885 | 0.99157 | -0.058969 | 0.99131 | -0.060789 | 16.8306
49 | 0.059619 | 0.014962 | -0.059604 | -0.014957 | 1.4781e-05 | 5.5327e-06 | 0.089499 | 0.089499 | 0.089499 | 0.99131 | -0.060789 | 0.99105 | -0.062575 | 16.5738
50 | 0.041243 | 0.010348 | -0.041198 | -0.010332 | 4.4809e-05 | 1.6275e-05 | 0.062007 | 0.062007 | 0.062007 | 0.9898 | -0.071404 | 0.98869 | -0.079242 | 11.4828
51 | -0.041873 | -0.010506 | 0.041902 | 0.010517 | 2.9068e-05 | 1.0575e-05 | 0.062954 | 0.062954 | 0.062954 | 0.9898 | -0.071404 | 0.99051 | -0.066404 | 11.6582
52 | 0.038846 | 0.0097421 | -0.038842 | -0.0097407 | 4.0032e-06 | 1.4434e-06 | 0.058466 | 0.058466 | 0.058466 | 0.98869 | -0.079242 | 0.98859 | -0.079986 | 10.8271
53 | 0.016754 | 0.0041987 | -0.016747 | -0.0041964 | 6.5736e-06 | 2.3143e-06 | 0.025169 | 0.025169 | 0.025169 | 0.99051 | -0.066404 | 0.99011 | -0.069239 | 9.3219
54 | -0.058656 | -0.014715 | 0.058688 | 0.014727 | 3.1165e-05 | 1.1655e-05 | 0.088123 | 0.088123 | 0.088123 | 0.99051 | -0.066404 | 0.99105 | -0.062575 | 16.3191
55 | 0.035184 | 0.0088241 | -0.035137 | -0.0088072 | 4.7766e-05 | 1.6974e-05 | 0.052962 | 0.052962 | 0.052962 | 0.98859 | -0.079986 | 0.9872 | -0.089791 | 9.8078
56 | 0.01495 | 0.0037459 | -0.01494 | -0.0037424 | 1.0172e-05 | 3.4972e-06 | 0.022468 | 0.022468 | 0.022468 | 0.99011 | -0.069239 | 0.98942 | -0.074159 | 8.3215
57 | 0.030442 | 0.0076306 | -0.030415 | -0.0076212 | 2.7103e-05 | 9.3703e-06 | 0.045886 | 0.045886 | 0.045886 | 0.9872 | -0.089791 | 0.9863 | -0.096225 | 8.4975
58 | 0.01494 | 0.0037424 | -0.014935 | -0.0037406 | 5.2971e-06 | 1.8215e-06 | 0.022468 | 0.022468 | 0.022468 | 0.98942 | -0.074159 | 0.98905 | -0.076724 | 8.3215
59 | 0.013485 | 0.0033803 | -0.013476 | -0.0033772 | 9.1353e-06 | 3.0625e-06 | 0.020345 | 0.020345 | 0.020345 | 0.9863 | -0.096225 | 0.98561 | -0.10112 | 7.5352
60 | 0.01693 | 0.0042409 | -0.016885 | -0.0042293 | 4.4741e-05 | 1.1613e-05 | 0.025542 | 0.025544 | 0.025544 | 0.9863 | -0.096225 | 0.98361 | -0.11536 | 4.7303
61 | 0.012746 | 0.003192 | -0.012743 | -0.0031911 | 2.7802e-06 | 9.1384e-07 | 0.019175 | 0.019175 | 0.019175 | 0.98905 | -0.076724 | 0.98883 | -0.078302 | 7.1018
62 | 0.011636 | 0.0029137 | -0.011636 | -0.0029135 | 5.3335e-07 | 1.6937e-07 | 0.01751 | 0.01751 | 0.01751 | 0.98883 | -0.078302 | 0.98878 | -0.078634 | 6.485
63 | 0.0080876 | 0.0020243 | -0.0080861 | -0.0020239 | 1.4682e-06 | 3.6095e-07 | 0.01217 | 0.01217 | 0.01217 | 0.98878 | -0.078634 | 0.9886 | -0.079948 | 4.5074
64 | -0.0013755 | -0.00034474 | 0.0013756 | 0.00034445 | 6.6775e-08 | -2.8991e-07 | 0.0020778 | 0.0020777 | 0.0020778 | 0.98508 | -0.10485 | 0.98513 | -0.1045 | 0.76955
65 | -0.0054872 | -0.0013749 | 0.0054878 | 0.001375 | 5.3875e-07 | 4.7172e-08 | 0.0082882 | 0.0082881 | 0.0082882 | 0.98513 | -0.1045 | 0.98523 | -0.10379 | 3.0697
66 | -0.0092258 | -0.0023118 | 0.0092271 | 0.0023122 | 1.3011e-06 | 3.6364e-07 | 0.013934 | 0.013934 | 0.013934 | 0.98523 | -0.10379 | 0.98537 | -0.10277 | 5.1607
67 | -0.012459 | -0.0031222 | 0.012462 | 0.0031232 | 2.8535e-06 | 9.3291e-07 | 0.018815 | 0.018815 | 0.018815 | 0.98537 | -0.10277 | 0.98561 | -0.10112 | 6.9684
68 | 0.015398 | 0.0038569 | -0.015368 | -0.0038463 | 3.0452e-05 | 1.0573e-05 | 0.023294 | 0.023294 | 0.023294 | 0.98361 | -0.11536 | 0.9816 | -0.12969 | 8.6276
69 | 0.00024702 | 6.1679e-05 | -0.00024702 | -6.1908e-05 | 1.5783e-09 | -2.2933e-07 | 0.00037361 | 0.00037369 | 0.00037369 | 0.98361 | -0.11536 | 0.9836 | -0.11541 | 0.1384
70 | 0.0035379 | 0.00088502 | -0.0035375 | -0.00088514 | 3.8662e-07 | -1.2362e-07 | 0.0053625 | 0.0053626 | 0.0053626 | 0.9816 | -0.12969 | 0.98149 | -0.13048 | 1.9862
71 | 0.01183 | 0.0029613 | -0.011807 | -0.0029538 | 2.3252e-05 | 7.4812e-06 | 0.017932 | 0.017932 | 0.017932 | 0.9816 | -0.12969 | 0.97961 | -0.14394 | 6.6416
72 | 0.00763 | 0.0019096 | -0.0076298 | -0.0019096 | 2.4377e-07 | 5.5775e-08 | 0.011484 | 0.011484 | 0.011484 | 0.9886 | -0.079948 | 0.98857 | -0.08018 | 4.2532
73 | 0.0071715 | 0.0017947 | -0.0071706 | -0.0017945 | 8.3865e-07 | 1.7467e-07 | 0.010794 | 0.010794 | 0.010794 | 0.98857 | -0.08018 | 0.98845 | -0.081027 | 3.9977
74 | 0.0064453 | 0.0016128 | -0.0064435 | -0.0016125 | 1.8194e-06 | 3.0284e-07 | 0.0097019 | 0.0097021 | 0.0097021 | 0.98845 | -0.081027 | 0.98816 | -0.083073 | 3.5934
75 | 0.0059353 | 0.0014851 | -0.0059342 | -0.001485 | 1.0717e-06 | 1.3676e-07 | 0.0089367 | 0.0089368 | 0.0089368 | 0.98816 | -0.083073 | 0.98798 | -0.084381 | 3.3099
76 | 0.0049971 | 0.0012501 | -0.0049966 | -0.0012501 | 5.5661e-07 | 1.2411e-08 | 0.0075255 | 0.0075256 | 0.0075256 | 0.98798 | -0.084381 | 0.98786 | -0.085189 | 2.7873
77 | 0.0046995 | 0.0011756 | -0.0046983 | -0.0011757 | 1.2739e-06 | -3.1572e-08 | 0.0070781 | 0.0070783 | 0.0070783 | 0.98786 | -0.085189 | 0.98759 | -0.087154 | 2.6216
78 | 0.0016454 | 0.00041125 | -0.0016453 | -0.00041178 | 1.8038e-07 | -5.3247e-07 | 0.0024788 | 0.002479 | 0.002479 | 0.98759 | -0.087154 | 0.98747 | -0.087949 | 0.91816
79 | 0.00093798 | 0.00023439 | -0.00093791 | -0.00023506 | 6.7884e-08 | -6.7089e-07 | 0.001413 | 0.0014133 | 0.0014133 | 0.98759 | -0.087154 | 0.98751 | -0.087678 | 0.52344
80 | 0.00082263 | 0.00020561 | -0.00082259 | -0.00020616 | 4.2036e-08 | -5.4472e-07 | 0.0012394 | 0.0012396 | 0.0012396 | 0.98747 | -0.087949 | 0.98742 | -0.088319 | 0.45912
81 | -0.00030325 | -7.6002e-05 | 0.00030327 | 7.4531e-05 | 1.6068e-08 | -1.4706e-06 | 0.0004647 | 0.00046417 | 0.0004647 | 0.97103 | -0.20583 | 0.97109 | -0.20544 | 0.17211
82 | -0.0032735 | -0.00081849 | 0.0032747 | 0.00081801 | 1.1953e-06 | -4.8284e-07 | 0.0050153 | 0.005015 | 0.0050153 | 0.97109 | -0.20544 | 0.97145 | -0.20279 | 1.8575
83 | 0.0029702 | 0.00074396 | -0.0029697 | -0.00074427 | 5.3151e-07 | -3.0422e-07 | 0.0045511 | 0.0045513 | 0.0045513 | 0.97109 | -0.20544 | 0.97091 | -0.20673 | 1.6857
84 | -0.0039536 | -0.00098816 | 0.0039567 | 0.00098767 | 3.1336e-06 | -4.9223e-07 | 0.0060549 | 0.0060543 | 0.0060549 | 0.97145 | -0.20279 | 0.97225 | -0.19702 | 2.2425
85 | 0.0073583 | 0.0018395 | -0.0073378 | -0.0018349 | 2.051e-05 | 4.6358e-06 | 0.011219 | 0.01122 | 0.01122 | 0.97582 | -0.17122 | 0.97301 | -0.19148 | 4.1556
86 | -0.0073583 | -0.0018395 | 0.0073648 | 0.001841 | 6.4778e-06 | 1.4601e-06 | 0.011219 | 0.011219 | 0.011219 | 0.97582 | -0.17122 | 0.97671 | -0.16483 | 4.1552
87 | 0.0073378 | 0.0018349 | -0.0073345 | -0.0018341 | 3.3337e-06 | 7.5536e-07 | 0.01122 | 0.01122 | 0.01122 | 0.97301 | -0.19148 | 0.97256 | -0.19477 | 4.1557
88 | -0.0075546 | -0.0018886 | 0.0075565 | 0.001889 | 1.9383e-06 | 4.5187e-07 | 0.011508 | 0.011508 | 0.011508 | 0.97671 | -0.16483 | 0.97696 | -0.16297 | 4.2621
89 | -0.0071043 | -0.0017765 | 0.0071065 | 0.001777 | 2.2055e-06 | 4.7729e-07 | 0.010872 | 0.010872 | 0.010872 | 0.97225 | -0.19702 | 0.97256 | -0.19477 | 4.0265
90 | 0.00058729 | 0.00014646 | -0.00058729 | -0.00014652 | 2.2387e-09 | -5.5424e-08 | 0.00089382 | 0.00089384 | 0.00089384 | 0.97743 | -0.15961 | 0.97743 | -0.15964 | 0.33105
91 | -0.00091221 | -0.0002279 | 0.00091223 | 0.00022778 | 1.22e-08 | -1.2243e-07 | 0.0013885 | 0.0013884 | 0.0013885 | 0.97743 | -0.15961 | 0.97744 | -0.15951 | 0.51425
92 | 0.00040925 | 0.0001019 | -0.00040925 | -0.00010201 | 2.2641e-09 | -1.1637e-07 | 0.00062279 | 0.00062283 | 0.00062283 | 0.97743 | -0.15964 | 0.97742 | -0.15968 | 0.23068
93 | -0.00091223 | -0.00022778 | 0.00091224 | 0.00022764 | 1.3725e-08 | -1.3774e-07 | 0.0013884 | 0.0013884 | 0.0013884 | 0.97744 | -0.15951 | 0.97746 | -0.1594 | 0.51423
94 | 0.000309 | 7.689e-05 | -0.00030899 | -7.7441e-05 | 6.0886e-09 | -5.5052e-07 | 0.00047022 | 0.00047041 | 0.00047041 | 0.97742 | -0.15968 | 0.9774 | -0.15982 | 0.17423
95 | 0.0089794 | 0.0022457 | -0.0089773 | -0.0022451 | 2.0491e-06 | 5.6783e-07 | 0.013668 | 0.013668 | 0.013668 | 0.97746 | -0.1594 | 0.97723 | -0.16106 | 5.0622
96 | -0.0098916 | -0.0024733 | 0.0099094 | 0.0024786 | 1.785e-05 | 5.2808e-06 | 0.015056 | 0.015056 | 0.015056 | 0.97746 | -0.1594 | 0.97928 | -0.14632 | 5.5764
97 | 0.0081947 | 0.002049 | -0.0081926 | -0.0020484 | 2.1552e-06 | 5.5101e-07 | 0.012476 | 0.012476 | 0.012476 | 0.97723 | -0.16106 | 0.97696 | -0.16297 | 4.6209
98 | -0.0099094 | -0.0024786 | 0.0099127 | 0.0024796 | 3.2542e-06 | 9.6207e-07 | 0.015056 | 0.015056 | 0.015056 | 0.97928 | -0.14632 | 0.97961 | -0.14394 | 5.5762
99 | -0.0011167 | -0.00027969 | 0.0011168 | 0.00027945 | 3.6622e-08 | -2.4271e-07 | 0.0016963 | 0.0016962 | 0.0016963 | 0.97958 | -0.14418 | 0.97961 | -0.14394 | 0.62826
100 | 0.00063726 | 0.00015953 | -0.00063725 | -0.00015971 | 8.7818e-09 | -1.857e-07 | 0.00096796 | 0.00096803 | 0.00096803 | 0.97958 | -0.14418 | 0.97956 | -0.14428 | 0.35853
101 | 0.0034477 | 0.00086263 | -0.0034475 | -0.00086268 | 1.4451e-07 | -5.1562e-08 | 0.0052264 | 0.0052265 | 0.0052265 | 0.98149 | -0.13048 | 0.98145 | -0.13078 | 1.9357
102 | 0.00060776 | 0.00015167 | -0.00060775 | -0.00015189 | 9.2812e-09 | -2.1789e-07 | 0.00092121 | 0.00092129 | 0.00092129 | 0.98145 | -0.13078 | 0.98143 | -0.1309 | 0.34122
103 | 0.0028398 | 0.00071101 | -0.0028394 | -0.0007113 | 4.0811e-07 | -2.8885e-07 | 0.0043053 | 0.0043054 | 0.0043054 | 0.98145 | -0.13078 | 0.9813 | -0.13182 | 1.5946
104 | 0.0025315 | 0.00063413 | -0.0025312 | -0.00063438 | 2.5617e-07 | -2.5342e-07 | 0.0038385 | 0.0038387 | 0.0038387 | 0.9813 | -0.13182 | 0.9812 | -0.13256 | 1.4217
105 | 0.00047207 | 0.00011788 | -0.00047206 | -0.000118 | 3.1259e-09 | -1.2242e-07 | 0.00071558 | 0.00071562 | 0.00071562 | 0.98143 | -0.1309 | 0.98143 | -0.13094 | 0.26505
106 | 0.00029835 | 7.4468e-05 | -0.00029835 | -7.4773e-05 | 3.092e-09 | -3.0489e-07 | 0.00045224 | 0.00045235 | 0.00045235 | 0.98143 | -0.13094 | 0.98142 | -0.13102 | 0.16754
107 | -0.0017248 | -0.00043228 | 0.0017248 | 0.00043219 | 3.2783e-08 | -8.9478e-08 | 0.0025824 | 0.0025824 | 0.0025824 | 0.99385 | -0.043092 | 0.99387 | -0.042955 | 0.95645
108 | -0.0046791 | -0.0011726 | 0.0046797 | 0.0011726 | 5.159e-07 | -1.9906e-08 | 0.0070056 | 0.0070055 | 0.0070056 | 0.99387 | -0.042955 | 0.99398 | -0.042158 | 2.5947
109 | 0.016948 | 0.0042501 | -0.016946 | -0.0042494 | 1.9006e-06 | 6.7366e-07 | 0.025804 | 0.025804 | 0.025804 | 0.97739 | -0.15869 | 0.97728 | -0.1595 | 9.5569
110 | 0.016453 | 0.0041258 | -0.016452 | -0.0041254 | 1.3231e-06 | 4.6657e-07 | 0.025053 | 0.025053 | 0.025053 | 0.97728 | -0.1595 | 0.97719 | -0.16008 | 9.2788
111 | 0.015959 | 0.0040017 | -0.015957 | -0.0040013 | 1.2432e-06 | 4.3588e-07 | 0.024301 | 0.024301 | 0.024301 | 0.97719 | -0.16008 | 0.97712 | -0.16064 | 9.0006
112 | 0.015464 | 0.0038776 | -0.015458 | -0.0038756 | 5.7372e-06 | 1.9991e-06 | 0.02355 | 0.02355 | 0.02355 | 0.97712 | -0.16064 | 0.97674 | -0.16332 | 8.7223
113 | 0.014626 | 0.003667 | -0.014617 | -0.003664 | 8.7315e-06 | 3.0057e-06 | 0.022282 | 0.022282 | 0.022282 | 0.97674 | -0.16332 | 0.97614 | -0.16763 | 8.2526
114 | 0.013274 | 0.0033275 | -0.013269 | -0.0033256 | 5.6788e-06 | 1.9065e-06 | 0.020236 | 0.020236 | 0.020236 | 0.97614 | -0.16763 | 0.97571 | -0.17072 | 7.4947
115 | 0.013269 | 0.0033256 | -0.013266 | -0.0033248 | 2.2499e-06 | 7.5538e-07 | 0.020236 | 0.020236 | 0.020236 | 0.97571 | -0.17072 | 0.97554 | -0.17194 | 7.4947
116 | 0.011849 | 0.0029695 | -0.011847 | -0.002969 | 1.6793e-06 | 5.4302e-07 | 0.018073 | 0.018073 | 0.018073 | 0.97554 | -0.17194 | 0.9754 | -0.17297 | 6.6938
117 | 0.0089599 | 0.0022454 | -0.0089595 | -0.0022453 | 3.3499e-07 | 9.2979e-08 | 0.013669 | 0.013669 | 0.013669 | 0.9754 | -0.17297 | 0.97536 | -0.17324 | 5.0625
118 | 0.0071383 | 0.0017888 | -0.0071352 | -0.0017882 | 3.0902e-06 | 6.6761e-07 | 0.01089 | 0.01089 | 0.01089 | 0.97536 | -0.17324 | 0.97492 | -0.17636 | 4.0335
119 | 0.004374 | 0.0010961 | -0.0043737 | -0.0010962 | 2.4327e-07 | -1.5505e-08 | 0.0066759 | 0.006676 | 0.006676 | 0.97492 | -0.17636 | 0.97487 | -0.17677 | 2.4726
120 | -0.007979 | -0.0019994 | 0.0079807 | 0.0019998 | 1.6471e-06 | 3.935e-07 | 0.011943 | 0.011943 | 0.011943 | 0.99414 | -0.040988 | 0.99436 | -0.039496 | 4.4232
121 | 0.0072407 | 0.0018144 | -0.0072402 | -0.0018143 | 4.6342e-07 | 9.6259e-08 | 0.010838 | 0.010838 | 0.010838 | 0.99414 | -0.040988 | 0.99408 | -0.04145 | 4.0139
122 | -0.010021 | -0.0025112 | 0.010023 | 0.0025118 | 2.0998e-06 | 6.1348e-07 | 0.014996 | 0.014996 | 0.014996 | 0.99436 | -0.039496 | 0.99457 | -0.037983 | 5.5542
123 | 0.0061977 | 0.001553 | -0.0061971 | -0.0015529 | 6.0727e-07 | 8.6985e-08 | 0.0092771 | 0.0092772 | 0.0092772 | 0.99408 | -0.04145 | 0.99398 | -0.042158 | 3.436

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22181 | 0.055731

## res_load
| p_mw | q_mvar
0 | 0.0078923 | 0.001978
1 | 0.00052147 | 0.00013069
2 | 0.0032511 | 0.00081481
3 | 0.028327 | 0.0070995
4 | 0.0037634 | 0.00094319
5 | 0.00078212 | 0.00019602
6 | 0.0049784 | 0.0012477
7 | 0.0006843 | 0.0001715
8 | 0.0031328 | 0.00078515
9 | 0.01108 | 0.002777
10 | 0.001484 | 0.00037194
11 | 0.01051 | 0.002634
12 | 0.0044408 | 0.001113
13 | 0.0014398 | 0.00036085
14 | 0.0026468 | 0.00066335
15 | 0.00052676 | 0.00013202
16 | 0.0033076 | 0.00082897
17 | 0.0010647 | 0.00026685
18 | 0.0018278 | 0.0004581
19 | 0.0038146 | 0.00095603
20 | 0.0034687 | 0.00086933
21 | 0.0012536 | 0.00031418
22 | 0.0016468 | 0.00041272
23 | 0.0011421 | 0.00028623
24 | 0.0014067 | 0.00035254
25 | 0.0013403 | 0.0003359
26 | 0.0012063 | 0.00030233
27 | 0.0027161 | 0.00068072
28 | 0.0019644 | 0.00049233
29 | 0.00074037 | 0.00018556
30 | 0.0018931 | 0.00047445
31 | 0.0029072 | 0.0007286
32 | 0.0032973 | 0.00082638
33 | 0.00087792 | 0.00022003
34 | 0.0015854 | 0.00039733
35 | 0.00092351 | 0.00023145
36 | 0.0041925 | 0.0010507
37 | 0.00073918 | 0.00018526
38 | 0.00092312 | 0.00023136
39 | 0.00092383 | 0.00023153
40 | 0.00063028 | 0.00015796
41 | 0.0023526 | 0.00058962
42 | 0.0036571 | 0.00091655
43 | 0.0017973 | 0.00045045
44 | 0.00091646 | 0.00022969
45 | 0.0046946 | 0.0011766
46 | 0.002189 | 0.00054861
47 | 0.0011067 | 0.00027737
48 | 0.0035481 | 0.00088925
49 | 0.0013755 | 0.00034474
50 | 0.0041116 | 0.0010305
51 | 0.003738 | 0.00093684
52 | 0.0032322 | 0.00081007
53 | 0.0010136 | 0.00025403
54 | 0.00124 | 0.00031078
55 | 0.00024702 | 6.1908e-05
56 | 0.0004561 | 0.00011431
57 | 0.00045829 | 0.00011486
58 | 0.0007253 | 0.00018178
59 | 0.00050824 | 0.00012738
60 | 0.00093704 | 0.00023485
61 | 0.00029706 | 7.4449e-05
62 | 0.0021148 | 0.00053003
63 | 0.00082263 | 0.00020617
64 | 0.00093791 | 0.00023506
65 | 0.00082259 | 0.00020616
66 | 0.00030325 | 7.6002e-05
67 | 0.00067891 | 0.00017015
68 | 0.0029697 | 0.00074427
69 | 0.00018975 | 4.7557e-05
70 | 0.0031476 | 0.00078886
71 | 0.000228 | 5.7141e-05
72 | 0.00032492 | 8.1433e-05
73 | 0.00017804 | 4.4622e-05
74 | 0.00010025 | 2.5125e-05
75 | 0.00030899 | 7.7441e-05
76 | 0.0007826 | 0.00019614
77 | 0.00047947 | 0.00012017
78 | 0.00077725 | 0.0001948
79 | 0.00063725 | 0.00015971
80 | 8.9837e-05 | 2.2515e-05
81 | 0.0003079 | 7.7168e-05
82 | 0.0025312 | 0.00063438
83 | 0.00013568 | 3.4005e-05
84 | 0.00017371 | 4.3537e-05
85 | 0.00029835 | 7.4773e-05
86 | 0.00063605 | 0.00015941
87 | 0.0017248 | 0.00043228
88 | 0.0029543 | 0.00074042
89 | 0.00072755 | 0.00018234
90 | 0.00049322 | 0.00012361
91 | 0.00049337 | 0.00012365
92 | 0.00049337 | 0.00012365
93 | 0.00083253 | 0.00020865
94 | 0.0013425 | 0.00033647
95 | 0.0014177 | 0.00035531
96 | 0.0028872 | 0.0007236
97 | 0.0018212 | 0.00045645
98 | 0.0027612 | 0.00069203
99 | 0.0043737 | 0.0010962
100 | 0.00073837 | 0.00018505
101 | 0.0020406 | 0.00051142
102 | 0.0010425 | 0.00026127
103 | 0.00058159 | 0.00014576
104 | 0.0015175 | 0.00038031

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1