## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1403-22_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1403-22_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1403-22_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1403-22_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1403-22_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1403-22_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1403-22_0_4_node_57 | 0.4 | n |  | TRUE
7 | bus_LV_1403-22_0_4_node_56 | 0.4 | n |  | TRUE
8 | bus_LV_1403-22_0_4_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_1403-22_0_4_node_59 | 0.4 | n |  | TRUE
10 | bus_LV_1403-22_0_4_node_54 | 0.4 | n |  | TRUE
11 | bus_LV_1403-22_0_4_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1403-22_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1403-22_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1403-22_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1403-22_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1403-22_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1403-22_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1403-22_0_4_node_75 | 0.4 | n |  | TRUE
19 | bus_LV_1403-22_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1403-22_0_4_node_73 | 0.4 | n |  | TRUE
21 | bus_LV_1403-22_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1403-22_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1403-22_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1403-22_0_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1403-22_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1403-22_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_1403-22_0_4_node_70 | 0.4 | n |  | TRUE
28 | bus_LV_1403-22_0_4_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_1403-22_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1403-22_0_4_node_64 | 0.4 | n |  | TRUE
31 | bus_LV_1403-22_0_4_node_68 | 0.4 | n |  | TRUE
32 | bus_LV_1403-22_0_4_node_107 | 0.4 | n |  | TRUE
33 | bus_LV_1403-22_0_4_node_60 | 0.4 | n |  | TRUE
34 | bus_LV_1403-22_0_4_node_66 | 0.4 | n |  | TRUE
35 | bus_LV_1403-22_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1403-22_0_4_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_1403-22_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1403-22_0_4_node_58 | 0.4 | n |  | TRUE
39 | bus_LV_1403-22_0_4_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_1403-22_0_4_node_53 | 0.4 | n |  | TRUE
41 | bus_LV_1403-22_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1403-22_0_4_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1403-22_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1403-22_0_4_node_101 | 0.4 | n |  | TRUE
45 | bus_LV_1403-22_0_4_node_100 | 0.4 | n |  | TRUE
46 | bus_LV_1403-22_0_4_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_1403-22_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1403-22_0_4_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1403-22_0_4_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_1403-22_0_4_node_99 | 0.4 | n |  | TRUE
51 | bus_LV_1403-22_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_1403-22_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_1403-22_0_4_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_1403-22_0_4_node_108 | 0.4 | n |  | TRUE
55 | bus_LV_1403-22_0_4_node_109 | 0.4 | n |  | TRUE
56 | bus_LV_1403-22_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_1403-22_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_1403-22_0_4_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_1403-22_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_1403-22_0_4_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_1403-22_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_1403-22_0_4_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_1403-22_0_4_node_82 | 0.4 | n |  | TRUE
64 | bus_LV_1403-22_0_4_node_42 | 0.4 | n |  | TRUE
65 | bus_LV_1403-22_0_4_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_1403-22_0_4_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_1403-22_0_4_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_1403-22_0_4_node_105 | 0.4 | n |  | TRUE
69 | bus_LV_1403-22_0_4_node_106 | 0.4 | n |  | TRUE
70 | bus_LV_1403-22_0_4_node_83 | 0.4 | n |  | TRUE
71 | bus_LV_1403-22_0_4_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_1403-22_0_4_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_1403-22_0_4_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1403-22_0_4_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_1403-22_0_4_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_1403-22_0_4_node_61 | 0.4 | n |  | TRUE
77 | bus_LV_1403-22_0_4_node_63 | 0.4 | n |  | TRUE
78 | bus_LV_1403-22_0_4_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_1403-22_0_4_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_1403-22_0_4_node_69 | 0.4 | n |  | TRUE
81 | bus_LV_1403-22_0_4_node_104 | 0.4 | n |  | TRUE
82 | bus_LV_1403-22_0_4_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_1403-22_0_4_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_1403-22_0_4_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_1403-22_0_4_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_1403-22_0_4_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_1403-22_0_4_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_1403-22_0_4_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_1403-22_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_1403-22_0_4_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_1403-22_0_4_node_91 | 0.4 | n |  | TRUE
92 | bus_LV_1403-22_0_4_node_89 | 0.4 | n |  | TRUE
93 | bus_LV_1403-22_0_4_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_1403-22_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_1403-22_0_4_node_95 | 0.4 | n |  | TRUE
96 | bus_LV_1403-22_0_4_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_1403-22_0_4_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_1403-22_0_4_node_92 | 0.4 | n |  | TRUE
99 | bus_LV_1403-22_0_4_node_98 | 0.4 | n |  | TRUE
100 | bus_LV_1403-22_0_4_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_1403-22_0_4_node_97 | 0.4 | n |  | TRUE
102 | bus_LV_1403-22_0_4_node_93 | 0.4 | n |  | TRUE
103 | bus_LV_1403-22_0_4_node_94 | 0.4 | n |  | TRUE
104 | bus_LV_1403-22_0_4_node_102 | 0.4 | n |  | TRUE
105 | bus_LV_1403-22_0_4_node_103 | 0.4 | n |  | TRUE
106 | bus_MV_138_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1403-22_0_4_load_0 | 0 | 0.0030375 | 0.00076128 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1403-22_0_4_load_1 | 1 | 0.0018018 | 0.00045157 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1403-22_0_4_load_2 | 2 | 0.0022567 | 0.00056559 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1403-22_0_4_load_5 | 5 | 0.0039548 | 0.00099117 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1403-22_0_4_load_57 | 6 | 0.00062814 | 0.00015743 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1403-22_0_4_load_56 | 7 | 0.0014758 | 0.00036988 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1403-22_0_4_load_59 | 9 | 0.0058922 | 0.0014767 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1403-22_0_4_load_6 | 12 | 0.0080913 | 0.0020279 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1403-22_0_4_load_8 | 14 | 0.015177 | 0.0038038 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1403-22_0_4_load_9 | 15 | 0.0089139 | 0.002234 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1403-22_0_4_load_11 | 17 | 0.022415 | 0.0056176 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1403-22_0_4_load_75 | 18 | 0.0032044 | 0.00080311 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1403-22_0_4_load_18 | 22 | 0.0062275 | 0.0015608 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1403-22_0_4_load_14 | 25 | 0.0031972 | 0.00080128 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1403-22_0_4_load_24 | 26 | 0.0053595 | 0.0013432 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1403-22_0_4_load_70 | 27 | 0.0074379 | 0.0018641 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1403-22_0_4_load_13 | 28 | 0.0031148 | 0.00078063 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1403-22_0_4_load_64 | 30 | 0.0059564 | 0.0014928 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1403-22_0_4_load_68 | 31 | 0.0034654 | 0.00086851 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1403-22_0_4_load_107 | 32 | 0.0076386 | 0.0019144 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1403-22_0_4_load_66 | 34 | 0.0013195 | 0.0003307 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1403-22_0_4_load_22 | 35 | 0.0029261 | 0.00073336 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1403-22_0_4_load_55 | 36 | 0.0023449 | 0.00058768 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1403-22_0_4_load_23 | 37 | 0.0030356 | 0.00076079 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1403-22_0_4_load_53 | 40 | 0.001865 | 0.00046741 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1403-22_0_4_load_26 | 41 | 0.001587 | 0.00039774 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1403-22_0_4_load_27 | 42 | 0.00045394 | 0.00011377 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1403-22_0_4_load_28 | 43 | 0.0026659 | 0.00066813 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1403-22_0_4_load_101 | 44 | 0.0014566 | 0.00036506 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1403-22_0_4_load_29 | 46 | 0.00091902 | 0.00023033 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1403-22_0_4_load_31 | 48 | 0.00080997 | 0.000203 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1403-22_0_4_load_99 | 50 | 0.012837 | 0.0032171 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1403-22_0_4_load_33 | 52 | 0.0006203 | 0.00015546 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1403-22_0_4_load_32 | 53 | 0.0013231 | 0.0003316 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1403-22_0_4_load_108 | 54 | 0.00099447 | 0.00024924 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1403-22_0_4_load_109 | 55 | 0.0008268 | 0.00020721 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1403-22_0_4_load_36 | 56 | 0.0013186 | 0.00033046 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1403-22_0_4_load_37 | 57 | 0.0014682 | 0.00036796 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1403-22_0_4_load_39 | 60 | 0.0011953 | 0.00029956 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1403-22_0_4_load_82 | 63 | 0.0010435 | 0.00026152 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1403-22_0_4_load_42 | 64 | 0.00058016 | 0.0001454 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1403-22_0_4_load_41 | 65 | 0.0022836 | 0.00057233 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1403-22_0_4_load_47 | 66 | 0.0016056 | 0.00040241 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1403-22_0_4_load_48 | 67 | 0.00075348 | 0.00018884 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1403-22_0_4_load_105 | 68 | 0.0006706 | 0.00016807 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1403-22_0_4_load_106 | 69 | 0.0026778 | 0.00067113 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1403-22_0_4_load_83 | 70 | 0.0007819 | 0.00019596 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1403-22_0_4_load_49 | 71 | 0.0012967 | 0.00032498 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1403-22_0_4_load_50 | 72 | 0.00080308 | 0.00020127 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1403-22_0_4_load_51 | 73 | 0.0035368 | 0.0008864 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1403-22_0_4_load_52 | 74 | 0.0010867 | 0.00027235 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1403-22_0_4_load_62 | 75 | 0.0029272 | 0.00073363 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1403-22_0_4_load_61 | 76 | 0.0031671 | 0.00079375 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1403-22_0_4_load_63 | 77 | 0.0031723 | 0.00079505 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1403-22_0_4_load_65 | 78 | 0.003305 | 0.0008283 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1403-22_0_4_load_67 | 79 | 0.0027116 | 0.00067959 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1403-22_0_4_load_69 | 80 | 0.0027116 | 0.0006796 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1403-22_0_4_load_104 | 81 | 0.0061655 | 0.0015452 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1403-22_0_4_load_71 | 82 | 0.0019899 | 0.00049872 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1403-22_0_4_load_74 | 83 | 0.0014262 | 0.00035745 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1403-22_0_4_load_76 | 84 | 0.00049923 | 0.00012512 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1403-22_0_4_load_77 | 85 | 0.0019118 | 0.00047914 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1403-22_0_4_load_78 | 86 | 0.0016099 | 0.00040347 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1403-22_0_4_load_79 | 87 | 0.0015503 | 0.00038853 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1403-22_0_4_load_80 | 88 | 0.0079656 | 0.0019964 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1403-22_0_4_load_81 | 89 | 0.0042887 | 0.0010749 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1403-22_0_4_load_84 | 90 | 0.00060957 | 0.00015277 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1403-22_0_4_load_91 | 91 | 0.00056157 | 0.00014074 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1403-22_0_4_load_89 | 92 | 0.00050491 | 0.00012654 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1403-22_0_4_load_85 | 93 | 0.0008031 | 0.00020127 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1403-22_0_4_load_86 | 94 | 0.0029273 | 0.00073366 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1403-22_0_4_load_95 | 95 | 0.00055 | 0.00013784 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1403-22_0_4_load_87 | 96 | 0.00055883 | 0.00014006 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1403-22_0_4_load_88 | 97 | 0.0013429 | 0.00033656 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1403-22_0_4_load_92 | 98 | 0.00054281 | 0.00013604 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1403-22_0_4_load_98 | 99 | 0.00040731 | 0.00010208 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1403-22_0_4_load_90 | 100 | 0.00086416 | 0.00021658 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1403-22_0_4_load_93 | 102 | 0.00048668 | 0.00012197 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1403-22_0_4_load_94 | 103 | 0.00058685 | 0.00014708 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1403-22_0_4_load_102 | 104 | 0.00399 | 0.00099998 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1403-22_0_4_load_103 | 105 | 0.0019809 | 0.00049645 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1403-22_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.037914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1403-22_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.017743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1403-22_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.060754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1403-22_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.002085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1403-22_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0083542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1403-22_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.026461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1403-22_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.012951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1403-22_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.026946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1403-22_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.018287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1403-22_0_4_line_9 | NAYY 4x150 SE | 7 | 10 | 0.003511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1403-22_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.029418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1403-22_0_4_line_11 | NAYY 4x150 SE | 9 | 38 | 0.021777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1403-22_0_4_line_12 | NAYY 4x150 SE | 10 | 74 | 0.016873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1403-22_0_4_line_13 | NAYY 4x150 SE | 10 | 73 | 0.017801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1403-22_0_4_line_14 | NAYY 4x150 SE | 11 | 22 | 0.022927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1403-22_0_4_line_15 | NAYY 4x150 SE | 12 | 13 | 0.030943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1403-22_0_4_line_16 | NAYY 4x150 SE | 12 | 14 | 0.0081484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1403-22_0_4_line_17 | NAYY 4x150 SE | 13 | 15 | 0.017913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1403-22_0_4_line_18 | NAYY 4x150 SE | 13 | 16 | 0.02529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1403-22_0_4_line_19 | NAYY 4x150 SE | 15 | 17 | 0.0080237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1403-22_0_4_line_20 | NAYY 4x150 SE | 16 | 18 | 0.02174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1403-22_0_4_line_21 | NAYY 4x150 SE | 17 | 19 | 0.021674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_1403-22_0_4_line_22 | NAYY 4x150 SE | 18 | 20 | 0.026779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1403-22_0_4_line_23 | NAYY 4x150 SE | 19 | 21 | 0.042711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1403-22_0_4_line_24 | NAYY 4x150 SE | 19 | 22 | 0.0086718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1403-22_0_4_line_25 | NAYY 4x150 SE | 20 | 83 | 0.011842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1403-22_0_4_line_26 | NAYY 4x150 SE | 20 | 82 | 0.023886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1403-22_0_4_line_27 | NAYY 4x150 SE | 21 | 26 | 0.025052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1403-22_0_4_line_28 | NAYY 4x150 SE | 21 | 27 | 0.020845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1403-22_0_4_line_29 | NAYY 4x150 SE | 21 | 23 | 0.063697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1403-22_0_4_line_30 | NAYY 4x150 SE | 23 | 24 | 0.047612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1403-22_0_4_line_31 | NAYY 4x150 SE | 23 | 25 | 0.025788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1403-22_0_4_line_32 | NAYY 4x150 SE | 24 | 32 | 0.035284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1403-22_0_4_line_33 | NAYY 4x150 SE | 25 | 28 | 0.016311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1403-22_0_4_line_34 | NAYY 4x150 SE | 26 | 37 | 0.0051462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1403-22_0_4_line_35 | NAYY 4x150 SE | 29 | 30 | 0.046435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1403-22_0_4_line_36 | NAYY 4x150 SE | 29 | 31 | 0.089989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1403-22_0_4_line_37 | NAYY 4x150 SE | 30 | 33 | 0.070502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1403-22_0_4_line_38 | NAYY 4x150 SE | 31 | 34 | 0.0032476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1403-22_0_4_line_39 | NAYY 4x150 SE | 33 | 75 | 0.0092029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1403-22_0_4_line_40 | NAYY 4x150 SE | 33 | 38 | 0.033644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1403-22_0_4_line_41 | NAYY 4x150 SE | 34 | 78 | 0.010011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1403-22_0_4_line_42 | NAYY 4x150 SE | 35 | 36 | 0.041943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1403-22_0_4_line_43 | NAYY 4x150 SE | 36 | 39 | 0.10122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1403-22_0_4_line_44 | NAYY 4x150 SE | 36 | 40 | 0.0054193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1403-22_0_4_line_45 | NAYY 4x150 SE | 39 | 68 | 0.068243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1403-22_0_4_line_46 | NAYY 4x150 SE | 40 | 74 | 0.057205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1403-22_0_4_line_47 | NAYY 4x150 SE | 41 | 42 | 0.024292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1403-22_0_4_line_48 | NAYY 4x150 SE | 42 | 43 | 0.026232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1403-22_0_4_line_49 | NAYY 4x150 SE | 43 | 46 | 0.0185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1403-22_0_4_line_50 | NAYY 4x150 SE | 44 | 45 | 0.037095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1403-22_0_4_line_51 | NAYY 4x150 SE | 45 | 50 | 0.071498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1403-22_0_4_line_52 | NAYY 4x150 SE | 45 | 47 | 0.14564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1403-22_0_4_line_53 | NAYY 4x150 SE | 46 | 47 | 0.094208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1403-22_0_4_line_54 | NAYY 4x150 SE | 47 | 48 | 0.035106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1403-22_0_4_line_55 | NAYY 4x150 SE | 48 | 49 | 0.043192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1403-22_0_4_line_56 | NAYY 4x150 SE | 49 | 51 | 0.093663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1403-22_0_4_line_57 | NAYY 4x150 SE | 49 | 52 | 0.041955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1403-22_0_4_line_58 | NAYY 4x150 SE | 50 | 89 | 0.023811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1403-22_0_4_line_59 | NAYY 4x150 SE | 51 | 54 | 0.038972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1403-22_0_4_line_60 | NAYY 4x150 SE | 51 | 55 | 0.034447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1403-22_0_4_line_61 | NAYY 4x150 SE | 52 | 53 | 0.026656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1403-22_0_4_line_62 | NAYY 4x150 SE | 56 | 57 | 0.01498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1403-22_0_4_line_63 | NAYY 4x150 SE | 56 | 58 | 0.021859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1403-22_0_4_line_64 | NAYY 4x150 SE | 57 | 59 | 0.13238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1403-22_0_4_line_65 | NAYY 4x150 SE | 58 | 60 | 0.021339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1403-22_0_4_line_66 | NAYY 4x150 SE | 58 | 61 | 0.026921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1403-22_0_4_line_67 | NAYY 4x150 SE | 59 | 62 | 0.011091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1403-22_0_4_line_68 | NAYY 4x150 SE | 61 | 64 | 0.025981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1403-22_0_4_line_69 | NAYY 4x150 SE | 61 | 65 | 0.0087616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1403-22_0_4_line_70 | NAYY 4x150 SE | 62 | 63 | 0.084813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1403-22_0_4_line_71 | NAYY 4x150 SE | 63 | 70 | 0.024466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1403-22_0_4_line_72 | NAYY 4x150 SE | 64 | 66 | 0.01504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1403-22_0_4_line_73 | NAYY 4x150 SE | 66 | 67 | 0.00087753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1403-22_0_4_line_74 | NAYY 4x150 SE | 67 | 71 | 0.0029388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1403-22_0_4_line_75 | NAYY 4x150 SE | 68 | 69 | 0.014528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1403-22_0_4_line_76 | NAYY 4x150 SE | 69 | 104 | 0.19592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1403-22_0_4_line_77 | NAYY 4x150 SE | 70 | 90 | 0.093065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1403-22_0_4_line_78 | NAYY 4x150 SE | 70 | 91 | 0.098489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1403-22_0_4_line_79 | NAYY 4x150 SE | 71 | 72 | 0.005802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1403-22_0_4_line_80 | NAYY 4x150 SE | 72 | 73 | 0.036917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1403-22_0_4_line_81 | NAYY 4x150 SE | 75 | 76 | 0.0044482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1403-22_0_4_line_82 | NAYY 4x150 SE | 76 | 77 | 0.008924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1403-22_0_4_line_83 | NAYY 4x150 SE | 78 | 79 | 0.014551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1403-22_0_4_line_84 | NAYY 4x150 SE | 79 | 80 | 0.023884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1403-22_0_4_line_85 | NAYY 4x150 SE | 80 | 81 | 0.0089011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1403-22_0_4_line_86 | NAYY 4x150 SE | 83 | 84 | 0.001589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_1403-22_0_4_line_87 | NAYY 4x150 SE | 84 | 85 | 0.018548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_1403-22_0_4_line_88 | NAYY 4x150 SE | 85 | 86 | 0.019178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_1403-22_0_4_line_89 | NAYY 4x150 SE | 86 | 87 | 0.014823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1403-22_0_4_line_90 | NAYY 4x150 SE | 87 | 88 | 0.10418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
91 | LV_1403-22_0_4_line_91 | NAYY 4x150 SE | 88 | 89 | 0.022767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1403-22_0_4_line_92 | NAYY 4x150 SE | 90 | 93 | 0.0057641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1403-22_0_4_line_93 | NAYY 4x150 SE | 91 | 92 | 0.0085862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1403-22_0_4_line_94 | NAYY 4x150 SE | 92 | 95 | 0.034435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1403-22_0_4_line_95 | NAYY 4x150 SE | 93 | 94 | 0.013479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1403-22_0_4_line_96 | NAYY 4x150 SE | 95 | 101 | 0.027022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1403-22_0_4_line_97 | NAYY 4x150 SE | 95 | 102 | 0.0057581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1403-22_0_4_line_98 | NAYY 4x150 SE | 96 | 97 | 0.037615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1403-22_0_4_line_99 | NAYY 4x150 SE | 96 | 98 | 0.11379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1403-22_0_4_line_100 | NAYY 4x150 SE | 97 | 99 | 0.029633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1403-22_0_4_line_101 | NAYY 4x150 SE | 98 | 100 | 0.026863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1403-22_0_4_line_102 | NAYY 4x150 SE | 100 | 101 | 0.025215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1403-22_0_4_line_103 | NAYY 4x150 SE | 102 | 103 | 0.016225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1403-22_0_4_line_104 | NAYY 4x150 SE | 104 | 105 | 0.024626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1403-22_0_4_trafo_1 | 0.25 MVA 20/0.4 kV | 106 | 1 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2656857.1517 | 1186847.5283 | 2656871.2299 | 1186851.921 | 2656874.7886 | 1186854.8119 | 2656876.2892 | 1186858.2948 | 2656876.137 | 1186860.6613 | 2656875.9924 | 1186863.028 | 2656875.9297 | 1186864.0057 | 2656874.5559 | 1186872.9678
1 | 2656840.214 | 1186842.2435 | 2656857.1517 | 1186847.5283
2 | 2656918.8465 | 1186902.7683 | 2656882.2228 | 1186890.6916 | 2656878.4572 | 1186888.7103 | 2656874.6935 | 1186885.7173 | 2656873.4361 | 1186883.1372 | 2656873.4163 | 1186880.4022 | 2656874.5559 | 1186872.9678
3 | 2656918.8465 | 1186902.7683 | 2656919.2094 | 1186900.7151
4 | 2656918.8465 | 1186902.7683 | 2656916.7858 | 1186910.8644
5 | 2656919.2094 | 1186900.7151 | 2656932.5711 | 1186900.553 | 2656937.3823 | 1186900.8989 | 2656939.3308 | 1186901.4066 | 2656941.1548 | 1186902.1577 | 2656942.9113 | 1186903.5974 | 2656944.1936 | 1186905.1549
6 | 2656919.2094 | 1186900.7151 | 2656919.7586 | 1186887.7758
7 | 2656904.2229 | 1186934.5696 | 2656909.4164 | 1186926.8034 | 2656911.8888 | 1186922.7579 | 2656916.7858 | 1186910.8644
8 | 2656949.3957 | 1186922.5032 | 2656949.4425 | 1186921.2583 | 2656948.8937 | 1186917.9846 | 2656945.7548 | 1186907.8713 | 2656944.1936 | 1186905.1549
9 | 2656919.9074 | 1186884.268 | 2656919.7586 | 1186887.7758
10 | 2656879.3831 | 1186947.0741 | 2656882.8555 | 1186947.7964 | 2656884.8082 | 1186947.8594 | 2656886.6651 | 1186947.5546 | 2656888.8241 | 1186946.7858 | 2656892.1669 | 1186945.0832 | 2656895.7453 | 1186942.6825 | 2656899.4461 | 1186939.438 | 2656904.2229 | 1186934.5696
11 | 2656935.312 | 1186938.0891 | 2656945.7995 | 1186929.6506 | 2656947.7639 | 1186927.6793 | 2656948.9119 | 1186925.7002 | 2656949.3506 | 1186923.7032 | 2656949.3957 | 1186922.5032
12 | 2656919.9074 | 1186884.268 | 2656921.2274 | 1186867.447
13 | 2656919.9074 | 1186884.268 | 2656927.3547 | 1186883.4271 | 2656936.5453 | 1186881.3911 | 2656937.4295 | 1186881.2651
14 | 2656879.3831 | 1186947.0741 | 2656872.7631 | 1186967.6784 | 2656872.3172 | 1186968.884
15 | 2656823.8392 | 1186962.945 | 2656834.8554 | 1186943.7942 | 2656839.191 | 1186936.0795
16 | 2656843.183 | 1186928.976 | 2656839.191 | 1186936.0795
17 | 2656823.8392 | 1186962.945 | 2656832.7746 | 1186965.2755 | 2656841.049 | 1186967.892
18 | 2656798.5919 | 1186960.5265 | 2656823.8392 | 1186962.945
19 | 2656841.049 | 1186967.892 | 2656848.6993 | 1186970.3111
20 | 2656798.5919 | 1186960.5265 | 2656793.3441 | 1186958.7535 | 2656789.023 | 1186955.7998 | 2656784.7764 | 1186951.4349 | 2656782.2841 | 1186947.2426
21 | 2656869.3096 | 1186977.0176 | 2656850.6437 | 1186970.9259 | 2656848.6993 | 1186970.3111
22 | 2656767.5 | 1186925.112 | 2656774.8356 | 1186933.6196 | 2656777.3387 | 1186937.6011 | 2656780.9612 | 1186945.0173 | 2656782.2841 | 1186947.2426
23 | 2656869.3096 | 1186977.0176 | 2656864.8768 | 1186988.2485 | 2656859.9754 | 1186999.8196 | 2656876.0883 | 1187007.9993
24 | 2656869.3096 | 1186977.0176 | 2656872.3172 | 1186968.884
25 | 2656767.5 | 1186925.112 | 2656768.7648 | 1186923.6898 | 2656769.2316 | 1186921.1261 | 2656769.1695 | 1186913.793
26 | 2656767.5 | 1186925.112 | 2656765.8716 | 1186926.2527 | 2656763.4852 | 1186926.8749 | 2656744.1157 | 1186928.4232
27 | 2656876.0883 | 1187007.9993 | 2656888.8007 | 1187015.1129 | 2656891.0535 | 1187017.3133 | 2656892.036 | 1187019.913 | 2656891.1393 | 1187024.38
28 | 2656876.0883 | 1187007.9993 | 2656882.148 | 1187006.2225 | 2656886.0565 | 1187003.6026 | 2656888.9405 | 1187002.0068 | 2656891.5002 | 1187001.6198 | 2656895.3726 | 1187002.3459
29 | 2656840.1217 | 1187040.8988 | 2656846.1029 | 1187028.1039 | 2656859.9754 | 1186999.8196 | 2656876.0883 | 1187007.9993
30 | 2656822.4844 | 1187081.6211 | 2656824.8029 | 1187079.3085 | 2656827.7464 | 1187077.8689 | 2656831.0006 | 1187077.4551 | 2656832.7963 | 1187067.5221 | 2656833.6976 | 1187061.783 | 2656834.8061 | 1187056.7351 | 2656835.8146 | 1187053.3761 | 2656837.153 | 1187049.8201 | 2656840.1217 | 1187040.8988
31 | 2656840.1217 | 1187040.8988 | 2656846.6496 | 1187043.6512 | 2656845.5864 | 1187047.1542 | 2656851.5494 | 1187049.1229 | 2656853.1041 | 1187050.116 | 2656858.9907 | 1187046.4809 | 2656858.9907 | 1187046.4809
32 | 2656824.4781 | 1187046.7982 | 2656825.3069 | 1187051.9201 | 2656825.4328 | 1187056.346 | 2656824.6719 | 1187060.9524 | 2656822.7965 | 1187067.216 | 2656822.2964 | 1187070.0684 | 2656822.1868 | 1187072.78 | 2656822.4844 | 1187081.6211
33 | 2656858.9907 | 1187046.4809 | 2656871.1005 | 1187057.4085
34 | 2656889.6418 | 1187029.2633 | 2656890.5303 | 1187027.414 | 2656891.1393 | 1187024.38
35 | 2656929.4634 | 1187053.2983 | 2656927.3749 | 1187051.4775 | 2656926.2822 | 1187049.2436 | 2656926.2942 | 1187045.575 | 2656927.1659 | 1187042.1591 | 2656929.1544 | 1187039.2541 | 2656936.6808 | 1187033.2778 | 2656940.9615 | 1187029.2273 | 2656943.8957 | 1187024.7638 | 2656946.5891 | 1187017.5298 | 2656946.9823 | 1187015.6729
36 | 2656929.4634 | 1187053.2983 | 2656933.9445 | 1187053.8523 | 2656938.0125 | 1187052.9127 | 2656944.1352 | 1187050.1248 | 2656952.1386 | 1187043.7306 | 2656969.0649 | 1187027.3378 | 2656975.8563 | 1187018.4196 | 2656979.8768 | 1187010.4533 | 2656987.9403 | 1186991.4635
37 | 2656966.2111 | 1186948.7443 | 2656966.9244 | 1186950.7633 | 2656967.0033 | 1186952.8986 | 2656966.6184 | 1186955.6631 | 2656965.8761 | 1186958.302 | 2656962.2136 | 1186967.1388 | 2656954.5557 | 1186983.7198 | 2656951.8216 | 1186992.8212 | 2656946.9823 | 1187015.6729
38 | 2656987.9403 | 1186991.4635 | 2656989.2097 | 1186988.4743
39 | 2656966.2111 | 1186948.7443 | 2656971.6404 | 1186945.8831 | 2656974.1144 | 1186944.0723 | 2656974.1144 | 1186944.0723
40 | 2656966.2111 | 1186948.7443 | 2656965.1377 | 1186946.8886 | 2656963.8611 | 1186945.5423 | 2656962.1708 | 1186944.3589 | 2656960.2417 | 1186943.429 | 2656957.6107 | 1186942.4812 | 2656935.312 | 1186938.0891
41 | 2656992.8637 | 1186979.1595 | 2656991.5371 | 1186982.9932 | 2656989.2097 | 1186988.4743
42 | 2656922.5682 | 1186805.0153 | 2656914.8874 | 1186823.9975 | 2656908.0618 | 1186844.3489
43 | 2656959.7753 | 1186710.8604 | 2656922.5682 | 1186805.0153
44 | 2656922.5682 | 1186805.0153 | 2656923.1333 | 1186810.4051
45 | 2656959.7753 | 1186710.8604 | 2656955.7677 | 1186707.0312 | 2656954.7956 | 1186705.7435 | 2656953.843 | 1186704.0224 | 2656952.896 | 1186700.9005 | 2656952.542 | 1186698.0066 | 2656952.4802 | 1186694.8709 | 2656953.1694 | 1186685.7835 | 2656953.2755 | 1186681.8489 | 2656953.0723 | 1186679.1455 | 2656952.2489 | 1186674.2571 | 2656950.632 | 1186668.5719 | 2656948.2519 | 1186662.8905 | 2656945.0469 | 1186656.5009 | 2656941.6131 | 1186650.098 | 2656939.8267 | 1186648.204
46 | 2656921.2274 | 1186867.447 | 2656923.9183 | 1186833.1551 | 2656924.1772 | 1186820.3615 | 2656923.1333 | 1186810.4051
47 | 2656636.1538 | 1186409.4168 | 2656638.3221 | 1186410.5895 | 2656643.6542 | 1186412.3853 | 2656651.0437 | 1186414.4786 | 2656653.9817 | 1186416.0739 | 2656657.0231 | 1186418.026 | 2656658.2277 | 1186419.0226
48 | 2656658.2277 | 1186419.0226 | 2656661.0737 | 1186421.3772 | 2656662.8811 | 1186423.918 | 2656665.9351 | 1186430.1837 | 2656667.275 | 1186432.1197 | 2656669.1923 | 1186433.5164 | 2656676.1968 | 1186436.769
49 | 2656676.1968 | 1186436.769 | 2656692.4093 | 1186444.2976 | 2656692.9045 | 1186444.679
50 | 2656767.0679 | 1186637.4128 | 2656729.8803 | 1186636.3267
51 | 2656767.0679 | 1186637.4128 | 2656767.5836 | 1186708.9089
52 | 2656767.0679 | 1186637.4128 | 2656773.811 | 1186491.9282
53 | 2656773.811 | 1186491.9282 | 2656747.2077 | 1186479.3915 | 2656724.0747 | 1186467.8215 | 2656716.7285 | 1186463.5829 | 2656708.9285 | 1186458.1061 | 2656702.0836 | 1186452.4937 | 2656697.7424 | 1186448.4059 | 2656692.9045 | 1186444.679
54 | 2656773.811 | 1186491.9282 | 2656775.0231 | 1186488.8269 | 2656776.0555 | 1186485.368 | 2656776.3281 | 1186481.5685 | 2656776.1054 | 1186477.6864 | 2656775.2443 | 1186473.5426 | 2656773.782 | 1186469.2263 | 2656771.4943 | 1186463.4347 | 2656768.8471 | 1186458.6689
55 | 2656737.5272 | 1186429.972 | 2656754.3637 | 1186440.8932 | 2656758.6491 | 1186444.4246 | 2656761.5941 | 1186447.6877 | 2656763.9602 | 1186450.8452 | 2656767.4655 | 1186456.1814 | 2656768.8471 | 1186458.6689
56 | 2656737.5272 | 1186429.972 | 2656732.113 | 1186422.3498 | 2656728.03 | 1186414.3623 | 2656725.8915 | 1186408.9279 | 2656725.007 | 1186404.8283 | 2656724.8329 | 1186401.4581 | 2656725.1243 | 1186397.2807 | 2656726.2428 | 1186387.9527 | 2656726.9671 | 1186384.7912 | 2656728.3173 | 1186381.6133 | 2656729.9197 | 1186379.1937 | 2656732.3548 | 1186376.682 | 2656745.0374 | 1186366.1629 | 2656747.7244 | 1186365.2545 | 2656749.343 | 1186365.1586 | 2656751.178 | 1186365.5762 | 2656753.0684 | 1186366.5947 | 2656758.5645 | 1186370.4156 | 2656761.1042 | 1186372.9633
57 | 2656737.5272 | 1186429.972 | 2656718.2595 | 1186417.1269 | 2656713.7774 | 1186413.4157 | 2656705.4205 | 1186403.8869 | 2656705.1875 | 1186403.6902
58 | 2656767.7553 | 1186732.7191 | 2656767.5836 | 1186708.9089
59 | 2656784.6639 | 1186403.9483 | 2656775.3639 | 1186390.0857 | 2656770.881 | 1186384.0288 | 2656764.7099 | 1186376.5661 | 2656761.1042 | 1186372.9633
60 | 2656745.2849 | 1186342.4519 | 2656752.8949 | 1186355.1088 | 2656757.9822 | 1186365.0293 | 2656760.2096 | 1186369.9309 | 2656761.1042 | 1186372.9633
61 | 2656686.5673 | 1186384.8546 | 2656692.7178 | 1186393.1607 | 2656705.1875 | 1186403.6902
62 | 2657020.6029 | 1186821.6877 | 2657018.3677 | 1186817.4775 | 2657015.9598 | 1186813.13 | 2657012.9183 | 1186811.2222 | 2657013.9207 | 1186809.9075
63 | 2657016.4906 | 1186838.327 | 2657021.1489 | 1186836.3146 | 2657023.9054 | 1186833.6949 | 2657024.6211 | 1186830.6444 | 2657023.3448 | 1186826.8524 | 2657020.6029 | 1186821.6877
64 | 2657013.9207 | 1186809.9075 | 2657127.9703 | 1186742.6904
65 | 2657016.4906 | 1186838.327 | 2657015.8405 | 1186844.1018 | 2657014.8987 | 1186846.8499 | 2657009.8747 | 1186858.4309
66 | 2656992.0878 | 1186828.1002 | 2656998.7959 | 1186832.7777 | 2657005.6413 | 1186835.8557 | 2657011.3571 | 1186838.1669 | 2657016.4906 | 1186838.327
67 | 2657138.9864 | 1186742.8844 | 2657136.1762 | 1186742.324 | 2657133.0006 | 1186742.4716 | 2657130.1121 | 1186742.922 | 2657127.9703 | 1186742.6904
68 | 2656992.0878 | 1186828.1002 | 2656975.6829 | 1186839.3505 | 2656972.4365 | 1186844.5025
69 | 2656992.0878 | 1186828.1002 | 2656988.0215 | 1186820.3394
70 | 2657138.9864 | 1186742.8844 | 2657142.2788 | 1186744.8836 | 2657146.6421 | 1186748.2049 | 2657166.5832 | 1186767.8394 | 2657170.9898 | 1186771.4168 | 2657175.0593 | 1186774.3351 | 2657182.123 | 1186778.527 | 2657186.8175 | 1186781.518 | 2657189.4451 | 1186784.4224 | 2657191.6304 | 1186787.2894 | 2657194.6641 | 1186793.2105 | 2657195.7819 | 1186801.9935
71 | 2657195.7819 | 1186801.9935 | 2657196.7792 | 1186809.829 | 2657197.3355 | 1186818.6837 | 2657198.7516 | 1186823.0108 | 2657200.4902 | 1186825.628
72 | 2656964.538 | 1186857.1192 | 2656964.9652 | 1186856.7251 | 2656968.4908 | 1186852.6674 | 2656971.4143 | 1186846.1249 | 2656972.4365 | 1186844.5025
73 | 2656963.893 | 1186857.7143 | 2656964.538 | 1186857.1192
74 | 2656961.7329 | 1186859.7069 | 2656963.893 | 1186857.7143
75 | 2656929.8588 | 1186637.6349 | 2656939.8267 | 1186648.204
76 | 2656929.8588 | 1186637.6349 | 2657051.6487 | 1186484.1716
77 | 2657200.4902 | 1186825.628 | 2657201.2489 | 1186826.77 | 2657215.4891 | 1186843.282 | 2657217.4409 | 1186846.6358 | 2657218.1541 | 1186849.4553 | 2657217.79 | 1186853.2206 | 2657216.2739 | 1186856.1745 | 2657214.4276 | 1186858.5582 | 2657200.1504 | 1186869.0834 | 2657197.1505 | 1186872.4122 | 2657194.2083 | 1186878.4986 | 2657193.5119 | 1186885.1068 | 2657194.5309 | 1186892.6541 | 2657196.4483 | 1186902.2071
78 | 2657298.7776 | 1186831.9242 | 2657200.4902 | 1186825.628
79 | 2656961.7329 | 1186859.7069 | 2656957.6294 | 1186863.4925 | 2656957.622 | 1186863.7114
80 | 2656957.622 | 1186863.7114 | 2656957.5658 | 1186865.3707 | 2656961.1844 | 1186873.1873 | 2656961.2449 | 1186874.0439 | 2656960.9623 | 1186874.875 | 2656953.7565 | 1186879.209 | 2656951.8051 | 1186879.813 | 2656942.1763 | 1186880.5886 | 2656937.4295 | 1186881.2651
81 | 2656976.621 | 1186940.4072 | 2656976.1862 | 1186941.2349 | 2656974.1144 | 1186944.0723
82 | 2656980.7709 | 1186932.5069 | 2656976.621 | 1186940.4072
83 | 2656992.8637 | 1186979.1595 | 2656995.1068 | 1186972.6769 | 2656997.1274 | 1186965.2561
84 | 2656997.1274 | 1186965.2561 | 2657003.4023 | 1186942.2112
85 | 2657005.7408 | 1186933.6228 | 2657003.4023 | 1186942.2112
86 | 2656769.156 | 1186912.2041 | 2656769.1695 | 1186913.793
87 | 2656769.156 | 1186912.2041 | 2656768.999 | 1186893.6571
88 | 2656768.999 | 1186893.6571 | 2656768.8366 | 1186874.4801
89 | 2656768.8366 | 1186874.4801 | 2656768.7111 | 1186859.6577
90 | 2656768.7111 | 1186859.6577 | 2656768.4396 | 1186827.5882 | 2656767.9195 | 1186755.4857
91 | 2656767.9195 | 1186755.4857 | 2656767.7553 | 1186732.7191
92 | 2657197.5827 | 1186907.8585 | 2657196.4483 | 1186902.2071
93 | 2657303.1743 | 1186839.2993 | 2657298.7776 | 1186831.9242
94 | 2657303.1743 | 1186839.2993 | 2657337.3255 | 1186834.8865
95 | 2657197.5827 | 1186907.8585 | 2657197.5827 | 1186907.8585 | 2657201.1447 | 1186911.9726 | 2657208.3791 | 1186915.4733
96 | 2657324.794 | 1186857.2011 | 2657327.29 | 1186857.1027 | 2657328.4294 | 1186856.0463 | 2657330.0031 | 1186852.6594 | 2657334.5479 | 1186842.575 | 2657337.3255 | 1186834.8865
97 | 2657338.9517 | 1186829.3642 | 2657337.5498 | 1186834.2657 | 2657337.3255 | 1186834.8865
98 | 2657316.3699 | 1187047.4753 | 2657324.0008 | 1187042.9092 | 2657325.599 | 1187040.1451 | 2657326.4175 | 1187037.5404 | 2657326.4957 | 1187034.1503 | 2657323.7602 | 1187026.5977 | 2657318.6208 | 1187016.4497
99 | 2657342.4531 | 1186905.1863 | 2657318.6208 | 1187016.4497
100 | 2657289.1176 | 1187058.829 | 2657300.2147 | 1187053.6878 | 2657312.3521 | 1187049.8795 | 2657316.3699 | 1187047.4753
101 | 2657328.6973 | 1186882.1121 | 2657342.4531 | 1186905.1863
102 | 2657328.6973 | 1186882.1121 | 2657324.794 | 1186857.2011
103 | 2657338.9517 | 1186829.3642 | 2657340.1786 | 1186825.0746 | 2657342.7644 | 1186813.5987
104 | 2657051.6487 | 1186484.1716 | 2657071.171 | 1186499.1816

## bus_geodata
| x | y | coords
0 | 2656857.1517 | 1186847.5283
1 | 2656874.5559 | 1186872.9678
2 | 2656840.214 | 1186842.2435
3 | 2656918.8466 | 1186902.7683
4 | 2656919.2094 | 1186900.7151
5 | 2656916.7858 | 1186910.8644
6 | 2656944.1936 | 1186905.1549
7 | 2656919.7586 | 1186887.7758
8 | 2656904.2229 | 1186934.5696
9 | 2656949.3957 | 1186922.5032
10 | 2656919.9074 | 1186884.268
11 | 2656879.3831 | 1186947.0741
12 | 2656839.191 | 1186936.0795
13 | 2656823.8392 | 1186962.945
14 | 2656843.183 | 1186928.976
15 | 2656841.049 | 1186967.892
16 | 2656798.5919 | 1186960.5265
17 | 2656848.6993 | 1186970.3111
18 | 2656782.2841 | 1186947.2426
19 | 2656869.3096 | 1186977.0176
20 | 2656767.5 | 1186925.112
21 | 2656876.0883 | 1187007.9993
22 | 2656872.3172 | 1186968.884
23 | 2656840.1217 | 1187040.8988
24 | 2656822.4844 | 1187081.6211
25 | 2656858.9907 | 1187046.481
26 | 2656891.1393 | 1187024.38
27 | 2656895.3726 | 1187002.3459
28 | 2656871.1005 | 1187057.4085
29 | 2656929.4634 | 1187053.2983
30 | 2656946.9823 | 1187015.6729
31 | 2656987.9403 | 1186991.4635
32 | 2656824.4781 | 1187046.7982
33 | 2656966.2111 | 1186948.7443
34 | 2656989.2097 | 1186988.4743
35 | 2656908.0618 | 1186844.3489
36 | 2656922.5682 | 1186805.0153
37 | 2656889.6418 | 1187029.2633
38 | 2656935.312 | 1186938.0891
39 | 2656959.7753 | 1186710.8604
40 | 2656923.1333 | 1186810.4051
41 | 2656636.1538 | 1186409.4168
42 | 2656658.2277 | 1186419.0226
43 | 2656676.1968 | 1186436.769
44 | 2656729.8803 | 1186636.3267
45 | 2656767.0679 | 1186637.4128
46 | 2656692.9045 | 1186444.679
47 | 2656773.811 | 1186491.9282
48 | 2656768.8471 | 1186458.6689
49 | 2656737.5272 | 1186429.972
50 | 2656767.5836 | 1186708.9089
51 | 2656761.1042 | 1186372.9633
52 | 2656705.1875 | 1186403.6902
53 | 2656686.5673 | 1186384.8546
54 | 2656784.6639 | 1186403.9483
55 | 2656745.2849 | 1186342.4519
56 | 2657020.6029 | 1186821.6877
57 | 2657013.9207 | 1186809.9075
58 | 2657016.4906 | 1186838.327
59 | 2657127.9703 | 1186742.6904
60 | 2657009.8747 | 1186858.4309
61 | 2656992.0878 | 1186828.1002
62 | 2657138.9864 | 1186742.8844
63 | 2657195.7819 | 1186801.9935
64 | 2656972.4365 | 1186844.5025
65 | 2656988.0215 | 1186820.3394
66 | 2656964.538 | 1186857.1193
67 | 2656963.893 | 1186857.7143
68 | 2656939.8267 | 1186648.204
69 | 2656929.8588 | 1186637.6349
70 | 2657200.4902 | 1186825.628
71 | 2656961.7329 | 1186859.7069
72 | 2656957.622 | 1186863.7114
73 | 2656937.4295 | 1186881.2651
74 | 2656921.2274 | 1186867.447
75 | 2656974.1144 | 1186944.0723
76 | 2656976.621 | 1186940.4072
77 | 2656980.7709 | 1186932.5069
78 | 2656992.8637 | 1186979.1595
79 | 2656997.1274 | 1186965.2561
80 | 2657003.4023 | 1186942.2112
81 | 2657005.7408 | 1186933.6228
82 | 2656744.1157 | 1186928.4232
83 | 2656769.1695 | 1186913.793
84 | 2656769.156 | 1186912.2041
85 | 2656768.999 | 1186893.6571
86 | 2656768.8366 | 1186874.4801
87 | 2656768.7111 | 1186859.6577
88 | 2656767.9195 | 1186755.4857
89 | 2656767.7553 | 1186732.7191
90 | 2657196.4483 | 1186902.2071
91 | 2657298.7776 | 1186831.9242
92 | 2657303.1743 | 1186839.2993
93 | 2657197.5827 | 1186907.8585
94 | 2657208.3791 | 1186915.4733
95 | 2657337.3255 | 1186834.8865
96 | 2657318.6208 | 1187016.4497
97 | 2657316.3699 | 1187047.4753
98 | 2657342.4531 | 1186905.1863
99 | 2657289.1176 | 1187058.829
100 | 2657328.6973 | 1186882.1121
101 | 2657324.794 | 1186857.2011
102 | 2657338.9517 | 1186829.3642
103 | 2657342.7644 | 1186813.5987
104 | 2657051.6487 | 1186484.1716
105 | 2657071.171 | 1186499.1816
106 | 2656840.214 | 1186842.2435

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99971 | -0.0020052 | 0.0030375 | 0.00076128
1 | 1 | 0 | -0.24118 | -0.060689
2 | 0.99966 | -0.0024053 | 0.0022567 | 0.00056559
3 | 0.99321 | -0.047161 | 0 | 0
4 | 0.99295 | -0.049018 | 0 | 0
5 | 0.99263 | -0.051212 | 0.0039548 | 0.00099117
6 | 0.99136 | -0.060141 | 0.00062814 | 0.00015743
7 | 0.99208 | -0.055129 | 0.0014758 | 0.00036988
8 | 0.99081 | -0.063949 | 0 | 0
9 | 0.99028 | -0.067731 | 0.0058922 | 0.0014767
10 | 0.99185 | -0.056735 | 0 | 0
11 | 0.98883 | -0.077908 | 0 | 0
12 | 0.98365 | -0.11456 | 0.0080913 | 0.0020279
13 | 0.98469 | -0.10714 | 0 | 0
14 | 0.98347 | -0.11584 | 0.015177 | 0.0038038
15 | 0.98532 | -0.1027 | 0.0089139 | 0.002234
16 | 0.98409 | -0.1114 | 0 | 0
17 | 0.98563 | -0.10047 | 0.022415 | 0.0056176
18 | 0.98357 | -0.11507 | 0.0032044 | 0.00080311
19 | 0.98672 | -0.092778 | 0 | 0
20 | 0.98298 | -0.11929 | 0 | 0
21 | 0.98488 | -0.10585 | 0 | 0
22 | 0.98728 | -0.088825 | 0.0062275 | 0.0015608
23 | 0.98359 | -0.11502 | 0 | 0
24 | 0.98306 | -0.11877 | 0 | 0
25 | 0.98335 | -0.1167 | 0.0031972 | 0.00080128
26 | 0.98457 | -0.10802 | 0.0053595 | 0.0013432
27 | 0.98465 | -0.10745 | 0.0074379 | 0.0018641
28 | 0.98328 | -0.11722 | 0.0031148 | 0.00078063
29 | 0.98352 | -0.11548 | 0 | 0
30 | 0.98485 | -0.10605 | 0.0059564 | 0.0014928
31 | 0.98094 | -0.1338 | 0.0034654 | 0.00086851
32 | 0.98267 | -0.12156 | 0.0076386 | 0.0019144
33 | 0.98747 | -0.08749 | 0 | 0
34 | 0.98087 | -0.13435 | 0.0013195 | 0.0003307
35 | 0.98977 | -0.071404 | 0.0029261 | 0.00073336
36 | 0.98995 | -0.070153 | 0.0023449 | 0.00058768
37 | 0.98455 | -0.10818 | 0.0030356 | 0.00076079
38 | 0.98918 | -0.075482 | 0 | 0
39 | 0.98859 | -0.079808 | 0 | 0
40 | 0.99006 | -0.069346 | 0.001865 | 0.00046741
41 | 0.97263 | -0.19343 | 0.001587 | 0.00039774
42 | 0.97268 | -0.19302 | 0.00045394 | 0.00011377
43 | 0.97276 | -0.19246 | 0.0026659 | 0.00066813
44 | 0.97576 | -0.17083 | 0.0014566 | 0.00036506
45 | 0.97584 | -0.17026 | 0 | 0
46 | 0.97289 | -0.19154 | 0.00091902 | 0.00023033
47 | 0.97367 | -0.18594 | 0 | 0
48 | 0.97343 | -0.18764 | 0.00080997 | 0.000203
49 | 0.97319 | -0.18937 | 0 | 0
50 | 0.97706 | -0.16149 | 0.012837 | 0.0032171
51 | 0.97294 | -0.19118 | 0 | 0
52 | 0.97307 | -0.19023 | 0.0006203 | 0.00015546
53 | 0.97302 | -0.1906 | 0.0013231 | 0.0003316
54 | 0.97289 | -0.19159 | 0.00099447 | 0.00024924
55 | 0.9729 | -0.19148 | 0.0008268 | 0.00020721
56 | 0.98729 | -0.088959 | 0.0013186 | 0.00033046
57 | 0.98698 | -0.091125 | 0.0014682 | 0.00036796
58 | 0.98778 | -0.085506 | 0 | 0
59 | 0.98457 | -0.10831 | 0 | 0
60 | 0.98774 | -0.085767 | 0.0011953 | 0.00029956
61 | 0.98842 | -0.080929 | 0 | 0
62 | 0.98436 | -0.10975 | 0 | 0
63 | 0.98282 | -0.1208 | 0.0010435 | 0.00026152
64 | 0.98913 | -0.07591 | 0.00058016 | 0.0001454
65 | 0.98839 | -0.081133 | 0.0022836 | 0.00057233
66 | 0.98955 | -0.072919 | 0.0016056 | 0.00040241
67 | 0.98958 | -0.07273 | 0.00075348 | 0.00018884
68 | 0.98767 | -0.086327 | 0.0006706 | 0.00016807
69 | 0.98749 | -0.087616 | 0.0026778 | 0.00067113
70 | 0.98241 | -0.12373 | 0.0007819 | 0.00019596
71 | 0.98967 | -0.072075 | 0.0012967 | 0.00032498
72 | 0.98987 | -0.070706 | 0.00080308 | 0.00020127
73 | 0.99114 | -0.061706 | 0.0035368 | 0.0008864
74 | 0.99142 | -0.059748 | 0.0010867 | 0.00027235
75 | 0.98735 | -0.088363 | 0.0029272 | 0.00073363
76 | 0.98731 | -0.088652 | 0.0031671 | 0.00079375
77 | 0.98727 | -0.088941 | 0.0031723 | 0.00079505
78 | 0.98065 | -0.1359 | 0.003305 | 0.0008283
79 | 0.98041 | -0.13765 | 0.0027116 | 0.00067959
80 | 0.9801 | -0.13985 | 0.0027116 | 0.0006796
81 | 0.98002 | -0.14042 | 0.0061655 | 0.0015452
82 | 0.98291 | -0.11979 | 0.0019899 | 0.00049872
83 | 0.98272 | -0.12108 | 0.0014262 | 0.00035745
84 | 0.98269 | -0.12131 | 0.00049923 | 0.00012512
85 | 0.98231 | -0.12399 | 0.0019118 | 0.00047914
86 | 0.98194 | -0.12664 | 0.0016099 | 0.00040347
87 | 0.98167 | -0.1286 | 0.0015503 | 0.00038853
88 | 0.97887 | -0.14853 | 0.0079656 | 0.0019964
89 | 0.97791 | -0.15538 | 0.0042887 | 0.0010749
90 | 0.98182 | -0.12792 | 0.00060957 | 0.00015277
91 | 0.98149 | -0.1303 | 0.00056157 | 0.00014074
92 | 0.98142 | -0.13082 | 0.00050491 | 0.00012654
93 | 0.98179 | -0.12814 | 0.0008031 | 0.00020127
94 | 0.98173 | -0.12855 | 0.0029273 | 0.00073366
95 | 0.98115 | -0.13273 | 0.00055 | 0.00013784
96 | 0.98038 | -0.1383 | 0.00055883 | 0.00014006
97 | 0.98028 | -0.13899 | 0.0013429 | 0.00033656
98 | 0.98076 | -0.13556 | 0.00054281 | 0.00013604
99 | 0.98026 | -0.13911 | 0.00040731 | 0.00010208
100 | 0.98087 | -0.13476 | 0.00086416 | 0.00021658
101 | 0.981 | -0.13378 | 0 | 0
102 | 0.98114 | -0.1328 | 0.00048668 | 0.00012197
103 | 0.98113 | -0.1329 | 0.00058685 | 0.00014708
104 | 0.9858 | -0.099632 | 0.00399 | 0.00099998
105 | 0.98572 | -0.10013 | 0.0019809 | 0.00049645
106 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0052944 | -0.0013267 | 0.0052959 | 0.0013268 | 1.4691e-06 | 6.7789e-08 | 0.0078803 | 0.0078801 | 0.0078803 | 0.99971 | -0.0020052 | 1 | 0 | 2.9186
1 | 0.0022568 | 0.0005654 | -0.0022567 | -0.00056559 | 1.2493e-07 | -1.8458e-07 | 0.0033591 | 0.0033592 | 0.0033592 | 0.99971 | -0.0020052 | 0.99966 | -0.0024053 | 1.2441
2 | 0.23508 | 0.059362 | -0.23353 | -0.058769 | 0.0015477 | 0.00059288 | 0.34996 | 0.34996 | 0.34996 | 1 | 0 | 0.99321 | -0.047161 | 43.2052
3 | 0.088517 | 0.022249 | -0.088494 | -0.02224 | 2.2889e-05 | 8.7765e-06 | 0.13264 | 0.13264 | 0.13264 | 0.99321 | -0.047161 | 0.99295 | -0.049018 | 49.1251
4 | 0.14502 | 0.03652 | -0.14493 | -0.036489 | 8.207e-05 | 3.1241e-05 | 0.21732 | 0.21732 | 0.21732 | 0.99321 | -0.047161 | 0.99263 | -0.051212 | 26.8302
5 | 0.041781 | 0.010514 | -0.041716 | -0.01049 | 6.4763e-05 | 2.4567e-05 | 0.062628 | 0.062628 | 0.062628 | 0.99295 | -0.049018 | 0.99136 | -0.060141 | 23.1955
6 | 0.046713 | 0.011726 | -0.046673 | -0.011711 | 3.961e-05 | 1.5067e-05 | 0.07001 | 0.07001 | 0.07001 | 0.99295 | -0.049018 | 0.99208 | -0.055129 | 25.9297
7 | 0.14098 | 0.035497 | -0.14073 | -0.035402 | 0.00025047 | 9.5291e-05 | 0.2114 | 0.2114 | 0.2114 | 0.99263 | -0.051212 | 0.99081 | -0.063949 | 26.0983
8 | 0.041088 | 0.010332 | -0.041045 | -0.010316 | 4.3421e-05 | 1.6465e-05 | 0.061685 | 0.061685 | 0.061685 | 0.99136 | -0.060141 | 0.99028 | -0.067731 | 22.8464
9 | 0.045198 | 0.011341 | -0.045187 | -0.011337 | 1.007e-05 | 3.8277e-06 | 0.067796 | 0.067796 | 0.067796 | 0.99208 | -0.055129 | 0.99185 | -0.056735 | 25.1098
10 | 0.14073 | 0.035402 | -0.14046 | -0.035298 | 0.00027345 | 0.00010404 | 0.2114 | 0.2114 | 0.2114 | 0.99081 | -0.063949 | 0.98883 | -0.077908 | 26.0983
11 | 0.035153 | 0.0088393 | -0.035115 | -0.008825 | 3.7929e-05 | 1.4308e-05 | 0.052831 | 0.052832 | 0.052832 | 0.99028 | -0.067731 | 0.98918 | -0.075482 | 19.5672
12 | 0.017606 | 0.0044143 | -0.017599 | -0.0044117 | 7.3457e-06 | 2.6076e-06 | 0.026414 | 0.026414 | 0.026414 | 0.99185 | -0.056735 | 0.99142 | -0.059748 | 9.7829
13 | 0.027582 | 0.0069227 | -0.027563 | -0.0069156 | 1.9023e-05 | 7.0868e-06 | 0.041383 | 0.041383 | 0.041383 | 0.99185 | -0.056735 | 0.99114 | -0.061706 | 15.3269
14 | 0.14046 | 0.035298 | -0.14024 | -0.035217 | 0.00021311 | 8.1085e-05 | 0.2114 | 0.2114 | 0.2114 | 0.98883 | -0.077908 | 0.98728 | -0.088825 | 26.0984
15 | -0.023271 | -0.0058325 | 0.023295 | 0.0058414 | 2.3928e-05 | 8.8101e-06 | 0.035204 | 0.035203 | 0.035204 | 0.98365 | -0.11456 | 0.98469 | -0.10714 | 13.0384
16 | 0.01518 | 0.0038047 | -0.015177 | -0.0038038 | 2.6812e-06 | 9.2782e-07 | 0.022964 | 0.022964 | 0.022964 | 0.98365 | -0.11456 | 0.98347 | -0.11584 | 8.505
17 | -0.072564 | -0.018215 | 0.072609 | 0.018232 | 4.4808e-05 | 1.655e-05 | 0.10967 | 0.10966 | 0.10967 | 0.98469 | -0.10714 | 0.98532 | -0.1027 | 13.5389
18 | 0.049269 | 0.012374 | -0.049239 | -0.012364 | 2.9166e-05 | 1.0253e-05 | 0.074462 | 0.074462 | 0.074462 | 0.98469 | -0.10714 | 0.98409 | -0.1114 | 9.1929
19 | -0.081522 | -0.020466 | 0.081548 | 0.020475 | 2.5301e-05 | 9.4245e-06 | 0.12313 | 0.12313 | 0.12313 | 0.98532 | -0.1027 | 0.98563 | -0.10047 | 15.2008
20 | 0.049239 | 0.012364 | -0.049214 | -0.012355 | 2.5073e-05 | 8.8152e-06 | 0.074462 | 0.074462 | 0.074462 | 0.98409 | -0.1114 | 0.98357 | -0.11507 | 9.1929
21 | -0.10396 | -0.026093 | 0.10407 | 0.026135 | 0.00011107 | 4.1891e-05 | 0.15697 | 0.15697 | 0.15697 | 0.98563 | -0.10047 | 0.98672 | -0.092778 | 19.3785
22 | 0.04601 | 0.011552 | -0.045983 | -0.011542 | 2.6993e-05 | 9.3631e-06 | 0.069614 | 0.069615 | 0.069615 | 0.98357 | -0.11507 | 0.98298 | -0.11929 | 8.5944
23 | 0.029868 | 0.0074934 | -0.029814 | -0.0074731 | 5.4078e-05 | 2.0255e-05 | 0.045045 | 0.045045 | 0.045045 | 0.98672 | -0.092778 | 0.98488 | -0.10585 | 16.6834
24 | -0.13394 | -0.033628 | 0.13402 | 0.033656 | 7.3607e-05 | 2.7978e-05 | 0.20201 | 0.20201 | 0.20201 | 0.98672 | -0.092778 | 0.98728 | -0.088825 | 24.9396
25 | 0.043993 | 0.011044 | -0.043982 | -0.01104 | 1.0927e-05 | 3.7523e-06 | 0.066602 | 0.066603 | 0.066603 | 0.98298 | -0.11929 | 0.98272 | -0.12108 | 8.2225
26 | 0.00199 | 0.00049847 | -0.0019899 | -0.00049872 | 1.3526e-07 | -2.5074e-07 | 0.0030124 | 0.0030125 | 0.0030125 | 0.98298 | -0.11929 | 0.98291 | -0.11979 | 1.1157
27 | 0.0083976 | 0.0021046 | -0.0083951 | -0.002104 | 2.5165e-06 | 6.4917e-07 | 0.012688 | 0.012688 | 0.012688 | 0.98488 | -0.10585 | 0.98457 | -0.10802 | 4.6992
28 | 0.0074395 | 0.0018645 | -0.0074379 | -0.0018641 | 1.6433e-06 | 3.6686e-07 | 0.01124 | 0.01124 | 0.01124 | 0.98488 | -0.10585 | 0.98465 | -0.10745 | 4.163
29 | 0.013977 | 0.0035041 | -0.013959 | -0.0034981 | 1.7725e-05 | 6.008e-06 | 0.021118 | 0.021118 | 0.021118 | 0.98488 | -0.10585 | 0.98359 | -0.11502 | 7.8214
30 | 0.0076455 | 0.001916 | -0.0076415 | -0.0019151 | 3.9748e-06 | 9.2477e-07 | 0.011566 | 0.011567 | 0.011567 | 0.98359 | -0.11502 | 0.98306 | -0.11877 | 4.2839
31 | 0.0063136 | 0.001582 | -0.0063121 | -0.0015818 | 1.4681e-06 | 2.3741e-07 | 0.0095514 | 0.0095515 | 0.0095515 | 0.98359 | -0.11502 | 0.98335 | -0.1167 | 3.5376
32 | 0.0076415 | 0.0019151 | -0.0076386 | -0.0019144 | 2.9457e-06 | 6.8577e-07 | 0.011567 | 0.011567 | 0.011567 | 0.98306 | -0.11877 | 0.98267 | -0.12156 | 4.284
33 | 0.003115 | 0.00078051 | -0.0031148 | -0.00078063 | 2.2614e-07 | -1.1993e-07 | 0.0047136 | 0.0047136 | 0.0047136 | 0.98335 | -0.1167 | 0.98328 | -0.11722 | 1.7458
34 | 0.0030356 | 0.00076075 | -0.0030356 | -0.00076079 | 6.7591e-08 | -3.9449e-08 | 0.0045878 | 0.0045879 | 0.0045879 | 0.98457 | -0.10802 | 0.98455 | -0.10818 | 1.6992
35 | -0.019739 | -0.0049533 | 0.019765 | 0.0049626 | 2.5846e-05 | 9.3507e-06 | 0.029867 | 0.029866 | 0.029867 | 0.98352 | -0.11548 | 0.98485 | -0.10605 | 11.0617
36 | 0.019739 | 0.0049533 | -0.019689 | -0.0049352 | 5.009e-05 | 1.8126e-05 | 0.029867 | 0.029867 | 0.029867 | 0.98352 | -0.11548 | 0.98094 | -0.1338 | 11.0618
37 | -0.025721 | -0.0064555 | 0.025788 | 0.0064801 | 6.6454e-05 | 2.466e-05 | 0.038866 | 0.038866 | 0.038866 | 0.98485 | -0.10605 | 0.98747 | -0.08749 | 14.3948
38 | 0.016224 | 0.0040667 | -0.016222 | -0.0040662 | 1.2274e-06 | 4.3108e-07 | 0.02461 | 0.02461 | 0.02461 | 0.98094 | -0.1338 | 0.98087 | -0.13435 | 9.1149
39 | 0.0092682 | 0.0023227 | -0.009267 | -0.0023224 | 1.1201e-06 | 3.131e-07 | 0.013966 | 0.013966 | 0.013966 | 0.98747 | -0.08749 | 0.98735 | -0.088363 | 5.1726
40 | -0.035056 | -0.0088029 | 0.035115 | 0.008825 | 5.8598e-05 | 2.2106e-05 | 0.052832 | 0.052832 | 0.052832 | 0.98747 | -0.08749 | 0.98918 | -0.075482 | 19.5673
41 | 0.014903 | 0.0037355 | -0.0149 | -0.0037344 | 3.1932e-06 | 1.1018e-06 | 0.022608 | 0.022608 | 0.022608 | 0.98087 | -0.13435 | 0.98065 | -0.1359 | 8.3735
42 | -0.0029261 | -0.00073336 | 0.0029267 | 0.00073302 | 5.0648e-07 | -3.4436e-07 | 0.0043991 | 0.004399 | 0.0043991 | 0.98977 | -0.071404 | 0.98995 | -0.070153 | 1.6293
43 | 0.0093518 | 0.002343 | -0.0093393 | -0.0023395 | 1.2481e-05 | 3.5006e-06 | 0.014057 | 0.014057 | 0.014057 | 0.98995 | -0.070153 | 0.98859 | -0.079808 | 5.2063
44 | -0.014623 | -0.0036637 | 0.014625 | 0.0036642 | 1.6338e-06 | 5.5868e-07 | 0.02198 | 0.02198 | 0.02198 | 0.98995 | -0.070153 | 0.99006 | -0.069346 | 8.1408
45 | 0.0093393 | 0.0023395 | -0.0093309 | -0.0023371 | 8.4148e-06 | 2.3623e-06 | 0.014057 | 0.014057 | 0.014057 | 0.98859 | -0.079808 | 0.98767 | -0.086327 | 5.2064
46 | -0.01649 | -0.0041316 | 0.016512 | 0.0041393 | 2.1924e-05 | 7.6957e-06 | 0.024783 | 0.024783 | 0.024783 | 0.99006 | -0.069346 | 0.99142 | -0.059748 | 9.1789
47 | -0.001587 | -0.00039774 | 0.0015871 | 0.00039747 | 8.9353e-08 | -2.6714e-07 | 0.0024279 | 0.0024278 | 0.0024279 | 0.97263 | -0.19343 | 0.97268 | -0.19302 | 0.89923
48 | -0.002041 | -0.00051124 | 0.0020412 | 0.00051097 | 1.5956e-07 | -2.6425e-07 | 0.0031223 | 0.0031221 | 0.0031223 | 0.97268 | -0.19302 | 0.97276 | -0.19246 | 1.1564
49 | -0.0047071 | -0.0011791 | 0.0047077 | 0.0011791 | 5.9846e-07 | 4.7672e-10 | 0.0072001 | 0.0072 | 0.0072001 | 0.97276 | -0.19246 | 0.97289 | -0.19154 | 2.6667
50 | -0.0014566 | -0.00036506 | 0.0014567 | 0.00036464 | 1.142e-07 | -4.1947e-07 | 0.0022213 | 0.0022211 | 0.0022213 | 0.97576 | -0.17083 | 0.97584 | -0.17026 | 0.82269
51 | -0.011687 | -0.002925 | 0.011701 | 0.0029295 | 1.4167e-05 | 4.5545e-06 | 0.01782 | 0.01782 | 0.01782 | 0.97584 | -0.17026 | 0.97706 | -0.16149 | 6.6
52 | 0.010231 | 0.0025603 | -0.010208 | -0.0025536 | 2.2114e-05 | 6.6899e-06 | 0.015599 | 0.015599 | 0.015599 | 0.97584 | -0.17026 | 0.97367 | -0.18594 | 5.7776
53 | -0.0056267 | -0.0014094 | 0.005631 | 0.0014099 | 4.3533e-06 | 5.0356e-07 | 0.0086056 | 0.0086052 | 0.0086056 | 0.97289 | -0.19154 | 0.97367 | -0.18594 | 3.1873
54 | 0.0045774 | 0.0011437 | -0.0045764 | -0.0011437 | 1.0716e-06 | -2.4345e-08 | 0.0069943 | 0.0069944 | 0.0069944 | 0.97367 | -0.18594 | 0.97343 | -0.18764 | 2.5905
55 | 0.0037664 | 0.00094072 | -0.0037655 | -0.00094091 | 8.9308e-07 | -1.9332e-07 | 0.0057563 | 0.0057565 | 0.0057565 | 0.97343 | -0.18764 | 0.97319 | -0.18937 | 2.132
56 | 0.0018218 | 0.00045459 | -0.0018214 | -0.00045558 | 4.5334e-07 | -9.8914e-07 | 0.0027848 | 0.0027853 | 0.0027853 | 0.97319 | -0.18937 | 0.97294 | -0.19118 | 1.0316
57 | 0.0019437 | 0.00048632 | -0.0019435 | -0.00048675 | 2.312e-07 | -4.3232e-07 | 0.0029716 | 0.0029718 | 0.0029718 | 0.97319 | -0.18937 | 0.97307 | -0.19023 | 1.1007
58 | -0.024538 | -0.0061466 | 0.024559 | 0.0061543 | 2.0748e-05 | 7.6816e-06 | 0.037369 | 0.037369 | 0.037369 | 0.97706 | -0.16149 | 0.97791 | -0.15538 | 13.8404
59 | 0.00099453 | 0.00024878 | -0.00099447 | -0.00024924 | 5.6256e-08 | -4.6233e-07 | 0.0015209 | 0.001521 | 0.001521 | 0.97294 | -0.19118 | 0.97289 | -0.19159 | 0.56335
60 | 0.00082683 | 0.0002068 | -0.0008268 | -0.00020721 | 3.4368e-08 | -4.1456e-07 | 0.0012644 | 0.0012646 | 0.0012646 | 0.97294 | -0.19118 | 0.9729 | -0.19148 | 0.46835
61 | 0.0013232 | 0.00033129 | -0.0013231 | -0.0003316 | 6.8094e-08 | -3.0492e-07 | 0.0020233 | 0.0020234 | 0.0020234 | 0.97307 | -0.19023 | 0.97302 | -0.1906 | 0.7494
62 | 0.014113 | 0.0035367 | -0.014109 | -0.0035353 | 4.2293e-06 | 1.4351e-06 | 0.021271 | 0.021271 | 0.021271 | 0.98729 | -0.088959 | 0.98698 | -0.091125 | 7.8781
63 | -0.015432 | -0.0038672 | 0.015439 | 0.0038698 | 7.3783e-06 | 2.5581e-06 | 0.023258 | 0.023258 | 0.023258 | 0.98729 | -0.088959 | 0.98778 | -0.085506 | 8.6141
64 | 0.012641 | 0.0031673 | -0.012611 | -0.0031575 | 3.0002e-05 | 9.8516e-06 | 0.019057 | 0.019058 | 0.019058 | 0.98698 | -0.091125 | 0.98457 | -0.10831 | 7.0585
65 | 0.0011953 | 0.0002993 | -0.0011953 | -0.00029956 | 4.3171e-08 | -2.5654e-07 | 0.0018005 | 0.0018006 | 0.0018006 | 0.98778 | -0.085506 | 0.98774 | -0.085767 | 0.6669
66 | -0.016634 | -0.0041691 | 0.016645 | 0.0041728 | 1.0548e-05 | 3.7122e-06 | 0.025058 | 0.025058 | 0.025058 | 0.98778 | -0.085506 | 0.98842 | -0.080929 | 9.2809
67 | 0.012611 | 0.0031575 | -0.012608 | -0.0031567 | 2.5136e-06 | 8.2577e-07 | 0.019058 | 0.019058 | 0.019058 | 0.98457 | -0.10831 | 0.98436 | -0.10975 | 7.0585
68 | -0.018929 | -0.004745 | 0.018942 | 0.0047497 | 1.3165e-05 | 4.7302e-06 | 0.028496 | 0.028496 | 0.028496 | 0.98842 | -0.080929 | 0.98913 | -0.07591 | 10.5542
69 | 0.0022837 | 0.00057225 | -0.0022836 | -0.00057233 | 6.4621e-08 | -8.7442e-08 | 0.003438 | 0.003438 | 0.003438 | 0.98842 | -0.080929 | 0.98839 | -0.081133 | 1.2733
70 | 0.012608 | 0.0031567 | -0.012589 | -0.0031503 | 1.9222e-05 | 6.3167e-06 | 0.019058 | 0.019058 | 0.019058 | 0.98436 | -0.10975 | 0.98282 | -0.1208 | 7.0586
71 | 0.011545 | 0.0028888 | -0.011541 | -0.0028873 | 4.6639e-06 | 1.4839e-06 | 0.017478 | 0.017479 | 0.017479 | 0.98282 | -0.1208 | 0.98241 | -0.12373 | 6.4735
72 | -0.019522 | -0.0048951 | 0.01953 | 0.0048981 | 8.0949e-06 | 2.9203e-06 | 0.029369 | 0.029369 | 0.029369 | 0.98913 | -0.07591 | 0.98955 | -0.072919 | 10.8774
73 | -0.021136 | -0.0053005 | 0.021136 | 0.0053007 | 5.5315e-07 | 2.0148e-07 | 0.031783 | 0.031783 | 0.031783 | 0.98955 | -0.072919 | 0.98958 | -0.07273 | 11.7716
74 | -0.02189 | -0.0054895 | 0.021892 | 0.0054902 | 1.9869e-06 | 7.2643e-07 | 0.032916 | 0.032916 | 0.032916 | 0.98958 | -0.07273 | 0.98967 | -0.072075 | 12.1912
75 | 0.0086603 | 0.002169 | -0.0086587 | -0.0021686 | 1.5432e-06 | 4.0764e-07 | 0.013047 | 0.013047 | 0.013047 | 0.98767 | -0.086327 | 0.98749 | -0.087616 | 4.8323
76 | 0.0059809 | 0.0014975 | -0.005971 | -0.0014962 | 9.9297e-06 | 1.317e-06 | 0.0090119 | 0.0090128 | 0.0090128 | 0.98749 | -0.087616 | 0.9858 | -0.099632 | 3.3381
77 | 0.0043428 | 0.0010874 | -0.0043403 | -0.0010876 | 2.5126e-06 | -2.1129e-07 | 0.0065775 | 0.0065779 | 0.0065779 | 0.98241 | -0.12373 | 0.98182 | -0.12792 | 2.4363
78 | 0.0064161 | 0.001604 | -0.0064103 | -0.001603 | 5.8027e-06 | 9.8594e-07 | 0.0097167 | 0.0097172 | 0.0097172 | 0.98241 | -0.12373 | 0.98149 | -0.1303 | 3.599
79 | -0.023188 | -0.0058152 | 0.023193 | 0.0058168 | 4.4011e-06 | 1.6182e-06 | 0.034866 | 0.034866 | 0.034866 | 0.98967 | -0.072075 | 0.98987 | -0.070706 | 12.9133
80 | -0.023996 | -0.0060181 | 0.024026 | 0.0060292 | 2.9976e-05 | 1.1054e-05 | 0.036073 | 0.036073 | 0.036073 | 0.98987 | -0.070706 | 0.99114 | -0.061706 | 13.3604
81 | 0.0063398 | 0.0015888 | -0.0063395 | -0.0015887 | 2.5339e-07 | 4.057e-08 | 0.0095545 | 0.0095546 | 0.0095546 | 0.98735 | -0.088363 | 0.98731 | -0.088652 | 3.5387
82 | 0.0031724 | 0.00079499 | -0.0031723 | -0.00079505 | 1.273e-07 | -6.5157e-08 | 0.0047813 | 0.0047813 | 0.0047813 | 0.98731 | -0.088652 | 0.98727 | -0.088941 | 1.7709
83 | 0.011595 | 0.0029061 | -0.011592 | -0.0029052 | 2.8105e-06 | 8.9742e-07 | 0.017594 | 0.017594 | 0.017594 | 0.98065 | -0.1359 | 0.98041 | -0.13765 | 6.5162
84 | 0.0088803 | 0.0022256 | -0.0088776 | -0.0022249 | 2.7074e-06 | 7.4022e-07 | 0.013478 | 0.013478 | 0.013478 | 0.98041 | -0.13765 | 0.9801 | -0.13985 | 4.9919
85 | 0.006166 | 0.0015453 | -0.0061655 | -0.0015452 | 4.8675e-07 | 7.5047e-08 | 0.0093613 | 0.0093614 | 0.0093614 | 0.9801 | -0.13985 | 0.98002 | -0.14042 | 3.4672
86 | 0.042556 | 0.010683 | -0.042554 | -0.010682 | 1.3726e-06 | 4.6752e-07 | 0.064443 | 0.064443 | 0.064443 | 0.98272 | -0.12108 | 0.98269 | -0.12131 | 7.9559
87 | 0.042055 | 0.010557 | -0.04204 | -0.010552 | 1.5648e-05 | 5.3138e-06 | 0.063687 | 0.063687 | 0.063687 | 0.98269 | -0.12131 | 0.98231 | -0.12399 | 7.8626
88 | 0.040128 | 0.010073 | -0.040113 | -0.010068 | 1.4742e-05 | 4.9418e-06 | 0.060791 | 0.060792 | 0.060792 | 0.98231 | -0.12399 | 0.98194 | -0.12664 | 7.5051
89 | 0.038503 | 0.0096644 | -0.038493 | -0.0096609 | 1.0498e-05 | 3.4754e-06 | 0.058352 | 0.058352 | 0.058352 | 0.98194 | -0.12664 | 0.98167 | -0.1286 | 7.204
90 | 0.036942 | 0.0092724 | -0.03684 | -0.0092358 | 0.00010194 | 3.6581e-05 | 0.056002 | 0.056003 | 0.056003 | 0.98167 | -0.1286 | 0.97887 | -0.14853 | 10.371
91 | 0.028875 | 0.0072394 | -0.028847 | -0.0072292 | 2.7373e-05 | 1.0242e-05 | 0.043895 | 0.043895 | 0.043895 | 0.97887 | -0.14853 | 0.97791 | -0.15538 | 16.2573
92 | 0.0037307 | 0.0009348 | -0.0037306 | -0.00093483 | 1.1498e-07 | -2.8669e-08 | 0.0056541 | 0.0056541 | 0.0056541 | 0.98182 | -0.12792 | 0.98179 | -0.12814 | 2.0941
93 | 0.0058487 | 0.0014623 | -0.0058483 | -0.0014622 | 4.2114e-07 | 5.347e-08 | 0.0088658 | 0.0088658 | 0.0088658 | 0.98149 | -0.1303 | 0.98142 | -0.13082 | 3.2836
94 | 0.0053434 | 0.0013357 | -0.0053419 | -0.0013356 | 1.4099e-06 | 1.0727e-07 | 0.0081003 | 0.0081005 | 0.0081005 | 0.98142 | -0.13082 | 0.98115 | -0.13273 | 3.0002
95 | 0.0029275 | 0.00073355 | -0.0029273 | -0.00073366 | 1.6558e-07 | -1.0676e-07 | 0.0044369 | 0.004437 | 0.004437 | 0.98179 | -0.12814 | 0.98173 | -0.12855 | 1.6433
96 | 0.0037184 | 0.00092896 | -0.0037179 | -0.00092909 | 5.3606e-07 | -1.3505e-07 | 0.0056383 | 0.0056384 | 0.0056384 | 0.98115 | -0.13273 | 0.981 | -0.13378 | 2.0883
97 | 0.0010735 | 0.00026878 | -0.0010735 | -0.00026885 | 9.5237e-09 | -6.9058e-08 | 0.001628 | 0.0016281 | 0.0016281 | 0.98115 | -0.13273 | 0.98114 | -0.1328 | 0.60299
98 | 0.0017504 | 0.00043786 | -0.0017502 | -0.00043827 | 1.6564e-07 | -4.1055e-07 | 0.0026564 | 0.0026566 | 0.0026566 | 0.98038 | -0.1383 | 0.98028 | -0.13899 | 0.98392
99 | -0.0023092 | -0.00057791 | 0.0023101 | 0.00057681 | 8.7196e-07 | -1.1e-06 | 0.0035046 | 0.0035041 | 0.0035046 | 0.98038 | -0.1383 | 0.98076 | -0.13556 | 1.298
100 | 0.00040732 | 0.00010171 | -0.00040731 | -0.00010208 | 7.0674e-09 | -3.7086e-07 | 0.00061816 | 0.00061829 | 0.00061829 | 0.98028 | -0.13899 | 0.98026 | -0.13911 | 0.229
101 | -0.0028529 | -0.00071286 | 0.0028532 | 0.00071264 | 3.1394e-07 | -2.1829e-07 | 0.0043277 | 0.0043275 | 0.0043277 | 0.98076 | -0.13556 | 0.98087 | -0.13476 | 1.6028
102 | -0.0037174 | -0.00092922 | 0.0037179 | 0.00092909 | 5.0022e-07 | -1.2592e-07 | 0.0056385 | 0.0056384 | 0.0056385 | 0.98087 | -0.13476 | 0.981 | -0.13378 | 2.0883
103 | 0.00058686 | 0.00014688 | -0.00058685 | -0.00014708 | 8.0197e-09 | -2.0182e-07 | 0.00088997 | 0.00089004 | 0.00089004 | 0.98114 | -0.1328 | 0.98113 | -0.1329 | 0.32965
104 | 0.001981 | 0.00049619 | -0.0019809 | -0.00049645 | 1.374e-07 | -2.6109e-07 | 0.0029901 | 0.0029903 | 0.0029903 | 0.9858 | -0.099632 | 0.98572 | -0.10013 | 1.1075

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24298 | 0.06114

## res_load
| p_mw | q_mvar
0 | 0.0030375 | 0.00076128
1 | 0.0018018 | 0.00045157
2 | 0.0022567 | 0.00056559
3 | 0.0039548 | 0.00099117
4 | 0.00062814 | 0.00015743
5 | 0.0014758 | 0.00036988
6 | 0.0058922 | 0.0014767
7 | 0.0080913 | 0.0020279
8 | 0.015177 | 0.0038038
9 | 0.0089139 | 0.002234
10 | 0.022415 | 0.0056176
11 | 0.0032044 | 0.00080311
12 | 0.0062275 | 0.0015608
13 | 0.0031972 | 0.00080128
14 | 0.0053595 | 0.0013432
15 | 0.0074379 | 0.0018641
16 | 0.0031148 | 0.00078063
17 | 0.0059564 | 0.0014928
18 | 0.0034654 | 0.00086851
19 | 0.0076386 | 0.0019144
20 | 0.0013195 | 0.0003307
21 | 0.0029261 | 0.00073336
22 | 0.0023449 | 0.00058768
23 | 0.0030356 | 0.00076079
24 | 0.001865 | 0.00046741
25 | 0.001587 | 0.00039774
26 | 0.00045394 | 0.00011377
27 | 0.0026659 | 0.00066813
28 | 0.0014566 | 0.00036506
29 | 0.00091902 | 0.00023033
30 | 0.00080997 | 0.000203
31 | 0.012837 | 0.0032171
32 | 0.0006203 | 0.00015546
33 | 0.0013231 | 0.0003316
34 | 0.00099447 | 0.00024924
35 | 0.0008268 | 0.00020721
36 | 0.0013186 | 0.00033046
37 | 0.0014682 | 0.00036796
38 | 0.0011953 | 0.00029956
39 | 0.0010435 | 0.00026152
40 | 0.00058016 | 0.0001454
41 | 0.0022836 | 0.00057233
42 | 0.0016056 | 0.00040241
43 | 0.00075348 | 0.00018884
44 | 0.0006706 | 0.00016807
45 | 0.0026778 | 0.00067113
46 | 0.0007819 | 0.00019596
47 | 0.0012967 | 0.00032498
48 | 0.00080308 | 0.00020127
49 | 0.0035368 | 0.0008864
50 | 0.0010867 | 0.00027235
51 | 0.0029272 | 0.00073363
52 | 0.0031671 | 0.00079375
53 | 0.0031723 | 0.00079505
54 | 0.003305 | 0.0008283
55 | 0.0027116 | 0.00067959
56 | 0.0027116 | 0.0006796
57 | 0.0061655 | 0.0015452
58 | 0.0019899 | 0.00049872
59 | 0.0014262 | 0.00035745
60 | 0.00049923 | 0.00012512
61 | 0.0019118 | 0.00047914
62 | 0.0016099 | 0.00040347
63 | 0.0015503 | 0.00038853
64 | 0.0079656 | 0.0019964
65 | 0.0042887 | 0.0010749
66 | 0.00060957 | 0.00015277
67 | 0.00056157 | 0.00014074
68 | 0.00050491 | 0.00012654
69 | 0.0008031 | 0.00020127
70 | 0.0029273 | 0.00073366
71 | 0.00055 | 0.00013784
72 | 0.00055883 | 0.00014006
73 | 0.0013429 | 0.00033656
74 | 0.00054281 | 0.00013604
75 | 0.00040731 | 0.00010208
76 | 0.00086416 | 0.00021658
77 | 0.00048668 | 0.00012197
78 | 0.00058685 | 0.00014708
79 | 0.00399 | 0.00099998
80 | 0.0019809 | 0.00049645

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1